## TRV_parameters_calculator
Calculator of TRV parameters for generator circuit-breakers
Input data | Symbol | Unit of measure | Generator circuit-breaker
Class (as per Table M.1 of IEC/IEEE 62271-37-013) |  |  | 51-100 MVA
Rated voltage | Ur | kV | 20
RMS value of the AC component of the rated system-source short-circuit breaking current | ISC | kA | 50
Rated load breaking current | ILOAD | kA | 5
Capacitance value per phase installed phase to earth at the generator-side of the generator circuit-breaker | CG | µF | 0.1
Capacitance value per phase installed phase to earth at the transformer-side of the generator circuit-breaker | CS | µF | 0.1
Results of the calculation | Symbol | Unit of measure | 90 degrees out-of-phase current breaking | Load current breaking
Peak value of the standard TRV modified by the capacitors of the generator circuit-breaker | ucm | kV | 63.543 | 22.4844
Rate of rise of the standard TRV modified by the capacitors of the generator circuit-breaker | RRRVm | kV/µs | 1.6172 | 0.57177
Time delay of the standard TRV modified by the capacitors of the generator circuit-breaker | tdm | µs | 4.5154 | 4.5154
The following parameters are used in the GenCB TRV calculator as defined in Annex M and Annex N of IEC/IEEE 62271-37-013 | Symbol | Unit of measure | 90 degrees out-of-phase current breaking | Load current breaking
| Uclass | kV | 15.79 | 15.79
| Iclass | kA | 51.89 | 51.89
| KE2 | - | 3.1772 | 1.1242
| RRRV0 | kV/µs | 1.4908 | 0.52707
| KRRRV-U | 1/µs | 0.034965 | 0.012362
| KRRRV-I | kV/(µs x kA) | 0.010997 | 0.0038881
| td0 | µs | 4.1103 | 4.1103
| Ktd-U | µs/kV | 0.077295 | 0.077295
| Ktd-I | µs/kA | -0.042148 | -0.042148
Authored by MP. A free license is given for use by IEC and IEEE
Disclaimer: The IEC and IEEE disclaim liability for any personal injury, property or other damages of any nature whatsoever, whether special, indirect, consequential or compensatory, directly or indirectly resulting from this software and the document upon which its methods are based, use of, or reliance upon.

## Read me
The GenCB TRV calculator is a tool to determine the parameters of the prospective TRV, modified due to the capacitors of the generator circuit-breaker, for out-of-phase and load current breaking tests.
This tool shall be used in conjunction with the international standard IEC/IEEE 62271-37-013.
The calculated TRV parameters are valid for both 50 Hz and 60 Hz applications.
Conditions where the generator circuit-breaker is equipped with capacitors at the generator side of larger value than those on the step-up transformer side are not covered by the GenCB TRV calculator tool.
Unusual combinations of generator circuit-breaker ratings and values of capacitances (e.g. short-circuit currents or capacitances of unusual high value for a specific class) are not covered by the GenCB TRV calculator.
The GenCB TRV calculator is authored by MP. A free license is given for use by IEC and IEEE.
Disclaimer: The IEC and IEEE disclaim liability for any personal injury, property or other damages of any nature whatsoever, whether special, indirect, consequential or compensatory, directly or indirectly resulting from this software and the document upon which its methods are based, use of, or reliance upon.

## Intermediate calculations (hidden)
Class | 51-100 MVA
Rated voltage (kV) | 20
Symmetrical component of the rated system-source short-circuit breaking current (kA) | 50
Rated load breaking current (kA) | 5
Capacitance value per phase installed phase to earth at the generator-side of the generator circuit-breaker (µF) | 0.1
Capacitance value per phase installed phase to earth at the transformer-side of the generator circuit-breaker (µF) | 0.1
90 degrees out-of-phase current breaking
Peak value of the standard TRV modified by the capacitors of the generator circuit-breaker (kV) | 63.543
Rate of rise of the standard TRV modified by the capacitors of the generator circuit-breaker (kV/µs) | 1.6172
Time delay of the standard TRV modified by the capacitors of the generator circuit-breaker (µs) | 4.5154
Cs | 0.1
Cst | 0.05
Csb | 0.1
Cg/Cs | 1
Cg/Csl | 0.9
Cg/Csr | 1
U_ref | 15.79
Isc_ref | 51.89
KE2 | 3.1772
RRRV0 | 1.4908
𝐾_(𝑅𝑅𝑅𝑉−𝑈) | 0.034965
𝐾_(𝑅𝑅𝑅𝑉−I) | 0.010997
td0 | 4.1103
𝐾_(𝑡𝑑−𝑈) | 0.077295
𝐾_(𝑡𝑑−𝐼) | -0.042148
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
U_ref | 14.51 | 15.79 | 18.05 | 21.52 | 23.83 | 25.25 | 26.1 | 26.54
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
Isc_ref | 44.72 | 51.89 | 65.87 | 92.41 | 117.04 | 139.76 | 160.6 | 179.47
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
KE2avrg | 3.1824 | 3.1772 | 3.1578 | 3.09 | 3.0978 | 3.011 | 3.0475 | 2.9752
KE2tl | 3.1543 | 3.1371 | 3.1105 | 2.9842 | 2.9862 | 2.8781 | 2.9421 | 2.8266
KE2tr | 3.1242 | 3.1093 | 3.0847 | 2.97 | 2.973 | 2.8673 | 2.9328 | 2.8173
KE2bl | 3.2194 | 3.2129 | 3.1875 | 3.1194 | 3.1225 | 3.0306 | 3.067 | 2.994
KE2br | 3.1824 | 3.1772 | 3.1578 | 3.09 | 3.0978 | 3.011 | 3.0475 | 2.9752
KE2lm | 3.2194 | 3.2129 | 3.1875 | 3.1194 | 3.1225 | 3.0306 | 3.067 | 2.994
KE2rm | 3.1824 | 3.1772 | 3.1578 | 3.09 | 3.0978 | 3.011 | 3.0475 | 2.9752
KE2tm | 3.1242 | 3.1093 | 3.0847 | 2.97 | 2.973 | 2.8673 | 2.9328 | 2.8173
KE2bm | 3.1824 | 3.1772 | 3.1578 | 3.09 | 3.0978 | 3.011 | 3.0475 | 2.9752
KE2 | 3.1824 | 3.1772 | 3.1578 | 3.09 | 3.0978 | 3.011 | 3.0475 | 2.9752
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
RRRV0avrg | 1.3303 | 1.4908 | 1.8193 | 2.1569 | 2.5511 | 2.6857 | 3.0216 | 3.075
RRRV0tl | 1.7263 | 1.9295 | 2.3729 | 2.6876 | 3.1834 | 3.2711 | 3.7105 | 3.7169
RRRV0tr | 1.6893 | 1.8881 | 2.3188 | 2.6428 | 3.129 | 3.2267 | 3.653 | 3.6669
RRRV0bl | 1.367 | 1.5321 | 1.8725 | 2.207 | 2.6106 | 2.7391 | 3.0868 | 3.1347
RRRV0br | 1.3303 | 1.4908 | 1.8193 | 2.1569 | 2.5511 | 2.6857 | 3.0216 | 3.075
RRRV0lm | 1.367 | 1.5321 | 1.8725 | 2.207 | 2.6106 | 2.7391 | 3.0868 | 3.1347
RRRV0rm | 1.3303 | 1.4908 | 1.8193 | 2.1569 | 2.5511 | 2.6857 | 3.0216 | 3.075
RRRV0tm | 1.6893 | 1.8881 | 2.3188 | 2.6428 | 3.129 | 3.2267 | 3.653 | 3.6669
RRRV0bm | 1.3303 | 1.4908 | 1.8193 | 2.1569 | 2.5511 | 2.6857 | 3.0216 | 3.075
RRRV0 | 1.3303 | 1.4908 | 1.8193 | 2.1569 | 2.5511 | 2.6857 | 3.0216 | 3.075
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑅𝑅𝑅𝑉−𝑈)avrg | 0.036167 | 0.034965 | 0.03912 | 0.031227 | 0.034566 | 0.024162 | 0.03152 | 0.034478
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tl | 0.036867 | 0.037229 | 0.042462 | 0.027747 | 0.032828 | 0.015806 | 0.02276 | 0.029262
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tr | 0.037361 | 0.037199 | 0.042411 | 0.028669 | 0.033447 | 0.017523 | 0.024352 | 0.030184
𝐾_(𝑅𝑅𝑅𝑉−𝑈)bl | 0.03615 | 0.035145 | 0.039577 | 0.030642 | 0.03433 | 0.023013 | 0.030613 | 0.033893
𝐾_(𝑅𝑅𝑅𝑉−𝑈)br | 0.036167 | 0.034965 | 0.03912 | 0.031227 | 0.034566 | 0.024162 | 0.03152 | 0.034478
𝐾_(𝑅𝑅𝑅𝑉−𝑈)lm | 0.03615 | 0.035145 | 0.039577 | 0.030642 | 0.03433 | 0.023013 | 0.030613 | 0.033893
𝐾_(𝑅𝑅𝑅𝑉−𝑈)rm | 0.036167 | 0.034965 | 0.03912 | 0.031227 | 0.034566 | 0.024162 | 0.03152 | 0.034478
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tm | 0.037361 | 0.037199 | 0.042411 | 0.028669 | 0.033447 | 0.017523 | 0.024352 | 0.030184
𝐾_(𝑅𝑅𝑅𝑉−𝑈)bm | 0.036167 | 0.034965 | 0.03912 | 0.031227 | 0.034566 | 0.024162 | 0.03152 | 0.034478
𝐾_(𝑅𝑅𝑅𝑉−𝑈) | 0.036167 | 0.034965 | 0.03912 | 0.031227 | 0.034566 | 0.024162 | 0.03152 | 0.034478
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑅𝑅𝑅𝑉−I)avrg | 0.011635 | 0.010997 | 0.010812 | 0.0076666 | 0.0070982 | 0.0060346 | 0.005861 | 0.0048342
𝐾_(𝑅𝑅𝑅𝑉−I)tl | 0.012659 | 0.011801 | 0.011605 | 0.0072911 | 0.0068123 | 0.0055733 | 0.0052367 | 0.00424
𝐾_(𝑅𝑅𝑅𝑉−I)tr | 0.012679 | 0.011842 | 0.011636 | 0.0074224 | 0.0069344 | 0.0056722 | 0.0053106 | 0.0043046
𝐾_(𝑅𝑅𝑅𝑉−I)bl | 0.011723 | 0.011071 | 0.010914 | 0.0076554 | 0.0071104 | 0.0060056 | 0.0057823 | 0.0047208
𝐾_(𝑅𝑅𝑅𝑉−I)br | 0.011635 | 0.010997 | 0.010812 | 0.0076666 | 0.0070982 | 0.0060346 | 0.005861 | 0.0048342
𝐾_(𝑅𝑅𝑅𝑉−I)lm | 0.011723 | 0.011071 | 0.010914 | 0.0076554 | 0.0071104 | 0.0060056 | 0.0057823 | 0.0047208
𝐾_(𝑅𝑅𝑅𝑉−I)rm | 0.011635 | 0.010997 | 0.010812 | 0.0076666 | 0.0070982 | 0.0060346 | 0.005861 | 0.0048342
𝐾_(𝑅𝑅𝑅𝑉−I)tm | 0.012679 | 0.011842 | 0.011636 | 0.0074224 | 0.0069344 | 0.0056722 | 0.0053106 | 0.0043046
𝐾_(𝑅𝑅𝑅𝑉−I)bm | 0.011635 | 0.010997 | 0.010812 | 0.0076666 | 0.0070982 | 0.0060346 | 0.005861 | 0.0048342
𝐾_(𝑅𝑅𝑅𝑉−I) | 0.011635 | 0.010997 | 0.010812 | 0.0076666 | 0.0070982 | 0.0060346 | 0.005861 | 0.0048342
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
td0avrg | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0tl | 3.0499 | 2.8845 | 2.836 | 2.5465 | 2.3448 | 2.1528 | 2.1363 | 1.9994
td0tr | 3.1037 | 2.9363 | 2.8853 | 2.5945 | 2.3831 | 2.1847 | 2.1686 | 2.0279
td0bl | 4.2742 | 4.0733 | 3.9446 | 3.5554 | 3.265 | 2.9922 | 2.9369 | 2.7457
td0br | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0lm | 4.2742 | 4.0733 | 3.9446 | 3.5554 | 3.265 | 2.9922 | 2.9369 | 2.7457
td0rm | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0tm | 3.1037 | 2.9363 | 2.8853 | 2.5945 | 2.3831 | 2.1847 | 2.1686 | 2.0279
td0bm | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0 | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑡𝑑−𝑈)avrg | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)tl | 0.053875 | 0.042893 | 0.03495 | 0.015041 | 0.019194 | 0.003071 | 0.012747 | 0.010194
𝐾_(𝑡𝑑−𝑈)tr | 0.059239 | 0.046612 | 0.037059 | 0.016065 | 0.021049 | 0.0050557 | 0.014075 | 0.010983
𝐾_(𝑡𝑑−𝑈)bl | 0.094002 | 0.076052 | 0.068783 | 0.036052 | 0.042832 | 0.016956 | 0.030948 | 0.022369
𝐾_(𝑡𝑑−𝑈)br | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)lm | 0.094002 | 0.076052 | 0.068783 | 0.036052 | 0.042832 | 0.016956 | 0.030948 | 0.022369
𝐾_(𝑡𝑑−𝑈)rm | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)tm | 0.059239 | 0.046612 | 0.037059 | 0.016065 | 0.021049 | 0.0050557 | 0.014075 | 0.010983
𝐾_(𝑡𝑑−𝑈)bm | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈) | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑡𝑑−𝐼)avrg | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)tl | -0.037012 | -0.029125 | -0.020052 | -0.012582 | -0.0092115 | -0.0071505 | -0.0067292 | -0.0048972
𝐾_(𝑡𝑑−𝐼)tr | -0.037654 | -0.02932 | -0.020373 | -0.012842 | -0.0094223 | -0.0073457 | -0.0066908 | -0.0047844
𝐾_(𝑡𝑑−𝐼)bl | -0.053741 | -0.042351 | -0.029098 | -0.018636 | -0.014454 | -0.011197 | -0.010058 | -0.007383
𝐾_(𝑡𝑑−𝐼)br | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)lm | -0.053741 | -0.042351 | -0.029098 | -0.018636 | -0.014454 | -0.011197 | -0.010058 | -0.007383
𝐾_(𝑡𝑑−𝐼)rm | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)tm | -0.037654 | -0.02932 | -0.020373 | -0.012842 | -0.0094223 | -0.0073457 | -0.0066908 | -0.0047844
𝐾_(𝑡𝑑−𝐼)bm | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼) | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713

## CLASSES (hidden)
10-50 MVA
51-100 MVA
101-200 MVA
201-400 MVA
401-600 MVA
601-800 MVA
801-1000 MVA
≥1001 MVA

## Intermediate calculations_LS (hidden)
Class | 51-100 MVA
Rated voltage (kV) | 20
Symmetrical component of the rated system-source short-circuit breaking current (kA) | 50
Rated load breaking current (kA) | 5
Capacitance value per phase installed phase to earth at the generator-side of the generator circuit-breaker (µF) | 0.1
Capacitance value per phase installed phase to earth at the transformer-side of the generator circuit-breaker (µF) | 0.1
Iload/Isc x 5.6569 | 0.56569
Load current breaking
Peak value of the standard TRV modified by the capacitors of the generator circuit-breaker (kV) | 22.4844
Rate of rise of the standard TRV modified by the capacitors of the generator circuit-breaker (kV/µs) | 0.57177
Time delay of the standard TRV modified by the capacitors of the generator circuit-breaker (µs) | 4.5154
Cs | 0.1
Cst | 0.05
Csb | 0.1
Cg/Cs | 1
Cg/Csl | 0.9
Cg/Csr | 1
U_ref | 15.79
Isc_ref | 51.89
KE2 | 1.1242
RRRV0 | 0.52707
𝐾_(𝑅𝑅𝑅𝑉−𝑈) | 0.012362
𝐾_(𝑅𝑅𝑅𝑉−I) | 0.0038881
td0 | 4.1103
𝐾_(𝑡𝑑−𝑈) | 0.077295
𝐾_(𝑡𝑑−𝐼) | -0.042148
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
U_ref | 14.51 | 15.79 | 18.05 | 21.52 | 23.83 | 25.25 | 26.1 | 26.54
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
Isc_ref | 44.72 | 51.89 | 65.87 | 92.41 | 117.04 | 139.76 | 160.6 | 179.47
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
KE2avrg | 3.1824 | 3.1772 | 3.1578 | 3.09 | 3.0978 | 3.011 | 3.0475 | 2.9752
KE2tl | 3.1543 | 3.1371 | 3.1105 | 2.9842 | 2.9862 | 2.8781 | 2.9421 | 2.8266
KE2tr | 3.1242 | 3.1093 | 3.0847 | 2.97 | 2.973 | 2.8673 | 2.9328 | 2.8173
KE2bl | 3.2194 | 3.2129 | 3.1875 | 3.1194 | 3.1225 | 3.0306 | 3.067 | 2.994
KE2br | 3.1824 | 3.1772 | 3.1578 | 3.09 | 3.0978 | 3.011 | 3.0475 | 2.9752
KE2lm | 3.2194 | 3.2129 | 3.1875 | 3.1194 | 3.1225 | 3.0306 | 3.067 | 2.994
KE2rm | 3.1824 | 3.1772 | 3.1578 | 3.09 | 3.0978 | 3.011 | 3.0475 | 2.9752
KE2tm | 3.1242 | 3.1093 | 3.0847 | 2.97 | 2.973 | 2.8673 | 2.9328 | 2.8173
KE2bm | 3.1824 | 3.1772 | 3.1578 | 3.09 | 3.0978 | 3.011 | 3.0475 | 2.9752
KE2 | 3.1824 | 3.1772 | 3.1578 | 3.09 | 3.0978 | 3.011 | 3.0475 | 2.9752
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
RRRV0avrg | 1.3303 | 1.4908 | 1.8193 | 2.1569 | 2.5511 | 2.6857 | 3.0216 | 3.075
RRRV0tl | 1.7263 | 1.9295 | 2.3729 | 2.6876 | 3.1834 | 3.2711 | 3.7105 | 3.7169
RRRV0tr | 1.6893 | 1.8881 | 2.3188 | 2.6428 | 3.129 | 3.2267 | 3.653 | 3.6669
RRRV0bl | 1.367 | 1.5321 | 1.8725 | 2.207 | 2.6106 | 2.7391 | 3.0868 | 3.1347
RRRV0br | 1.3303 | 1.4908 | 1.8193 | 2.1569 | 2.5511 | 2.6857 | 3.0216 | 3.075
RRRV0lm | 1.367 | 1.5321 | 1.8725 | 2.207 | 2.6106 | 2.7391 | 3.0868 | 3.1347
RRRV0rm | 1.3303 | 1.4908 | 1.8193 | 2.1569 | 2.5511 | 2.6857 | 3.0216 | 3.075
RRRV0tm | 1.6893 | 1.8881 | 2.3188 | 2.6428 | 3.129 | 3.2267 | 3.653 | 3.6669
RRRV0bm | 1.3303 | 1.4908 | 1.8193 | 2.1569 | 2.5511 | 2.6857 | 3.0216 | 3.075
RRRV0 | 1.3303 | 1.4908 | 1.8193 | 2.1569 | 2.5511 | 2.6857 | 3.0216 | 3.075
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑅𝑅𝑅𝑉−𝑈)avrg | 0.036167 | 0.034965 | 0.03912 | 0.031227 | 0.034566 | 0.024162 | 0.03152 | 0.034478
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tl | 0.036867 | 0.037229 | 0.042462 | 0.027747 | 0.032828 | 0.015806 | 0.02276 | 0.029262
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tr | 0.037361 | 0.037199 | 0.042411 | 0.028669 | 0.033447 | 0.017523 | 0.024352 | 0.030184
𝐾_(𝑅𝑅𝑅𝑉−𝑈)bl | 0.03615 | 0.035145 | 0.039577 | 0.030642 | 0.03433 | 0.023013 | 0.030613 | 0.033893
𝐾_(𝑅𝑅𝑅𝑉−𝑈)br | 0.036167 | 0.034965 | 0.03912 | 0.031227 | 0.034566 | 0.024162 | 0.03152 | 0.034478
𝐾_(𝑅𝑅𝑅𝑉−𝑈)lm | 0.03615 | 0.035145 | 0.039577 | 0.030642 | 0.03433 | 0.023013 | 0.030613 | 0.033893
𝐾_(𝑅𝑅𝑅𝑉−𝑈)rm | 0.036167 | 0.034965 | 0.03912 | 0.031227 | 0.034566 | 0.024162 | 0.03152 | 0.034478
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tm | 0.037361 | 0.037199 | 0.042411 | 0.028669 | 0.033447 | 0.017523 | 0.024352 | 0.030184
𝐾_(𝑅𝑅𝑅𝑉−𝑈)bm | 0.036167 | 0.034965 | 0.03912 | 0.031227 | 0.034566 | 0.024162 | 0.03152 | 0.034478
𝐾_(𝑅𝑅𝑅𝑉−𝑈) | 0.036167 | 0.034965 | 0.03912 | 0.031227 | 0.034566 | 0.024162 | 0.03152 | 0.034478
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑅𝑅𝑅𝑉−I)avrg | 0.011635 | 0.010997 | 0.010812 | 0.0076666 | 0.0070982 | 0.0060346 | 0.005861 | 0.0048342
𝐾_(𝑅𝑅𝑅𝑉−I)tl | 0.012659 | 0.011801 | 0.011605 | 0.0072911 | 0.0068123 | 0.0055733 | 0.0052367 | 0.00424
𝐾_(𝑅𝑅𝑅𝑉−I)tr | 0.012679 | 0.011842 | 0.011636 | 0.0074224 | 0.0069344 | 0.0056722 | 0.0053106 | 0.0043046
𝐾_(𝑅𝑅𝑅𝑉−I)bl | 0.011723 | 0.011071 | 0.010914 | 0.0076554 | 0.0071104 | 0.0060056 | 0.0057823 | 0.0047208
𝐾_(𝑅𝑅𝑅𝑉−I)br | 0.011635 | 0.010997 | 0.010812 | 0.0076666 | 0.0070982 | 0.0060346 | 0.005861 | 0.0048342
𝐾_(𝑅𝑅𝑅𝑉−I)lm | 0.011723 | 0.011071 | 0.010914 | 0.0076554 | 0.0071104 | 0.0060056 | 0.0057823 | 0.0047208
𝐾_(𝑅𝑅𝑅𝑉−I)rm | 0.011635 | 0.010997 | 0.010812 | 0.0076666 | 0.0070982 | 0.0060346 | 0.005861 | 0.0048342
𝐾_(𝑅𝑅𝑅𝑉−I)tm | 0.012679 | 0.011842 | 0.011636 | 0.0074224 | 0.0069344 | 0.0056722 | 0.0053106 | 0.0043046
𝐾_(𝑅𝑅𝑅𝑉−I)bm | 0.011635 | 0.010997 | 0.010812 | 0.0076666 | 0.0070982 | 0.0060346 | 0.005861 | 0.0048342
𝐾_(𝑅𝑅𝑅𝑉−I) | 0.011635 | 0.010997 | 0.010812 | 0.0076666 | 0.0070982 | 0.0060346 | 0.005861 | 0.0048342
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
td0avrg | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0tl | 3.0499 | 2.8845 | 2.836 | 2.5465 | 2.3448 | 2.1528 | 2.1363 | 1.9994
td0tr | 3.1037 | 2.9363 | 2.8853 | 2.5945 | 2.3831 | 2.1847 | 2.1686 | 2.0279
td0bl | 4.2742 | 4.0733 | 3.9446 | 3.5554 | 3.265 | 2.9922 | 2.9369 | 2.7457
td0br | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0lm | 4.2742 | 4.0733 | 3.9446 | 3.5554 | 3.265 | 2.9922 | 2.9369 | 2.7457
td0rm | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0tm | 3.1037 | 2.9363 | 2.8853 | 2.5945 | 2.3831 | 2.1847 | 2.1686 | 2.0279
td0bm | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0 | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑡𝑑−𝑈)avrg | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)tl | 0.053875 | 0.042893 | 0.03495 | 0.015041 | 0.019194 | 0.003071 | 0.012747 | 0.010194
𝐾_(𝑡𝑑−𝑈)tr | 0.059239 | 0.046612 | 0.037059 | 0.016065 | 0.021049 | 0.0050557 | 0.014075 | 0.010983
𝐾_(𝑡𝑑−𝑈)bl | 0.094002 | 0.076052 | 0.068783 | 0.036052 | 0.042832 | 0.016956 | 0.030948 | 0.022369
𝐾_(𝑡𝑑−𝑈)br | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)lm | 0.094002 | 0.076052 | 0.068783 | 0.036052 | 0.042832 | 0.016956 | 0.030948 | 0.022369
𝐾_(𝑡𝑑−𝑈)rm | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)tm | 0.059239 | 0.046612 | 0.037059 | 0.016065 | 0.021049 | 0.0050557 | 0.014075 | 0.010983
𝐾_(𝑡𝑑−𝑈)bm | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈) | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑡𝑑−𝐼)avrg | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)tl | -0.037012 | -0.029125 | -0.020052 | -0.012582 | -0.0092115 | -0.0071505 | -0.0067292 | -0.0048972
𝐾_(𝑡𝑑−𝐼)tr | -0.037654 | -0.02932 | -0.020373 | -0.012842 | -0.0094223 | -0.0073457 | -0.0066908 | -0.0047844
𝐾_(𝑡𝑑−𝐼)bl | -0.053741 | -0.042351 | -0.029098 | -0.018636 | -0.014454 | -0.011197 | -0.010058 | -0.007383
𝐾_(𝑡𝑑−𝐼)br | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)lm | -0.053741 | -0.042351 | -0.029098 | -0.018636 | -0.014454 | -0.011197 | -0.010058 | -0.007383
𝐾_(𝑡𝑑−𝐼)rm | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)tm | -0.037654 | -0.02932 | -0.020373 | -0.012842 | -0.0094223 | -0.0073457 | -0.0066908 | -0.0047844
𝐾_(𝑡𝑑−𝐼)bm | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼) | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713

## Intermediate calculations_LS>= (hidden)
Class | 51-100 MVA
Rated voltage (kV) | 20
Symmetrical component of the rated system-source short-circuit breaking current (kA) | 50
Rated load breaking current (kA) | 5
Capacitance value per phase installed phase to earth at the generator-side of the generator circuit-breaker (µF) | 0.1
Capacitance value per phase installed phase to earth at the transformer-side of the generator circuit-breaker (µF) | 0.1
Load current breaking
Peak value of the standard TRV modified by the capacitors of the generator circuit-breaker (kV) | 22.4844 | 22.4844 | 0
Rate of rise of the standard TRV modified by the capacitors of the generator circuit-breaker (kV/µs) | 0.49946 | 0.49946 | 0
Time delay of the standard TRV modified by the capacitors of the generator circuit-breaker (µs) | 5.2665 | 5.2665 | 0
Cs | 0.1
Cst | 0.05
Csb | 0.1
Cg/Cs | 1
Cg/Csl | 0.9
Cg/Csr | 1
U_ref | 15.79 | 15.79
Isc_ref | 51.89 | 51.89
KE2 | 1.1242 | 1.1242
RRRV0 | 0.52707 | 0.46042
𝐾_(𝑅𝑅𝑅𝑉−𝑈) | 0.012362 | 0.010799
𝐾_(𝑅𝑅𝑅𝑉−I) | 0.0038881 | 0.0033964
td0 | 4.1103 | 4.7941
𝐾_(𝑡𝑑−𝑈) | 0.077295 | 0.090152
𝐾_(𝑡𝑑−𝐼) | -0.042148 | -0.049159
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
U_ref | 14.51 | 15.79 | 18.05 | 21.52 | 23.83 | 25.25 | 26.1 | 26.54
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
Isc_ref | 44.72 | 51.89 | 65.87 | 92.41 | 117.04 | 139.76 | 160.6 | 179.47
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
KE2avrg | 1.1261 | 1.1242 | 1.1174 | 1.0934 | 1.0961 | 1.0654 | 1.0784 | 1.0528
KE2tl | 1.1161 | 1.11 | 1.1006 | 1.0559 | 1.0567 | 1.0184 | 1.0411 | 1.0002
KE2tr | 1.1055 | 1.1002 | 1.0915 | 1.0509 | 1.052 | 1.0146 | 1.0378 | 0.99688
KE2bl | 1.1392 | 1.1369 | 1.1279 | 1.1038 | 1.1049 | 1.0724 | 1.0852 | 1.0594
KE2br | 1.1261 | 1.1242 | 1.1174 | 1.0934 | 1.0961 | 1.0654 | 1.0784 | 1.0528
KE2lm | 1.1392 | 1.1369 | 1.1279 | 1.1038 | 1.1049 | 1.0724 | 1.0852 | 1.0594
KE2rm | 1.1261 | 1.1242 | 1.1174 | 1.0934 | 1.0961 | 1.0654 | 1.0784 | 1.0528
KE2tm | 1.1055 | 1.1002 | 1.0915 | 1.0509 | 1.052 | 1.0146 | 1.0378 | 0.99688
KE2bm | 1.1261 | 1.1242 | 1.1174 | 1.0934 | 1.0961 | 1.0654 | 1.0784 | 1.0528
KE2 | 1.1261 | 1.1242 | 1.1174 | 1.0934 | 1.0961 | 1.0654 | 1.0784 | 1.0528
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
RRRV0avrg | 0.47032 | 0.52707 | 0.64322 | 0.76259 | 0.90196 | 0.94953 | 1.0683 | 1.0872
RRRV0tl | 0.61035 | 0.6822 | 0.83896 | 0.95022 | 1.1255 | 1.1565 | 1.3119 | 1.3141
RRRV0tr | 0.59727 | 0.66756 | 0.81983 | 0.93436 | 1.1063 | 1.1408 | 1.2915 | 1.2965
RRRV0bl | 0.48332 | 0.54168 | 0.66201 | 0.7803 | 0.923 | 0.96841 | 1.0914 | 1.1083
RRRV0br | 0.47032 | 0.52707 | 0.64322 | 0.76259 | 0.90196 | 0.94953 | 1.0683 | 1.0872
RRRV0lm | 0.48332 | 0.54168 | 0.66201 | 0.7803 | 0.923 | 0.96841 | 1.0914 | 1.1083
RRRV0rm | 0.47032 | 0.52707 | 0.64322 | 0.76259 | 0.90196 | 0.94953 | 1.0683 | 1.0872
RRRV0tm | 0.59727 | 0.66756 | 0.81983 | 0.93436 | 1.1063 | 1.1408 | 1.2915 | 1.2965
RRRV0bm | 0.47032 | 0.52707 | 0.64322 | 0.76259 | 0.90196 | 0.94953 | 1.0683 | 1.0872
RRRV0 | 0.47032 | 0.52707 | 0.64322 | 0.76259 | 0.90196 | 0.94953 | 1.0683 | 1.0872
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑅𝑅𝑅𝑉−𝑈)avrg | 0.012787 | 0.012362 | 0.013831 | 0.01104 | 0.012221 | 0.0085427 | 0.011144 | 0.01219
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tl | 0.013035 | 0.013162 | 0.015013 | 0.0098101 | 0.011607 | 0.0055883 | 0.008047 | 0.010346
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tr | 0.013209 | 0.013152 | 0.014994 | 0.010136 | 0.011825 | 0.0061953 | 0.0086098 | 0.010672
𝐾_(𝑅𝑅𝑅𝑉−𝑈)bl | 0.012781 | 0.012426 | 0.013993 | 0.010834 | 0.012137 | 0.0081363 | 0.010823 | 0.011983
𝐾_(𝑅𝑅𝑅𝑉−𝑈)br | 0.012787 | 0.012362 | 0.013831 | 0.01104 | 0.012221 | 0.0085427 | 0.011144 | 0.01219
𝐾_(𝑅𝑅𝑅𝑉−𝑈)lm | 0.012781 | 0.012426 | 0.013993 | 0.010834 | 0.012137 | 0.0081363 | 0.010823 | 0.011983
𝐾_(𝑅𝑅𝑅𝑉−𝑈)rm | 0.012787 | 0.012362 | 0.013831 | 0.01104 | 0.012221 | 0.0085427 | 0.011144 | 0.01219
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tm | 0.013209 | 0.013152 | 0.014994 | 0.010136 | 0.011825 | 0.0061953 | 0.0086098 | 0.010672
𝐾_(𝑅𝑅𝑅𝑉−𝑈)bm | 0.012787 | 0.012362 | 0.013831 | 0.01104 | 0.012221 | 0.0085427 | 0.011144 | 0.01219
𝐾_(𝑅𝑅𝑅𝑉−𝑈) | 0.012787 | 0.012362 | 0.013831 | 0.01104 | 0.012221 | 0.0085427 | 0.011144 | 0.01219
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑅𝑅𝑅𝑉−I)avrg | 0.0041135 | 0.0038881 | 0.0038227 | 0.0027105 | 0.0025096 | 0.0021335 | 0.0020722 | 0.0017091
𝐾_(𝑅𝑅𝑅𝑉−I)tl | 0.0044755 | 0.0041724 | 0.004103 | 0.0025778 | 0.0024085 | 0.0019705 | 0.0018514 | 0.0014991
𝐾_(𝑅𝑅𝑅𝑉−I)tr | 0.0044826 | 0.0041868 | 0.0041138 | 0.0026242 | 0.0024517 | 0.0020054 | 0.0018776 | 0.0015219
𝐾_(𝑅𝑅𝑅𝑉−I)bl | 0.0041447 | 0.0039142 | 0.0038587 | 0.0027066 | 0.0025139 | 0.0021233 | 0.0020444 | 0.0016691
𝐾_(𝑅𝑅𝑅𝑉−I)br | 0.0041135 | 0.0038881 | 0.0038227 | 0.0027105 | 0.0025096 | 0.0021335 | 0.0020722 | 0.0017091
𝐾_(𝑅𝑅𝑅𝑉−I)lm | 0.0041447 | 0.0039142 | 0.0038587 | 0.0027066 | 0.0025139 | 0.0021233 | 0.0020444 | 0.0016691
𝐾_(𝑅𝑅𝑅𝑉−I)rm | 0.0041135 | 0.0038881 | 0.0038227 | 0.0027105 | 0.0025096 | 0.0021335 | 0.0020722 | 0.0017091
𝐾_(𝑅𝑅𝑅𝑉−I)tm | 0.0044826 | 0.0041868 | 0.0041138 | 0.0026242 | 0.0024517 | 0.0020054 | 0.0018776 | 0.0015219
𝐾_(𝑅𝑅𝑅𝑉−I)bm | 0.0041135 | 0.0038881 | 0.0038227 | 0.0027105 | 0.0025096 | 0.0021335 | 0.0020722 | 0.0017091
𝐾_(𝑅𝑅𝑅𝑉−I) | 0.0041135 | 0.0038881 | 0.0038227 | 0.0027105 | 0.0025096 | 0.0021335 | 0.0020722 | 0.0017091
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
td0avrg | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0tl | 3.0499 | 2.8845 | 2.836 | 2.5465 | 2.3448 | 2.1528 | 2.1363 | 1.9994
td0tr | 3.1037 | 2.9363 | 2.8853 | 2.5945 | 2.3831 | 2.1847 | 2.1686 | 2.0279
td0bl | 4.2742 | 4.0733 | 3.9446 | 3.5554 | 3.265 | 2.9922 | 2.9369 | 2.7457
td0br | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0lm | 4.2742 | 4.0733 | 3.9446 | 3.5554 | 3.265 | 2.9922 | 2.9369 | 2.7457
td0rm | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0tm | 3.1037 | 2.9363 | 2.8853 | 2.5945 | 2.3831 | 2.1847 | 2.1686 | 2.0279
td0bm | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0 | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑡𝑑−𝑈)avrg | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)tl | 0.053875 | 0.042893 | 0.03495 | 0.015041 | 0.019194 | 0.003071 | 0.012747 | 0.010194
𝐾_(𝑡𝑑−𝑈)tr | 0.059239 | 0.046612 | 0.037059 | 0.016065 | 0.021049 | 0.0050557 | 0.014075 | 0.010983
𝐾_(𝑡𝑑−𝑈)bl | 0.094002 | 0.076052 | 0.068783 | 0.036052 | 0.042832 | 0.016956 | 0.030948 | 0.022369
𝐾_(𝑡𝑑−𝑈)br | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)lm | 0.094002 | 0.076052 | 0.068783 | 0.036052 | 0.042832 | 0.016956 | 0.030948 | 0.022369
𝐾_(𝑡𝑑−𝑈)rm | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)tm | 0.059239 | 0.046612 | 0.037059 | 0.016065 | 0.021049 | 0.0050557 | 0.014075 | 0.010983
𝐾_(𝑡𝑑−𝑈)bm | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈) | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑡𝑑−𝐼)avrg | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)tl | -0.037012 | -0.029125 | -0.020052 | -0.012582 | -0.0092115 | -0.0071505 | -0.0067292 | -0.0048972
𝐾_(𝑡𝑑−𝐼)tr | -0.037654 | -0.02932 | -0.020373 | -0.012842 | -0.0094223 | -0.0073457 | -0.0066908 | -0.0047844
𝐾_(𝑡𝑑−𝐼)bl | -0.053741 | -0.042351 | -0.029098 | -0.018636 | -0.014454 | -0.011197 | -0.010058 | -0.007383
𝐾_(𝑡𝑑−𝐼)br | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)lm | -0.053741 | -0.042351 | -0.029098 | -0.018636 | -0.014454 | -0.011197 | -0.010058 | -0.007383
𝐾_(𝑡𝑑−𝐼)rm | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)tm | -0.037654 | -0.02932 | -0.020373 | -0.012842 | -0.0094223 | -0.0073457 | -0.0066908 | -0.0047844
𝐾_(𝑡𝑑−𝐼)bm | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼) | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713

## CLASS1_OOP (hidden)
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
| 0.05 | 2.919 | 3.0345 | 3.1264 | 3.1846 | 3.2145 | 3.2238 | 3.2186 | 3.2034 | 3.1812 | 3.1543 | 3.1242
| 0.1 | 2.9263 | 3.0555 | 3.1835 | 3.2689 | 3.3062 | 3.3144 | 3.3043 | 3.2826 | 3.2535 | 3.2194 | 3.1824
| 0.15 | 2.8778 | 3.0559 | 3.1974 | 3.2806 | 3.3255 | 3.3374 | 3.3293 | 3.3084 | 3.2793 | 3.2448 | 3.2068
| 0.2 | 2.817 | 3.0321 | 3.2031 | 3.2897 | 3.3335 | 3.3514 | 3.3466 | 3.3271 | 3.298 | 3.2627 | 3.2237
| 0.25 | 2.7474 | 3.0056 | 3.1978 | 3.2934 | 3.3419 | 3.3639 | 3.3602 | 3.3403 | 3.3104 | 3.2742 | 3.2341
| 0.3 | 2.6786 | 2.9875 | 3.1894 | 3.293 | 3.3501 | 3.3733 | 3.3694 | 3.349 | 3.3185 | 3.2817 | 3.241
| 0.35 | 2.6147 | 2.9699 | 3.1806 | 3.2909 | 3.3562 | 3.3797 | 3.3756 | 3.355 | 3.3242 | 3.2872 | 3.2464
| 0.4 | 2.557 | 2.9536 | 3.1721 | 3.2888 | 3.3604 | 3.384 | 3.3801 | 3.3596 | 3.329 | 3.2919 | 3.2509
| 0.45 | 2.5055 | 2.9389 | 3.1641 | 3.2909 | 3.3631 | 3.3872 | 3.3838 | 3.3637 | 3.3331 | 3.2959 | 3.2547
| 0.5 | 2.4596 | 2.9257 | 3.1569 | 3.2922 | 3.3651 | 3.3901 | 3.3872 | 3.3672 | 3.3366 | 3.2993 | 3.2578
| 0.55 | 2.4188 | 2.9139 | 3.1515 | 3.2929 | 3.3668 | 3.3927 | 3.3902 | 3.3703 | 3.3396 | 3.302 | 3.2604
| 0.6 | 2.3826 | 2.9033 | 3.1468 | 3.2933 | 3.3684 | 3.3951 | 3.3929 | 3.3729 | 3.342 | 3.3044 | 3.2626
| 0.65 | 2.3501 | 2.8937 | 3.1428 | 3.2946 | 3.3701 | 3.3973 | 3.3952 | 3.3751 | 3.3441 | 3.3064 | 3.2647
| 0.7 | 2.3211 | 2.8849 | 3.1407 | 3.2966 | 3.3716 | 3.3993 | 3.3971 | 3.377 | 3.346 | 3.3082 | 3.267
| 0.75 | 2.2949 | 2.8769 | 3.1396 | 3.2982 | 3.3731 | 3.4009 | 3.3987 | 3.3787 | 3.3477 | 3.3099 | 3.2692
| 0.8 | 2.2713 | 2.8695 | 3.1391 | 3.2993 | 3.3744 | 3.4023 | 3.4002 | 3.3802 | 3.3492 | 3.3114 | 3.2711
| 0.85 | 2.2498 | 2.8627 | 3.1391 | 3.3001 | 3.373 | 3.4036 | 3.4016 | 3.3817 | 3.3506 | 3.3127 | 3.2728
| 0.9 | 2.2303 | 2.8564 | 3.1392 | 3.3006 | 3.3725 | 3.4047 | 3.4029 | 3.383 | 3.3519 | 3.3139 | 3.2744
| 0.95 | 2.2125 | 2.8505 | 3.1392 | 3.3009 | 3.3732 | 3.4057 | 3.404 | 3.3842 | 3.3531 | 3.3154 | 3.2758
| 1 | 2.1961 | 2.845 | 3.1392 | 3.301 | 3.3739 | 3.4067 | 3.4051 | 3.3853 | 3.3541 | 3.3168 | 3.2771
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| 0.05 | 2.159 | 2.1052 | 2.0509 | 1.9972 | 1.9461 | 1.8968 | 1.8511 | 1.8073 | 1.7655 | 1.7263 | 1.6893
| 0.1 | 1.894 | 1.8063 | 1.7299 | 1.6629 | 1.6025 | 1.5473 | 1.4968 | 1.4502 | 1.407 | 1.367 | 1.3303
| 0.15 | 1.7586 | 1.6319 | 1.5433 | 1.4718 | 1.4083 | 1.3517 | 1.3007 | 1.254 | 1.2116 | 1.173 | 1.1382
| 0.2 | 1.6796 | 1.5133 | 1.4168 | 1.3426 | 1.2771 | 1.2184 | 1.1672 | 1.1213 | 1.0799 | 1.0437 | 1.0104
| 0.25 | 1.627 | 1.4247 | 1.3237 | 1.2447 | 1.1765 | 1.1175 | 1.0671 | 1.0223 | 0.9834 | 0.94848 | 0.91718
| 0.3 | 1.5912 | 1.3546 | 1.2494 | 1.1652 | 1.0958 | 1.0375 | 0.98811 | 0.94516 | 0.908 | 0.87518 | 0.84543
| 0.35 | 1.5637 | 1.2981 | 1.1861 | 1.0988 | 1.0289 | 0.9715 | 0.92423 | 0.8829 | 0.84764 | 0.81636 | 0.78843
| 0.4 | 1.5436 | 1.2497 | 1.1319 | 1.0424 | 0.97248 | 0.9173 | 0.87108 | 0.83195 | 0.79758 | 0.76769 | 0.74137
| 0.45 | 1.5269 | 1.2084 | 1.0841 | 0.99322 | 0.92446 | 0.87043 | 0.82589 | 0.78827 | 0.75551 | 0.72691 | 0.70188
| 0.5 | 1.514 | 1.172 | 1.0419 | 0.95026 | 0.88263 | 0.83018 | 0.78733 | 0.75099 | 0.72003 | 0.69236 | 0.66838
| 0.55 | 1.5025 | 1.1389 | 1.0032 | 0.91194 | 0.84618 | 0.79482 | 0.75353 | 0.7187 | 0.68886 | 0.66218 | 0.63891
| 0.6 | 1.494 | 1.1088 | 0.96887 | 0.87837 | 0.81365 | 0.76408 | 0.72416 | 0.6902 | 0.66109 | 0.6361 | 0.61378
| 0.65 | 1.4856 | 1.0811 | 0.93782 | 0.84769 | 0.78462 | 0.7369 | 0.69748 | 0.66484 | 0.63671 | 0.61262 | 0.59094
| 0.7 | 1.4794 | 1.0552 | 0.90918 | 0.82031 | 0.75863 | 0.71167 | 0.67394 | 0.64216 | 0.61533 | 0.5913 | 0.5706
| 0.75 | 1.4731 | 1.0311 | 0.88304 | 0.7954 | 0.73511 | 0.68946 | 0.65284 | 0.62179 | 0.59548 | 0.57257 | 0.55228
| 0.8 | 1.4684 | 1.0083 | 0.85884 | 0.77242 | 0.71352 | 0.66908 | 0.63355 | 0.60335 | 0.57765 | 0.55525 | 0.53554
| 0.85 | 1.4644 | 0.98721 | 0.83661 | 0.75114 | 0.69361 | 0.65053 | 0.61532 | 0.58637 | 0.56107 | 0.5393 | 0.52001
| 0.9 | 1.4597 | 0.96721 | 0.81581 | 0.73204 | 0.67576 | 0.63343 | 0.5993 | 0.5706 | 0.54622 | 0.52489 | 0.50608
| 0.95 | 1.4565 | 0.94829 | 0.79689 | 0.714 | 0.65912 | 0.61754 | 0.584 | 0.55633 | 0.53252 | 0.51118 | 0.49321
| 1 | 1.4529 | 0.93039 | 0.77921 | 0.69713 | 0.64372 | 0.60257 | 0.56973 | 0.54258 | 0.51929 | 0.49892 | 0.48108
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.01958 | 0.024051 | 0.027236 | 0.029892 | 0.031757 | 0.033267 | 0.034563 | 0.035505 | 0.0363 | 0.036867 | 0.037361
| 0.1 | 0.014607 | 0.024433 | 0.028646 | 0.031388 | 0.033181 | 0.034605 | 0.035312 | 0.035856 | 0.03611 | 0.03615 | 0.036167
| 0.15 | 0.010328 | 0.023708 | 0.028677 | 0.031923 | 0.033758 | 0.034624 | 0.035072 | 0.034959 | 0.034725 | 0.034493 | 0.034016
| 0.2 | 0.006887 | 0.023446 | 0.029314 | 0.032428 | 0.033786 | 0.034078 | 0.033981 | 0.033587 | 0.03308 | 0.032512 | 0.031872
| 0.25 | 0.0047019 | 0.023203 | 0.029803 | 0.032387 | 0.033271 | 0.033214 | 0.03267 | 0.031995 | 0.031366 | 0.030564 | 0.029839
| 0.3 | 0.0031626 | 0.023455 | 0.030108 | 0.032245 | 0.032587 | 0.031993 | 0.031256 | 0.030505 | 0.02964 | 0.028754 | 0.028108
| 0.35 | 0.0019406 | 0.023737 | 0.030224 | 0.031834 | 0.031536 | 0.030934 | 0.029955 | 0.028983 | 0.028113 | 0.027322 | 0.026557
| 0.4 | 0.0011126 | 0.024112 | 0.030231 | 0.031156 | 0.030561 | 0.029732 | 0.028645 | 0.027631 | 0.026806 | 0.025911 | 0.025191
| 0.45 | 0.000346 | 0.02446 | 0.029998 | 0.030481 | 0.029638 | 0.028554 | 0.027432 | 0.026457 | 0.025637 | 0.02483 | 0.024072
| 0.5 | -0.00045512 | 0.024896 | 0.029726 | 0.02984 | 0.028773 | 0.027504 | 0.026471 | 0.025355 | 0.024496 | 0.023731 | 0.023031
| 0.55 | -0.0009025 | 0.02519 | 0.029427 | 0.029049 | 0.02787 | 0.026622 | 0.025507 | 0.024476 | 0.023593 | 0.022854 | 0.022148
| 0.6 | -0.0013167 | 0.025409 | 0.028977 | 0.028366 | 0.026997 | 0.025757 | 0.024576 | 0.023692 | 0.022781 | 0.02198 | 0.021329
| 0.65 | -0.0015931 | 0.025612 | 0.028627 | 0.027578 | 0.026225 | 0.025052 | 0.023927 | 0.022895 | 0.022045 | 0.021239 | 0.020601
| 0.7 | -0.0019167 | 0.025739 | 0.028227 | 0.026899 | 0.025538 | 0.0242 | 0.023131 | 0.022191 | 0.021458 | 0.020686 | 0.019934
| 0.75 | -0.0023889 | 0.025824 | 0.027658 | 0.026333 | 0.024877 | 0.023649 | 0.022546 | 0.021595 | 0.020821 | 0.019944 | 0.01936
| 0.8 | -0.002342 | 0.025905 | 0.027234 | 0.025734 | 0.024226 | 0.023011 | 0.021898 | 0.021076 | 0.020233 | 0.019499 | 0.018832
| 0.85 | -0.0027417 | 0.025925 | 0.026757 | 0.025215 | 0.023642 | 0.022472 | 0.021309 | 0.020469 | 0.019611 | 0.018974 | 0.018288
| 0.9 | -0.0025954 | 0.02583 | 0.026342 | 0.024634 | 0.023146 | 0.02196 | 0.020886 | 0.019974 | 0.019254 | 0.018498 | 0.017831
| 0.95 | -0.0030241 | 0.025849 | 0.025927 | 0.024125 | 0.0227 | 0.021462 | 0.020458 | 0.019579 | 0.018686 | 0.018062 | 0.017365
| 1 | -0.0031526 | 0.02576 | 0.025483 | 0.023641 | 0.022273 | 0.021018 | 0.020031 | 0.019132 | 0.018354 | 0.017582 | 0.016969
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0098232 | 0.010638 | 0.011226 | 0.011647 | 0.011958 | 0.012194 | 0.012392 | 0.012509 | 0.012609 | 0.012659 | 0.012679
| 0.1 | 0.0088065 | 0.010729 | 0.011353 | 0.011622 | 0.011782 | 0.011868 | 0.011914 | 0.011882 | 0.011833 | 0.011723 | 0.011635
| 0.15 | 0.0073973 | 0.010295 | 0.010867 | 0.011161 | 0.011306 | 0.011354 | 0.011308 | 0.011199 | 0.011042 | 0.010896 | 0.010716
| 0.2 | 0.0062821 | 0.0098392 | 0.010496 | 0.010846 | 0.010954 | 0.010901 | 0.010774 | 0.01059 | 0.010387 | 0.010166 | 0.0099695
| 0.25 | 0.0054744 | 0.0094964 | 0.010245 | 0.010601 | 0.010618 | 0.01049 | 0.010277 | 0.010028 | 0.0097863 | 0.0095464 | 0.0093135
| 0.3 | 0.0048766 | 0.0092238 | 0.010084 | 0.010362 | 0.010286 | 0.010062 | 0.0097956 | 0.0095191 | 0.0092501 | 0.0089931 | 0.0087488
| 0.35 | 0.0043513 | 0.0090517 | 0.0099455 | 0.010113 | 0.0099317 | 0.0096553 | 0.0093544 | 0.0090555 | 0.0087768 | 0.0085158 | 0.0082698
| 0.4 | 0.0039868 | 0.0089022 | 0.0098153 | 0.0098641 | 0.0096053 | 0.0092676 | 0.008949 | 0.0086408 | 0.0083556 | 0.0080926 | 0.007853
| 0.45 | 0.00369 | 0.0088208 | 0.0096638 | 0.0095926 | 0.0092861 | 0.0089249 | 0.0085804 | 0.0082622 | 0.0079844 | 0.0077287 | 0.0074854
| 0.5 | 0.0034244 | 0.0087621 | 0.0095139 | 0.0093392 | 0.0089824 | 0.0085933 | 0.0082573 | 0.0079234 | 0.0076601 | 0.0074018 | 0.0071659
| 0.55 | 0.0032242 | 0.0087146 | 0.0093527 | 0.0091028 | 0.0086914 | 0.0083005 | 0.007951 | 0.0076328 | 0.0073578 | 0.0071077 | 0.0068927
| 0.6 | 0.0030601 | 0.0086756 | 0.0091977 | 0.0088634 | 0.0084328 | 0.00803 | 0.0076849 | 0.0073775 | 0.0070954 | 0.0068547 | 0.0066412
| 0.65 | 0.0028639 | 0.0086433 | 0.0090321 | 0.0086368 | 0.0081896 | 0.0077866 | 0.0074438 | 0.0071393 | 0.0068676 | 0.0066381 | 0.0064184
| 0.7 | 0.0027391 | 0.0086102 | 0.0088689 | 0.008427 | 0.0079617 | 0.0075566 | 0.0072177 | 0.006918 | 0.0066652 | 0.0064266 | 0.0062165
| 0.75 | 0.0026388 | 0.0085639 | 0.0086964 | 0.0082217 | 0.0077511 | 0.0073602 | 0.0070092 | 0.006718 | 0.0064622 | 0.0062385 | 0.0060342
| 0.8 | 0.0025168 | 0.0085307 | 0.0085494 | 0.0080467 | 0.0075576 | 0.0071604 | 0.006826 | 0.0065395 | 0.0062867 | 0.0060696 | 0.0058673
| 0.85 | 0.0024432 | 0.0084789 | 0.0083971 | 0.0078513 | 0.0073709 | 0.0069901 | 0.0066535 | 0.0063745 | 0.0061295 | 0.0058974 | 0.0057095
| 0.9 | 0.0023704 | 0.0084354 | 0.0082551 | 0.0076822 | 0.0072013 | 0.006827 | 0.006487 | 0.0062177 | 0.0059651 | 0.0057569 | 0.0055632
| 0.95 | 0.0022826 | 0.0083678 | 0.008111 | 0.0075256 | 0.007057 | 0.0066715 | 0.0063488 | 0.0060808 | 0.0058363 | 0.0056223 | 0.0054298
| 1 | 0.0022026 | 0.0083166 | 0.0079607 | 0.0073722 | 0.0069023 | 0.006536 | 0.0062042 | 0.0059392 | 0.0056961 | 0.005493 | 0.0053182
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.3486 | 1.7582 | 2.0798 | 2.3281 | 2.5262 | 2.6797 | 2.8051 | 2.9109 | 2.9806 | 3.0499 | 3.1037
| 0.1 | 1.2327 | 2.109 | 2.7084 | 3.1577 | 3.495 | 3.738 | 3.9091 | 4.0851 | 4.2268 | 4.2742 | 4.3458
| 0.15 | 1.1207 | 2.4089 | 3.2492 | 3.7122 | 4.4173 | 4.5317 | 4.7553 | 4.9508 | 5.0726 | 5.0754 | 5.2976
| 0.2 | 1.0371 | 2.6864 | 3.6607 | 4.391 | 4.8916 | 5.2267 | 5.5418 | 5.7515 | 5.903 | 6.0266 | 6.1206
| 0.25 | 0.98632 | 2.979 | 4.096 | 4.8996 | 5.4722 | 5.872 | 6.1739 | 6.403 | 6.576 | 6.7191 | 6.8153
| 0.3 | 0.89171 | 3.1924 | 4.4682 | 5.3652 | 5.9726 | 6.415 | 6.7468 | 7.0045 | 7.1905 | 7.3422 | 7.4416
| 0.35 | 0.93618 | 3.4057 | 4.8565 | 5.7777 | 6.4235 | 6.9086 | 7.268 | 7.5343 | 7.7471 | 7.8953 | 8.0179
| 0.4 | 0.89506 | 3.6327 | 5.1788 | 6.1606 | 6.8556 | 7.3679 | 7.7457 | 8.0366 | 8.2556 | 8.4195 | 8.5446
| 0.45 | 0.88473 | 3.8457 | 5.477 | 6.511 | 7.25 | 7.7885 | 8.1912 | 8.5013 | 8.7409 | 8.9131 | 9.0483
| 0.5 | 0.86821 | 4.0487 | 5.7585 | 6.8538 | 7.6189 | 8.1866 | 8.6162 | 8.9428 | 9.1916 | 9.3744 | 9.5285
| 0.55 | 0.863 | 4.2322 | 6.0239 | 7.1582 | 7.9677 | 8.5612 | 9.0174 | 9.3652 | 9.628 | 9.82 | 9.969
| 0.6 | 0.85095 | 4.435 | 6.2708 | 7.4538 | 8.293 | 8.9233 | 9.4052 | 9.7644 | 10.0403 | 10.2544 | 10.4138
| 0.65 | 0.85074 | 4.6037 | 6.507 | 7.7319 | 8.6091 | 9.2794 | 9.7695 | 10.149 | 10.4373 | 10.6641 | 10.82
| 0.7 | 0.84087 | 4.7783 | 6.7379 | 8.0002 | 8.9161 | 9.6038 | 10.1292 | 10.5244 | 10.8203 | 11.0448 | 11.225
| 0.75 | 0.83918 | 4.9388 | 6.9515 | 8.2707 | 9.2132 | 9.9286 | 10.4742 | 10.8839 | 11.1893 | 11.4329 | 11.6154
| 0.8 | 0.82983 | 5.1071 | 7.1525 | 8.5136 | 9.5086 | 10.2406 | 10.8091 | 11.2249 | 11.5518 | 11.7995 | 11.9792
| 0.85 | 0.82459 | 5.2633 | 7.361 | 8.7562 | 9.7822 | 10.5446 | 11.1224 | 11.5618 | 11.8951 | 12.1454 | 12.3391
| 0.9 | 0.82416 | 5.4006 | 7.5518 | 8.9929 | 10.0524 | 10.8397 | 11.4417 | 11.8858 | 12.2368 | 12.4937 | 12.6932
| 0.95 | 0.81627 | 5.5543 | 7.7412 | 9.2269 | 10.3147 | 11.1227 | 11.7424 | 12.2097 | 12.562 | 12.8224 | 13.0307
| 1 | 0.8193 | 5.6889 | 7.9276 | 9.4463 | 10.5747 | 11.3969 | 12.0304 | 12.5105 | 12.8715 | 13.1444 | 13.3616
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.016634 | 0.020505 | 0.025156 | 0.030727 | 0.035003 | 0.039266 | 0.043413 | 0.047056 | 0.050536 | 0.053875 | 0.059239
| 0.1 | 0.015004 | 0.030043 | 0.047296 | 0.060312 | 0.070347 | 0.074086 | 0.079918 | 0.084217 | 0.090582 | 0.094002 | 0.10012
| 0.15 | 0.0065987 | 0.038138 | 0.063182 | 0.080852 | 0.094706 | 0.10891 | 0.10999 | 0.12138 | 0.13063 | 0.13413 | 0.141
| 0.2 | 0.002924 | 0.048816 | 0.079067 | 0.10139 | 0.11907 | 0.13587 | 0.14855 | 0.15854 | 0.16604 | 0.17038 | 0.18187
| 0.25 | -0.00041602 | 0.055884 | 0.094953 | 0.12193 | 0.14342 | 0.16283 | 0.1808 | 0.18681 | 0.19221 | 0.20075 | 0.20221
| 0.3 | -0.0032475 | 0.062951 | 0.11084 | 0.14247 | 0.16778 | 0.18979 | 0.20126 | 0.20983 | 0.22073 | 0.22152 | 0.22628
| 0.35 | -0.0047683 | 0.070019 | 0.12615 | 0.15733 | 0.19214 | 0.21333 | 0.22296 | 0.23026 | 0.23988 | 0.24303 | 0.24692
| 0.4 | -0.0064421 | 0.077086 | 0.13886 | 0.186 | 0.20847 | 0.22883 | 0.23966 | 0.24754 | 0.25678 | 0.2622 | 0.26805
| 0.45 | -0.0085543 | 0.084153 | 0.16313 | 0.19764 | 0.22584 | 0.24305 | 0.25706 | 0.26686 | 0.27576 | 0.28121 | 0.28567
| 0.5 | -0.0073515 | 0.091221 | 0.17273 | 0.21157 | 0.2381 | 0.25811 | 0.27423 | 0.28492 | 0.29116 | 0.29789 | 0.30437
| 0.55 | -0.0090714 | 0.098288 | 0.17882 | 0.22655 | 0.25166 | 0.27339 | 0.28964 | 0.30027 | 0.30673 | 0.31515 | 0.32108
| 0.6 | -0.010071 | 0.10536 | 0.18958 | 0.23582 | 0.2639 | 0.28686 | 0.3024 | 0.31684 | 0.32291 | 0.3276 | 0.33526
| 0.65 | -0.010687 | 0.11242 | 0.19739 | 0.24948 | 0.27584 | 0.30128 | 0.31894 | 0.33051 | 0.3381 | 0.3444 | 0.35217
| 0.7 | -0.011484 | 0.11949 | 0.21227 | 0.25926 | 0.28978 | 0.31128 | 0.32962 | 0.34144 | 0.35384 | 0.36163 | 0.36474
| 0.75 | -0.010223 | 0.12656 | 0.21897 | 0.2688 | 0.30121 | 0.32496 | 0.34334 | 0.35544 | 0.36746 | 0.3707 | 0.37794
| 0.8 | -0.012855 | 0.13363 | 0.22831 | 0.27727 | 0.31167 | 0.33655 | 0.35468 | 0.37008 | 0.37816 | 0.38678 | 0.39317
| 0.85 | -0.01144 | 0.1421 | 0.23414 | 0.28764 | 0.32154 | 0.34819 | 0.36588 | 0.38069 | 0.39096 | 0.40004 | 0.40549
| 0.9 | -0.014066 | 0.14439 | 0.2441 | 0.29565 | 0.33239 | 0.35905 | 0.37922 | 0.39277 | 0.40561 | 0.41294 | 0.41605
| 0.95 | -0.012752 | 0.15313 | 0.25127 | 0.30365 | 0.34186 | 0.3695 | 0.38999 | 0.40778 | 0.41486 | 0.42469 | 0.42973
| 1 | -0.013227 | 0.15839 | 0.25838 | 0.31251 | 0.35145 | 0.38006 | 0.40093 | 0.41646 | 0.42744 | 0.43268 | 0.43994
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0021579 | -0.010444 | -0.018906 | -0.024147 | -0.028715 | -0.031507 | -0.033327 | -0.034946 | -0.037251 | -0.037012 | -0.037654
| 0.1 | 0.0052353 | -0.01602 | -0.029631 | -0.038613 | -0.041966 | -0.04476 | -0.049242 | -0.051672 | -0.052768 | -0.053741 | -0.054739
| 0.15 | 0.0053041 | -0.021873 | -0.036731 | -0.046836 | -0.053279 | -0.056669 | -0.060208 | -0.061157 | -0.064164 | -0.065061 | -0.066244
| 0.2 | 0.0050167 | -0.026913 | -0.044117 | -0.053311 | -0.060768 | -0.065742 | -0.069155 | -0.070641 | -0.074102 | -0.076382 | -0.077095
| 0.25 | 0.0044098 | -0.030737 | -0.049151 | -0.060112 | -0.069342 | -0.072318 | -0.076169 | -0.080126 | -0.082729 | -0.083526 | -0.085097
| 0.3 | 0.0038897 | -0.03648 | -0.054662 | -0.065412 | -0.072874 | -0.078587 | -0.083182 | -0.086462 | -0.089264 | -0.090983 | -0.0927
| 0.35 | 0.0038238 | -0.040223 | -0.058432 | -0.069506 | -0.078068 | -0.084346 | -0.089502 | -0.093411 | -0.096101 | -0.098168 | -0.099966
| 0.4 | 0.003435 | -0.046421 | -0.062135 | -0.07389 | -0.082948 | -0.089912 | -0.095906 | -0.099583 | -0.10268 | -0.10481 | -0.10695
| 0.45 | 0.0031154 | -0.047776 | -0.065328 | -0.07788 | -0.087845 | -0.095327 | -0.1013 | -0.10596 | -0.10872 | -0.11126 | -0.11324
| 0.5 | 0.0029879 | -0.049131 | -0.068372 | -0.081744 | -0.092323 | -0.10018 | -0.10653 | -0.11121 | -0.11463 | -0.11745 | -0.11916
| 0.55 | 0.0027116 | -0.053257 | -0.071085 | -0.085554 | -0.096959 | -0.10509 | -0.11189 | -0.11643 | -0.12024 | -0.1231 | -0.12496
| 0.6 | 0.0024662 | -0.054885 | -0.074213 | -0.08915 | -0.1006 | -0.10976 | -0.11643 | -0.12184 | -0.12559 | -0.1285 | -0.13064
| 0.65 | 0.0026991 | -0.056264 | -0.077163 | -0.092576 | -0.10475 | -0.11399 | -0.12105 | -0.12651 | -0.13046 | -0.13328 | -0.13577
| 0.7 | 0.0024329 | -0.057695 | -0.079527 | -0.09598 | -0.10894 | -0.11842 | -0.12568 | -0.13135 | -0.13528 | -0.13838 | -0.14077
| 0.75 | 0.0022449 | -0.059669 | -0.081201 | -0.099164 | -0.11261 | -0.12259 | -0.13025 | -0.13602 | -0.1405 | -0.14324 | -0.14587
| 0.8 | 0.0022472 | -0.06121 | -0.084278 | -0.10235 | -0.11636 | -0.12667 | -0.13438 | -0.14024 | -0.14459 | -0.14791 | -0.15054
| 0.85 | 0.0021159 | -0.062752 | -0.087024 | -0.10571 | -0.1199 | -0.13038 | -0.13841 | -0.14428 | -0.14888 | -0.1526 | -0.15549
| 0.9 | 0.0019008 | -0.0645 | -0.089217 | -0.10877 | -0.12346 | -0.13402 | -0.14262 | -0.14851 | -0.1534 | -0.15697 | -0.15972
| 0.95 | 0.0019398 | -0.065951 | -0.091721 | -0.11181 | -0.12664 | -0.1377 | -0.14613 | -0.15228 | -0.15729 | -0.16102 | -0.16418
| 1 | 0.0020556 | -0.067112 | -0.093938 | -0.1148 | -0.13 | -0.14096 | -0.15002 | -0.15584 | -0.16166 | -0.16577 | -0.16788
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72)
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72)
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72)

## CLASS2_OOP (hidden)
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
| 0.05 | 2.9273 | 3.0302 | 3.1109 | 3.1628 | 3.1901 | 3.1992 | 3.1951 | 3.1817 | 3.1617 | 3.1371 | 3.1093
| 0.1 | 2.9356 | 3.0431 | 3.1768 | 3.258 | 3.2944 | 3.303 | 3.2939 | 3.2735 | 3.2456 | 3.2129 | 3.1772
| 0.15 | 2.9072 | 3.0502 | 3.1792 | 3.2776 | 3.3211 | 3.3325 | 3.3244 | 3.3038 | 3.2751 | 3.2413 | 3.2041
| 0.2 | 2.8464 | 3.045 | 3.1844 | 3.2808 | 3.332 | 3.3485 | 3.3432 | 3.3238 | 3.2953 | 3.2608 | 3.2226
| 0.25 | 2.7765 | 3.029 | 3.1916 | 3.2815 | 3.341 | 3.3618 | 3.3581 | 3.3388 | 3.3097 | 3.2742 | 3.2349
| 0.3 | 2.7076 | 3.0102 | 3.1927 | 3.2847 | 3.3497 | 3.3725 | 3.369 | 3.3493 | 3.3195 | 3.2833 | 3.2432
| 0.35 | 2.6436 | 2.992 | 3.1903 | 3.2884 | 3.3568 | 3.3804 | 3.3768 | 3.3567 | 3.3264 | 3.2899 | 3.2495
| 0.4 | 2.5858 | 2.9751 | 3.1862 | 3.2911 | 3.3622 | 3.3861 | 3.3824 | 3.3623 | 3.3319 | 3.2952 | 3.2546
| 0.45 | 2.5343 | 2.96 | 3.1812 | 3.2941 | 3.3661 | 3.3903 | 3.3869 | 3.3669 | 3.3366 | 3.2998 | 3.259
| 0.5 | 2.4885 | 2.9465 | 3.1759 | 3.2963 | 3.369 | 3.3937 | 3.3908 | 3.371 | 3.3406 | 3.3037 | 3.2627
| 0.55 | 2.4477 | 2.9344 | 3.1706 | 3.2978 | 3.3713 | 3.3968 | 3.3942 | 3.3746 | 3.3441 | 3.307 | 3.2658
| 0.6 | 2.4114 | 2.9236 | 3.1655 | 3.2988 | 3.3733 | 3.3996 | 3.3973 | 3.3777 | 3.3471 | 3.3098 | 3.2684
| 0.65 | 2.379 | 2.9137 | 3.1609 | 3.2995 | 3.3752 | 3.4021 | 3.4001 | 3.3804 | 3.3497 | 3.3123 | 3.2707
| 0.7 | 2.3499 | 2.9048 | 3.1568 | 3.3001 | 3.377 | 3.4044 | 3.4025 | 3.3827 | 3.352 | 3.3144 | 3.2728
| 0.75 | 2.3237 | 2.8966 | 3.1533 | 3.3008 | 3.3787 | 3.4065 | 3.4046 | 3.3848 | 3.354 | 3.3164 | 3.2746
| 0.8 | 2.3 | 2.889 | 3.1505 | 3.3014 | 3.3802 | 3.4083 | 3.4064 | 3.3866 | 3.3558 | 3.3181 | 3.2763
| 0.85 | 2.2786 | 2.882 | 3.1482 | 3.3021 | 3.3817 | 3.4099 | 3.4081 | 3.3883 | 3.3574 | 3.3198 | 3.2778
| 0.9 | 2.259 | 2.8755 | 3.1465 | 3.3029 | 3.383 | 3.4113 | 3.4096 | 3.3898 | 3.359 | 3.3212 | 3.2792
| 0.95 | 2.2411 | 2.8694 | 3.1453 | 3.3036 | 3.3841 | 3.4126 | 3.411 | 3.3913 | 3.3604 | 3.3226 | 3.2805
| 1 | 2.2248 | 2.8637 | 3.1445 | 3.3043 | 3.3852 | 3.4138 | 3.4123 | 3.3926 | 3.3617 | 3.3238 | 3.2817
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
| 0.05 | 2.4195 | 2.3559 | 2.2925 | 2.2319 | 2.1738 | 2.1188 | 2.0683 | 2.0189 | 1.9728 | 1.9295 | 1.8881
| 0.1 | 2.1255 | 2.0223 | 1.9366 | 1.8617 | 1.7943 | 1.733 | 1.6767 | 1.6248 | 1.5763 | 1.5321 | 1.4908
| 0.15 | 1.9744 | 1.828 | 1.7305 | 1.6502 | 1.5793 | 1.515 | 1.4582 | 1.4058 | 1.3581 | 1.3152 | 1.2763
| 0.2 | 1.8861 | 1.6967 | 1.5899 | 1.5056 | 1.4309 | 1.3656 | 1.3079 | 1.2568 | 1.2113 | 1.1707 | 1.1334
| 0.25 | 1.8272 | 1.5984 | 1.4852 | 1.3949 | 1.3184 | 1.2527 | 1.1961 | 1.1464 | 1.103 | 1.0644 | 1.0293
| 0.3 | 1.7871 | 1.5205 | 1.4007 | 1.3054 | 1.2277 | 1.163 | 1.1084 | 1.0605 | 1.0191 | 0.98255 | 0.94952
| 0.35 | 1.756 | 1.4572 | 1.3297 | 1.2313 | 1.1534 | 1.0899 | 1.0372 | 0.99137 | 0.95173 | 0.91653 | 0.88593
| 0.4 | 1.7336 | 1.4039 | 1.2676 | 1.1678 | 1.0911 | 1.0289 | 0.97773 | 0.93398 | 0.896 | 0.86281 | 0.83303
| 0.45 | 1.7155 | 1.3568 | 1.2139 | 1.1131 | 1.037 | 0.97726 | 0.92774 | 0.88552 | 0.84951 | 0.81729 | 0.78918
| 0.5 | 1.7002 | 1.3153 | 1.1667 | 1.0653 | 0.99047 | 0.93208 | 0.88443 | 0.8441 | 0.80895 | 0.77868 | 0.75166
| 0.55 | 1.6883 | 1.2779 | 1.1236 | 1.0228 | 0.94971 | 0.89299 | 0.84701 | 0.8079 | 0.77426 | 0.74511 | 0.71872
| 0.6 | 1.6774 | 1.2433 | 1.0856 | 0.98513 | 0.91347 | 0.85823 | 0.8136 | 0.77604 | 0.74366 | 0.71528 | 0.69017
| 0.65 | 1.6691 | 1.212 | 1.0508 | 0.95109 | 0.88152 | 0.82751 | 0.78439 | 0.74764 | 0.71616 | 0.68893 | 0.66471
| 0.7 | 1.6609 | 1.1819 | 1.0189 | 0.92041 | 0.8521 | 0.80009 | 0.75801 | 0.72234 | 0.69195 | 0.66555 | 0.64215
| 0.75 | 1.6547 | 1.1548 | 0.99004 | 0.89229 | 0.82566 | 0.77498 | 0.73382 | 0.69973 | 0.66994 | 0.6441 | 0.62127
| 0.8 | 1.6482 | 1.1293 | 0.96299 | 0.86697 | 0.80185 | 0.75202 | 0.71197 | 0.67866 | 0.64954 | 0.62464 | 0.60241
| 0.85 | 1.6438 | 1.1054 | 0.93859 | 0.84389 | 0.77986 | 0.73144 | 0.69231 | 0.65944 | 0.63173 | 0.60686 | 0.58544
| 0.9 | 1.6399 | 1.0831 | 0.9151 | 0.82201 | 0.75949 | 0.71235 | 0.6742 | 0.64192 | 0.6144 | 0.5909 | 0.56951
| 0.95 | 1.6351 | 1.0618 | 0.894 | 0.80234 | 0.74073 | 0.69432 | 0.65688 | 0.62585 | 0.59927 | 0.57568 | 0.55504
| 1 | 1.6318 | 1.0414 | 0.87407 | 0.78347 | 0.72343 | 0.67811 | 0.64119 | 0.61084 | 0.58461 | 0.56166 | 0.54132
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.029332 | 0.031248 | 0.032875 | 0.03438 | 0.03521 | 0.035898 | 0.036516 | 0.036802 | 0.037189 | 0.037229 | 0.037199
| 0.1 | 0.027458 | 0.032141 | 0.033782 | 0.034663 | 0.035366 | 0.035701 | 0.035757 | 0.035643 | 0.035411 | 0.035145 | 0.034965
| 0.15 | 0.022741 | 0.031071 | 0.032626 | 0.033729 | 0.034329 | 0.034616 | 0.034575 | 0.034215 | 0.033743 | 0.03329 | 0.032747
| 0.2 | 0.019135 | 0.029554 | 0.0318 | 0.033164 | 0.033724 | 0.033857 | 0.033319 | 0.03269 | 0.0321 | 0.031426 | 0.030573
| 0.25 | 0.016451 | 0.028524 | 0.031441 | 0.032968 | 0.033147 | 0.032629 | 0.031943 | 0.031148 | 0.030336 | 0.029498 | 0.028741
| 0.3 | 0.014366 | 0.027804 | 0.031353 | 0.032457 | 0.032237 | 0.03154 | 0.030623 | 0.029614 | 0.028802 | 0.02794 | 0.027079
| 0.35 | 0.012517 | 0.02736 | 0.031131 | 0.03189 | 0.031283 | 0.030309 | 0.029368 | 0.028297 | 0.027254 | 0.026374 | 0.025646
| 0.4 | 0.011519 | 0.027164 | 0.030935 | 0.031142 | 0.03031 | 0.029129 | 0.028003 | 0.026923 | 0.025964 | 0.025182 | 0.024311
| 0.45 | 0.010266 | 0.027073 | 0.030549 | 0.030382 | 0.029398 | 0.028108 | 0.026901 | 0.025878 | 0.024919 | 0.023969 | 0.023266
| 0.5 | 0.009367 | 0.027038 | 0.030216 | 0.029595 | 0.028375 | 0.027078 | 0.025893 | 0.024747 | 0.023847 | 0.023021 | 0.022288
| 0.55 | 0.0086688 | 0.027134 | 0.029711 | 0.028824 | 0.027492 | 0.026154 | 0.024855 | 0.023881 | 0.022908 | 0.022141 | 0.02139
| 0.6 | 0.0080853 | 0.027006 | 0.029291 | 0.028197 | 0.02672 | 0.025209 | 0.024041 | 0.023091 | 0.022198 | 0.021331 | 0.020684
| 0.65 | 0.0076416 | 0.027168 | 0.028791 | 0.02744 | 0.025878 | 0.024547 | 0.023334 | 0.0223 | 0.021515 | 0.020668 | 0.020009
| 0.7 | 0.0071844 | 0.027129 | 0.028316 | 0.026775 | 0.025119 | 0.023798 | 0.02268 | 0.021637 | 0.020806 | 0.020001 | 0.01936
| 0.75 | 0.0065775 | 0.027076 | 0.027755 | 0.026035 | 0.024501 | 0.023071 | 0.022017 | 0.021049 | 0.020176 | 0.019421 | 0.018777
| 0.8 | 0.0065046 | 0.02707 | 0.027414 | 0.025509 | 0.023882 | 0.022475 | 0.021399 | 0.020469 | 0.019637 | 0.018982 | 0.018281
| 0.85 | 0.0059666 | 0.026931 | 0.026734 | 0.024875 | 0.023242 | 0.021997 | 0.020944 | 0.020016 | 0.019163 | 0.018478 | 0.01781
| 0.9 | 0.0056568 | 0.026856 | 0.026328 | 0.024342 | 0.022757 | 0.021528 | 0.020383 | 0.019508 | 0.018757 | 0.017966 | 0.017444
| 0.95 | 0.0055307 | 0.026782 | 0.02598 | 0.023903 | 0.022188 | 0.021017 | 0.020062 | 0.019076 | 0.018232 | 0.017655 | 0.017031
| 1 | 0.0052598 | 0.026477 | 0.025405 | 0.023335 | 0.02184 | 0.020588 | 0.019563 | 0.018672 | 0.017875 | 0.017221 | 0.016598
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0087531 | 0.0095897 | 0.010187 | 0.010624 | 0.010979 | 0.011242 | 0.011459 | 0.011607 | 0.011715 | 0.011801 | 0.011842
| 0.1 | 0.008063 | 0.0099025 | 0.010522 | 0.01081 | 0.01098 | 0.011102 | 0.011163 | 0.011168 | 0.011135 | 0.011071 | 0.010997
| 0.15 | 0.0067867 | 0.0095289 | 0.010102 | 0.010408 | 0.010589 | 0.010676 | 0.010656 | 0.010596 | 0.010485 | 0.01034 | 0.010191
| 0.2 | 0.0056863 | 0.009127 | 0.0097662 | 0.010168 | 0.010315 | 0.010323 | 0.010231 | 0.01008 | 0.0099039 | 0.0097129 | 0.0095328
| 0.25 | 0.0049042 | 0.0087845 | 0.0095706 | 0.009996 | 0.010067 | 0.0099798 | 0.009799 | 0.0095935 | 0.009366 | 0.0091488 | 0.0089367
| 0.3 | 0.0043065 | 0.0085545 | 0.0094572 | 0.0098106 | 0.0097959 | 0.0096091 | 0.0093834 | 0.0091169 | 0.0088711 | 0.0086366 | 0.0084156
| 0.35 | 0.0038159 | 0.0083945 | 0.0093755 | 0.0096116 | 0.0094958 | 0.009259 | 0.0089696 | 0.0086872 | 0.0084322 | 0.0081809 | 0.0079541
| 0.4 | 0.0034275 | 0.0082513 | 0.0092838 | 0.0094014 | 0.009196 | 0.0089023 | 0.0086059 | 0.0083112 | 0.0080323 | 0.0077814 | 0.0075605
| 0.45 | 0.0031307 | 0.0081909 | 0.0091817 | 0.0091836 | 0.0089033 | 0.0085725 | 0.0082524 | 0.0079528 | 0.0076931 | 0.0074285 | 0.0072052
| 0.5 | 0.0028656 | 0.008157 | 0.0090416 | 0.008958 | 0.0086331 | 0.0082782 | 0.0079333 | 0.0076384 | 0.0073643 | 0.0071362 | 0.0069036
| 0.55 | 0.0026375 | 0.0081437 | 0.0089244 | 0.0087414 | 0.008368 | 0.0079888 | 0.0076592 | 0.0073491 | 0.0070979 | 0.0068583 | 0.0066327
| 0.6 | 0.0024777 | 0.0081226 | 0.0087828 | 0.0085243 | 0.008112 | 0.0077309 | 0.0074068 | 0.0071122 | 0.006835 | 0.0066046 | 0.0063977
| 0.65 | 0.0023063 | 0.0081105 | 0.0086348 | 0.0083203 | 0.0078839 | 0.0074978 | 0.00716 | 0.0068807 | 0.0066104 | 0.0063893 | 0.0061812
| 0.7 | 0.0021853 | 0.0081074 | 0.0084991 | 0.0081104 | 0.0076724 | 0.0072892 | 0.0069539 | 0.0066685 | 0.0064212 | 0.0061904 | 0.0059847
| 0.75 | 0.0020505 | 0.0080901 | 0.008345 | 0.0079147 | 0.0074605 | 0.0070741 | 0.0067634 | 0.0064711 | 0.0062288 | 0.0060131 | 0.0058187
| 0.8 | 0.001941 | 0.0080517 | 0.0082215 | 0.0077293 | 0.0072879 | 0.0068982 | 0.0065785 | 0.0063074 | 0.0060593 | 0.0058458 | 0.0056546
| 0.85 | 0.001863 | 0.0080286 | 0.008075 | 0.0075706 | 0.0071048 | 0.0067386 | 0.0064122 | 0.0061422 | 0.0058996 | 0.0056988 | 0.0055014
| 0.9 | 0.0017597 | 0.0079966 | 0.0079294 | 0.0073928 | 0.006943 | 0.0065768 | 0.006259 | 0.0059957 | 0.0057614 | 0.0055524 | 0.0053581
| 0.95 | 0.0016776 | 0.0079599 | 0.0078141 | 0.0072525 | 0.0067995 | 0.0064263 | 0.0061311 | 0.0058548 | 0.0056157 | 0.005421 | 0.0052377
| 1 | 0.0016243 | 0.0079015 | 0.0076779 | 0.0071076 | 0.0066557 | 0.0062943 | 0.0059865 | 0.0057324 | 0.0055002 | 0.0052996 | 0.0051242
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.3693 | 1.7383 | 2.0169 | 2.2377 | 2.4086 | 2.5474 | 2.6516 | 2.7488 | 2.8227 | 2.8845 | 2.9363
| 0.1 | 1.2795 | 2.0627 | 2.6018 | 2.9995 | 3.3024 | 3.5354 | 3.7053 | 3.9088 | 3.9562 | 4.0733 | 4.1103
| 0.15 | 1.203 | 2.3404 | 3.0875 | 3.6296 | 4.0316 | 4.3289 | 4.6368 | 4.7077 | 4.8051 | 4.96 | 4.9824
| 0.2 | 1.1472 | 2.588 | 3.5276 | 4.1523 | 4.6524 | 5.0038 | 5.2423 | 5.455 | 5.589 | 5.7071 | 5.7951
| 0.25 | 1.1128 | 2.8225 | 3.8457 | 4.675 | 5.1976 | 5.5778 | 5.8613 | 6.079 | 6.2549 | 6.3741 | 6.4761
| 0.3 | 1.0819 | 3.0789 | 4.2835 | 5.1058 | 5.6778 | 6.1042 | 6.4073 | 6.6523 | 6.8334 | 6.9778 | 7.0648
| 0.35 | 1.0665 | 3.2706 | 4.6135 | 5.4996 | 6.1159 | 6.5773 | 6.9115 | 7.1699 | 7.3713 | 7.5249 | 7.6426
| 0.4 | 1.0486 | 3.6173 | 4.9136 | 5.8588 | 6.5151 | 7.0128 | 7.375 | 7.6597 | 7.8667 | 8.0298 | 8.154
| 0.45 | 1.0301 | 3.6807 | 5.1645 | 6.1942 | 6.903 | 7.4235 | 7.812 | 8.1009 | 8.3384 | 8.5073 | 8.6367
| 0.5 | 1.0262 | 3.7441 | 5.4557 | 6.5137 | 7.2519 | 7.8039 | 8.2192 | 8.5317 | 8.7664 | 8.9611 | 9.0977
| 0.55 | 1.0131 | 4.0039 | 5.7263 | 6.8136 | 7.5915 | 8.1699 | 8.61 | 8.9381 | 9.1902 | 9.3886 | 9.5342
| 0.6 | 1.0137 | 4.2355 | 5.9558 | 7.0962 | 7.9104 | 8.5169 | 8.9783 | 9.3272 | 9.5943 | 9.799 | 9.9502
| 0.65 | 1.0025 | 4.3739 | 6.1811 | 7.3602 | 8.2175 | 8.8528 | 9.3367 | 9.6984 | 9.9775 | 10.1949 | 10.3554
| 0.7 | 1.0019 | 4.5631 | 6.3965 | 7.6204 | 8.5125 | 9.1793 | 9.6818 | 10.0624 | 10.3532 | 10.5798 | 10.7376
| 0.75 | 0.99266 | 4.7145 | 6.6174 | 7.8774 | 8.7962 | 9.4854 | 10.0086 | 10.4125 | 10.7103 | 10.9409 | 11.1086
| 0.8 | 0.99448 | 4.8611 | 6.8133 | 8.1195 | 9.0699 | 9.7875 | 10.3269 | 10.7457 | 11.0439 | 11.2901 | 11.4691
| 0.85 | 0.98648 | 4.9966 | 7.0077 | 8.3598 | 9.3491 | 10.0823 | 10.6439 | 11.059 | 11.3943 | 11.6347 | 11.8164
| 0.9 | 0.98056 | 5.1335 | 7.1948 | 8.583 | 9.6057 | 10.3702 | 10.9511 | 11.3755 | 11.7111 | 11.9653 | 12.1526
| 0.95 | 0.98283 | 5.2649 | 7.3806 | 8.8049 | 9.8608 | 10.6409 | 11.2375 | 11.6855 | 12.0378 | 12.2875 | 12.4866
| 1 | 0.97758 | 5.4087 | 7.5558 | 9.0166 | 10.1066 | 10.9154 | 11.5235 | 11.9871 | 12.3342 | 12.603 | 12.7936
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.027299 | 0.025175 | 0.026181 | 0.027245 | 0.031641 | 0.033309 | 0.034403 | 0.038584 | 0.041617 | 0.042893 | 0.046612
| 0.1 | 0.028088 | 0.036426 | 0.047094 | 0.04799 | 0.052027 | 0.054858 | 0.061699 | 0.064867 | 0.069618 | 0.076052 | 0.077295
| 0.15 | 0.022838 | 0.041492 | 0.058385 | 0.063236 | 0.072413 | 0.076407 | 0.088994 | 0.091149 | 0.09762 | 0.1052 | 0.10564
| 0.2 | 0.016339 | 0.046559 | 0.068437 | 0.081238 | 0.094783 | 0.10612 | 0.11504 | 0.11743 | 0.12562 | 0.13435 | 0.13398
| 0.25 | 0.010429 | 0.051625 | 0.078489 | 0.095644 | 0.11723 | 0.12844 | 0.13658 | 0.14371 | 0.15362 | 0.15562 | 0.15718
| 0.3 | 0.006884 | 0.056691 | 0.088709 | 0.11236 | 0.13561 | 0.14754 | 0.15812 | 0.17 | 0.17266 | 0.17412 | 0.179
| 0.35 | 0.0046273 | 0.061758 | 0.10139 | 0.12907 | 0.15366 | 0.16665 | 0.17559 | 0.18287 | 0.18853 | 0.19191 | 0.19386
| 0.4 | 0.00023239 | 0.066824 | 0.1193 | 0.14579 | 0.1658 | 0.18094 | 0.19508 | 0.19835 | 0.20387 | 0.21019 | 0.21105
| 0.45 | -0.00032594 | 0.069066 | 0.13149 | 0.16148 | 0.17876 | 0.19522 | 0.2077 | 0.21436 | 0.22068 | 0.2221 | 0.22617
| 0.5 | -0.0022584 | 0.073401 | 0.14368 | 0.17622 | 0.19418 | 0.20841 | 0.22099 | 0.22649 | 0.23325 | 0.2383 | 0.24063
| 0.55 | -0.0040517 | 0.078043 | 0.15002 | 0.18091 | 0.20293 | 0.22096 | 0.2312 | 0.23943 | 0.24633 | 0.25155 | 0.25525
| 0.6 | -0.0053788 | 0.083495 | 0.15449 | 0.19091 | 0.21426 | 0.23076 | 0.24273 | 0.25255 | 0.25815 | 0.26299 | 0.26833
| 0.65 | -0.0066564 | 0.087553 | 0.16201 | 0.2006 | 0.22417 | 0.24286 | 0.25573 | 0.26393 | 0.27118 | 0.27622 | 0.28125
| 0.7 | -0.0079171 | 0.099776 | 0.17283 | 0.20891 | 0.2321 | 0.25127 | 0.26684 | 0.27495 | 0.2843 | 0.28957 | 0.29351
| 0.75 | -0.0063821 | 0.10666 | 0.17761 | 0.21637 | 0.24208 | 0.26115 | 0.27554 | 0.28658 | 0.2951 | 0.29922 | 0.30493
| 0.8 | -0.0094273 | 0.11419 | 0.18582 | 0.22649 | 0.25058 | 0.26994 | 0.28499 | 0.29694 | 0.30417 | 0.31326 | 0.31533
| 0.85 | -0.0084187 | 0.1195 | 0.19022 | 0.23096 | 0.26034 | 0.28109 | 0.29637 | 0.30881 | 0.31559 | 0.32402 | 0.3268
| 0.9 | -0.0096091 | 0.12481 | 0.19777 | 0.23858 | 0.26782 | 0.2903 | 0.30454 | 0.31841 | 0.32743 | 0.33339 | 0.34162
| 0.95 | -0.010207 | 0.1327 | 0.204 | 0.24687 | 0.27484 | 0.29886 | 0.31663 | 0.3287 | 0.33541 | 0.34607 | 0.35056
| 1 | -0.011241 | 0.13982 | 0.21209 | 0.25311 | 0.28435 | 0.30805 | 0.32476 | 0.33661 | 0.34831 | 0.35553 | 0.35949
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.00042404 | -0.0087715 | -0.014896 | -0.019104 | -0.022194 | -0.02443 | -0.026477 | -0.027295 | -0.028174 | -0.029125 | -0.02932
| 0.1 | 0.002932 | -0.012981 | -0.022512 | -0.03037 | -0.031858 | -0.036595 | -0.039092 | -0.040716 | -0.041506 | -0.042351 | -0.042148
| 0.15 | 0.0028208 | -0.017992 | -0.029248 | -0.036707 | -0.041522 | -0.044968 | -0.047846 | -0.049475 | -0.051041 | -0.050905 | -0.052032
| 0.2 | 0.0027568 | -0.022518 | -0.035195 | -0.042013 | -0.047127 | -0.051418 | -0.054313 | -0.055606 | -0.057946 | -0.058351 | -0.060057
| 0.25 | 0.0021948 | -0.027586 | -0.039593 | -0.047519 | -0.052012 | -0.057944 | -0.06078 | -0.063247 | -0.064313 | -0.065797 | -0.066791
| 0.3 | 0.001755 | -0.028491 | -0.043876 | -0.053587 | -0.058278 | -0.062461 | -0.065661 | -0.068354 | -0.070527 | -0.071853 | -0.072843
| 0.35 | 0.0014784 | -0.03207 | -0.048159 | -0.055414 | -0.062011 | -0.066733 | -0.070789 | -0.073678 | -0.075798 | -0.07739 | -0.078644
| 0.4 | 0.00137 | -0.034553 | -0.050403 | -0.05878 | -0.065735 | -0.071435 | -0.075231 | -0.078473 | -0.081047 | -0.082932 | -0.084413
| 0.45 | 0.0010723 | -0.037412 | -0.05208 | -0.061593 | -0.069348 | -0.07523 | -0.079837 | -0.083247 | -0.086081 | -0.087814 | -0.089544
| 0.5 | 0.0009592 | -0.040272 | -0.053756 | -0.064366 | -0.072726 | -0.079577 | -0.084419 | -0.088119 | -0.090646 | -0.092794 | -0.0945
| 0.55 | 0.00086283 | -0.04087 | -0.055846 | -0.067322 | -0.076409 | -0.083005 | -0.088301 | -0.09201 | -0.094904 | -0.097275 | -0.099081
| 0.6 | 0.0006228 | -0.042454 | -0.058081 | -0.07015 | -0.079359 | -0.086766 | -0.092263 | -0.096221 | -0.099429 | -0.10181 | -0.10353
| 0.65 | 0.00061832 | -0.043643 | -0.060149 | -0.073136 | -0.08263 | -0.090115 | -0.096143 | -0.10013 | -0.10343 | -0.10597 | -0.10795
| 0.7 | 0.00040261 | -0.04578 | -0.062276 | -0.075423 | -0.085751 | -0.093589 | -0.099737 | -0.10405 | -0.10738 | -0.10973 | -0.11191
| 0.75 | 0.00043963 | -0.047079 | -0.064129 | -0.078116 | -0.089024 | -0.097001 | -0.10287 | -0.10787 | -0.11138 | -0.11399 | -0.1157
| 0.8 | 0.0004584 | -0.048826 | -0.066123 | -0.081084 | -0.091947 | -0.10018 | -0.10632 | -0.11091 | -0.11486 | -0.11754 | -0.11954
| 0.85 | 0.00022448 | -0.049491 | -0.068035 | -0.083189 | -0.09495 | -0.10325 | -0.10979 | -0.11458 | -0.11848 | -0.12102 | -0.12327
| 0.9 | 0.00028245 | -0.052035 | -0.070273 | -0.086012 | -0.09764 | -0.10639 | -0.11283 | -0.11788 | -0.12182 | -0.12451 | -0.127
| 0.95 | 0.00028203 | -0.052698 | -0.071885 | -0.088295 | -0.10016 | -0.10938 | -0.11564 | -0.12119 | -0.12508 | -0.128 | -0.13025
| 1 | 0.00013357 | -0.053362 | -0.073954 | -0.090605 | -0.10277 | -0.11204 | -0.11887 | -0.12412 | -0.12818 | -0.13146 | -0.13367
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89)
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89)
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89)

## CLASS3_OOP (hidden)
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
| 0.05 | 2.8826 | 2.9722 | 3.0616 | 3.1203 | 3.1516 | 3.1636 | 3.162 | 3.1508 | 3.133 | 3.1105 | 3.0847
| 0.1 | 2.8606 | 2.9946 | 3.1213 | 3.2013 | 3.2434 | 3.2566 | 3.2515 | 3.235 | 3.2138 | 3.1875 | 3.1578
| 0.15 | 2.7818 | 2.9889 | 3.1442 | 3.2338 | 3.2747 | 3.2907 | 3.2888 | 3.2741 | 3.2511 | 3.2225 | 3.1902
| 0.2 | 2.69 | 2.9691 | 3.1467 | 3.2473 | 3.293 | 3.3137 | 3.3134 | 3.299 | 3.2752 | 3.2454 | 3.2115
| 0.25 | 2.6038 | 2.9474 | 3.1439 | 3.2522 | 3.306 | 3.3309 | 3.3316 | 3.3169 | 3.2923 | 3.2612 | 3.226
| 0.3 | 2.5279 | 2.9277 | 3.1414 | 3.2547 | 3.3174 | 3.3442 | 3.3451 | 3.3299 | 3.3045 | 3.2725 | 3.2363
| 0.35 | 2.4626 | 2.9105 | 3.1371 | 3.2572 | 3.3267 | 3.3544 | 3.3553 | 3.3396 | 3.3136 | 3.281 | 3.2442
| 0.4 | 2.4068 | 2.8957 | 3.1322 | 3.2603 | 3.334 | 3.3622 | 3.3631 | 3.3472 | 3.3209 | 3.2878 | 3.2505
| 0.45 | 2.3591 | 2.8827 | 3.1275 | 3.2642 | 3.3398 | 3.3685 | 3.3694 | 3.3535 | 3.3269 | 3.2935 | 3.2558
| 0.5 | 2.318 | 2.8714 | 3.1235 | 3.2678 | 3.3445 | 3.3736 | 3.3748 | 3.3588 | 3.332 | 3.2984 | 3.2603
| 0.55 | 2.2824 | 2.8614 | 3.1203 | 3.2707 | 3.3484 | 3.3781 | 3.3795 | 3.3634 | 3.3365 | 3.3025 | 3.2642
| 0.6 | 2.2513 | 2.8524 | 3.1179 | 3.2731 | 3.3518 | 3.3821 | 3.3836 | 3.3675 | 3.3403 | 3.3061 | 3.2675
| 0.65 | 2.224 | 2.8442 | 3.1166 | 3.2751 | 3.3549 | 3.3856 | 3.3872 | 3.371 | 3.3436 | 3.3092 | 3.2704
| 0.7 | 2.1999 | 2.8369 | 3.1167 | 3.2769 | 3.3576 | 3.3888 | 3.3904 | 3.3741 | 3.3466 | 3.312 | 3.2729
| 0.75 | 2.1785 | 2.8302 | 3.1169 | 3.2786 | 3.3602 | 3.3916 | 3.3933 | 3.3769 | 3.3492 | 3.3144 | 3.2752
| 0.8 | 2.1593 | 2.8242 | 3.1171 | 3.2801 | 3.3625 | 3.3942 | 3.3959 | 3.3794 | 3.3516 | 3.3166 | 3.2773
| 0.85 | 2.142 | 2.8187 | 3.1172 | 3.2816 | 3.3646 | 3.3965 | 3.3982 | 3.3816 | 3.3537 | 3.3187 | 3.2791
| 0.9 | 2.1264 | 2.8137 | 3.1172 | 3.283 | 3.3666 | 3.3986 | 3.4003 | 3.3837 | 3.3557 | 3.3205 | 3.2808
| 0.95 | 2.1123 | 2.8093 | 3.1171 | 3.2843 | 3.3683 | 3.4005 | 3.4022 | 3.3856 | 3.3575 | 3.3222 | 3.2824
| 1 | 2.0994 | 2.8053 | 3.117 | 3.2855 | 3.37 | 3.4022 | 3.404 | 3.3873 | 3.3591 | 3.3237 | 3.2838
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1
| 0.05 | 3.05 | 2.9557 | 2.8656 | 2.7807 | 2.701 | 2.6262 | 2.5578 | 2.4919 | 2.4305 | 2.3729 | 2.3188
| 0.1 | 2.7002 | 2.5378 | 2.4151 | 2.3119 | 2.2201 | 2.1371 | 2.062 | 1.9929 | 1.9301 | 1.8725 | 1.8193
| 0.15 | 2.5293 | 2.2965 | 2.1556 | 2.0435 | 1.9453 | 1.8589 | 1.783 | 1.7147 | 1.6538 | 1.5986 | 1.5487
| 0.2 | 2.4323 | 2.1299 | 1.9765 | 1.8563 | 1.7541 | 1.6669 | 1.5923 | 1.5269 | 1.4686 | 1.417 | 1.3711
| 0.25 | 2.3701 | 2.0064 | 1.8402 | 1.7128 | 1.6092 | 1.5236 | 1.4514 | 1.389 | 1.334 | 1.2863 | 1.2431
| 0.3 | 2.3249 | 1.908 | 1.7295 | 1.5975 | 1.4945 | 1.4111 | 1.3418 | 1.2823 | 1.2312 | 1.1858 | 1.145
| 0.35 | 2.2935 | 1.8258 | 1.6368 | 1.5021 | 1.4009 | 1.3202 | 1.2538 | 1.1974 | 1.1483 | 1.1055 | 1.0677
| 0.4 | 2.2677 | 1.7554 | 1.5564 | 1.4217 | 1.3228 | 1.2449 | 1.1812 | 1.1271 | 1.0805 | 1.04 | 1.0036
| 0.45 | 2.2489 | 1.6939 | 1.4869 | 1.3529 | 1.256 | 1.1809 | 1.1196 | 1.0679 | 1.0237 | 0.98483 | 0.95051
| 0.5 | 2.2341 | 1.6379 | 1.426 | 1.2925 | 1.1983 | 1.1261 | 1.0674 | 1.0175 | 0.97484 | 0.93777 | 0.90507
| 0.55 | 2.22 | 1.5878 | 1.3715 | 1.2399 | 1.1484 | 1.0783 | 1.0212 | 0.97398 | 0.93268 | 0.89723 | 0.86548
| 0.6 | 2.2098 | 1.5424 | 1.3225 | 1.1932 | 1.104 | 1.0361 | 0.98156 | 0.93507 | 0.89573 | 0.86073 | 0.83058
| 0.65 | 2.1994 | 1.4998 | 1.2786 | 1.1513 | 1.0647 | 0.99897 | 0.9455 | 0.90075 | 0.8626 | 0.82898 | 0.79986
| 0.7 | 2.1923 | 1.4612 | 1.2387 | 1.1137 | 1.0289 | 0.96523 | 0.91339 | 0.87027 | 0.83311 | 0.80094 | 0.77219
| 0.75 | 2.1861 | 1.4254 | 1.2023 | 1.0793 | 0.9969 | 0.93495 | 0.88473 | 0.84243 | 0.8064 | 0.77475 | 0.74725
| 0.8 | 2.1787 | 1.3916 | 1.1685 | 1.0484 | 0.9681 | 0.90684 | 0.85821 | 0.81683 | 0.78202 | 0.75137 | 0.72453
| 0.85 | 2.1744 | 1.3602 | 1.1379 | 1.0198 | 0.94113 | 0.88175 | 0.83382 | 0.79391 | 0.7596 | 0.72985 | 0.70378
| 0.9 | 2.1682 | 1.3309 | 1.1097 | 0.99355 | 0.91676 | 0.85822 | 0.8116 | 0.77253 | 0.73945 | 0.71028 | 0.68468
| 0.95 | 2.1648 | 1.3028 | 1.083 | 0.96913 | 0.89348 | 0.83672 | 0.79086 | 0.75283 | 0.72042 | 0.69216 | 0.66732
| 1 | 2.1617 | 1.2769 | 1.058 | 0.94649 | 0.87242 | 0.81704 | 0.77193 | 0.73498 | 0.70256 | 0.67525 | 0.65108
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.036075 | 0.038465 | 0.039713 | 0.040623 | 0.041312 | 0.041773 | 0.042062 | 0.042024 | 0.042256 | 0.042462 | 0.042411
| 0.1 | 0.031768 | 0.037625 | 0.038918 | 0.039654 | 0.040236 | 0.040463 | 0.040352 | 0.040365 | 0.040098 | 0.039577 | 0.03912
| 0.15 | 0.027395 | 0.03538 | 0.037257 | 0.038912 | 0.039431 | 0.039278 | 0.038654 | 0.038191 | 0.037412 | 0.036668 | 0.035824
| 0.2 | 0.023386 | 0.03406 | 0.036862 | 0.038139 | 0.038136 | 0.037537 | 0.036509 | 0.035658 | 0.034753 | 0.033829 | 0.033035
| 0.25 | 0.020632 | 0.032823 | 0.036718 | 0.037165 | 0.036672 | 0.035492 | 0.034496 | 0.033427 | 0.032355 | 0.031452 | 0.030518
| 0.3 | 0.019137 | 0.032421 | 0.036168 | 0.035902 | 0.035082 | 0.033762 | 0.032572 | 0.031352 | 0.030496 | 0.029445 | 0.028635
| 0.35 | 0.017236 | 0.03245 | 0.035377 | 0.034845 | 0.033466 | 0.032155 | 0.030916 | 0.029712 | 0.028617 | 0.02772 | 0.026894
| 0.4 | 0.016068 | 0.032181 | 0.034546 | 0.033739 | 0.032078 | 0.030691 | 0.02939 | 0.028252 | 0.027207 | 0.026343 | 0.025448
| 0.45 | 0.015142 | 0.032216 | 0.03394 | 0.032471 | 0.030822 | 0.029454 | 0.028151 | 0.027043 | 0.025945 | 0.025129 | 0.02426
| 0.5 | 0.01436 | 0.032123 | 0.032926 | 0.03138 | 0.029735 | 0.028281 | 0.026937 | 0.025912 | 0.024861 | 0.024093 | 0.023309
| 0.55 | 0.013327 | 0.032011 | 0.032297 | 0.030431 | 0.028697 | 0.027174 | 0.025972 | 0.024928 | 0.023951 | 0.0231 | 0.022391
| 0.6 | 0.013201 | 0.031686 | 0.031418 | 0.0295 | 0.027766 | 0.026299 | 0.025079 | 0.024123 | 0.02311 | 0.022306 | 0.021535
| 0.65 | 0.012306 | 0.031479 | 0.030702 | 0.028672 | 0.026873 | 0.025478 | 0.024205 | 0.023192 | 0.022411 | 0.02157 | 0.02084
| 0.7 | 0.0119 | 0.03115 | 0.030023 | 0.027882 | 0.026167 | 0.0248 | 0.023484 | 0.022605 | 0.021612 | 0.020884 | 0.020181
| 0.75 | 0.012009 | 0.030927 | 0.029393 | 0.02714 | 0.025365 | 0.024051 | 0.022883 | 0.021958 | 0.02099 | 0.020326 | 0.01953
| 0.8 | 0.011304 | 0.030556 | 0.028791 | 0.026481 | 0.024753 | 0.023427 | 0.022304 | 0.021245 | 0.020398 | 0.019676 | 0.019046
| 0.85 | 0.011026 | 0.030258 | 0.028119 | 0.025816 | 0.024196 | 0.02289 | 0.021744 | 0.020776 | 0.019955 | 0.019162 | 0.018554
| 0.9 | 0.010865 | 0.03 | 0.027501 | 0.025292 | 0.023549 | 0.022308 | 0.021265 | 0.020256 | 0.019441 | 0.018755 | 0.018001
| 0.95 | 0.010618 | 0.029514 | 0.02706 | 0.024688 | 0.023037 | 0.021797 | 0.020643 | 0.019796 | 0.019011 | 0.018277 | 0.01758
| 1 | 0.010047 | 0.029316 | 0.026484 | 0.024221 | 0.022588 | 0.021406 | 0.020237 | 0.019291 | 0.018516 | 0.017828 | 0.017196
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0082601 | 0.0093959 | 0.010093 | 0.010542 | 0.010869 | 0.011123 | 0.011273 | 0.011459 | 0.011543 | 0.011605 | 0.011636
| 0.1 | 0.0071504 | 0.0095485 | 0.010238 | 0.010617 | 0.010865 | 0.01102 | 0.011039 | 0.01107 | 0.011017 | 0.010914 | 0.010812
| 0.15 | 0.0057746 | 0.0092322 | 0.0099817 | 0.010447 | 0.010661 | 0.010703 | 0.010635 | 0.010504 | 0.010345 | 0.010158 | 0.0099651
| 0.2 | 0.0047314 | 0.0088631 | 0.0098815 | 0.01033 | 0.010406 | 0.010311 | 0.010131 | 0.0099063 | 0.0096649 | 0.0094422 | 0.0092148
| 0.25 | 0.003974 | 0.0086736 | 0.0097797 | 0.010132 | 0.010072 | 0.0098612 | 0.0095997 | 0.0093293 | 0.0090638 | 0.0088114 | 0.0085775
| 0.3 | 0.0034594 | 0.0085648 | 0.0097214 | 0.0098948 | 0.0097082 | 0.0094134 | 0.0091022 | 0.0088013 | 0.0085172 | 0.0082711 | 0.0080218
| 0.35 | 0.0029713 | 0.0085359 | 0.00959 | 0.0095977 | 0.0093327 | 0.0089871 | 0.0086525 | 0.0083362 | 0.0080494 | 0.007794 | 0.0075599
| 0.4 | 0.0026813 | 0.0084979 | 0.0094357 | 0.0093139 | 0.0089631 | 0.008588 | 0.0082486 | 0.007938 | 0.0076652 | 0.0073926 | 0.0071686
| 0.45 | 0.002444 | 0.0085166 | 0.0092737 | 0.0090375 | 0.0086286 | 0.0082348 | 0.0078908 | 0.007573 | 0.0072976 | 0.0070547 | 0.0068357
| 0.5 | 0.002157 | 0.0085066 | 0.009087 | 0.0087523 | 0.0083206 | 0.0079239 | 0.0075742 | 0.0072714 | 0.0070095 | 0.0067541 | 0.0065403
| 0.55 | 0.0020135 | 0.0085089 | 0.0088924 | 0.0084976 | 0.0080366 | 0.0076373 | 0.0072917 | 0.0069961 | 0.0067307 | 0.0064885 | 0.0062799
| 0.6 | 0.0018401 | 0.0084566 | 0.0087274 | 0.0082506 | 0.0077668 | 0.0073776 | 0.0070444 | 0.0067408 | 0.0064933 | 0.0062654 | 0.0060552
| 0.65 | 0.0016971 | 0.0084349 | 0.0085316 | 0.0080183 | 0.0075372 | 0.0071458 | 0.0068173 | 0.0065263 | 0.0062697 | 0.0060573 | 0.0058452
| 0.7 | 0.001571 | 0.0083878 | 0.0083647 | 0.0077907 | 0.0073178 | 0.0069406 | 0.0066112 | 0.0063299 | 0.0060703 | 0.0058516 | 0.0056636
| 0.75 | 0.0015 | 0.0083565 | 0.0081882 | 0.007604 | 0.0071184 | 0.0067398 | 0.0064233 | 0.006144 | 0.0059154 | 0.0056889 | 0.0054947
| 0.8 | 0.0014557 | 0.0082882 | 0.008004 | 0.0074199 | 0.0069349 | 0.0065592 | 0.006248 | 0.0059796 | 0.0057268 | 0.0055282 | 0.0053346
| 0.85 | 0.00131 | 0.0082406 | 0.0078563 | 0.007238 | 0.0067618 | 0.006409 | 0.0060913 | 0.0058279 | 0.0055888 | 0.0053769 | 0.0052016
| 0.9 | 0.0012746 | 0.0081723 | 0.0076969 | 0.0070802 | 0.0066085 | 0.0062515 | 0.0059519 | 0.0056795 | 0.0054509 | 0.0052471 | 0.0050571
| 0.95 | 0.001193 | 0.0081155 | 0.0075507 | 0.0069228 | 0.0064643 | 0.0061194 | 0.005809 | 0.0055409 | 0.0053254 | 0.0051143 | 0.0049439
| 1 | 0.0011293 | 0.0080369 | 0.0074176 | 0.0067972 | 0.0063426 | 0.0059741 | 0.0056773 | 0.0054163 | 0.0051887 | 0.00501 | 0.0048285
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.2461 | 1.6405 | 1.936 | 2.1652 | 2.3439 | 2.4883 | 2.596 | 2.691 | 2.7682 | 2.836 | 2.8853
| 0.1 | 1.1537 | 1.9519 | 2.4987 | 2.9002 | 3.2 | 3.4303 | 3.6003 | 3.7587 | 3.8616 | 3.9446 | 4.0091
| 0.15 | 1.0928 | 2.2226 | 2.9881 | 3.5318 | 3.8906 | 4.2144 | 4.4305 | 4.6354 | 4.6858 | 4.8962 | 4.9096
| 0.2 | 1.0478 | 2.4803 | 3.4121 | 4.0222 | 4.4721 | 4.803 | 5.0279 | 5.2169 | 5.3702 | 5.4957 | 5.574
| 0.25 | 1.0175 | 2.715 | 3.8686 | 4.4053 | 4.975 | 5.3465 | 5.6171 | 5.8243 | 5.9838 | 6.1058 | 6.194
| 0.3 | 1.0039 | 2.9358 | 4.1073 | 4.8253 | 5.4083 | 5.8287 | 6.109 | 6.363 | 6.5289 | 6.6682 | 6.7754
| 0.35 | 0.98316 | 3.1724 | 4.4157 | 5.2454 | 5.8305 | 6.2726 | 6.5975 | 6.8495 | 7.0343 | 7.1874 | 7.296
| 0.4 | 0.97693 | 3.3692 | 4.6354 | 5.5808 | 6.2014 | 6.6773 | 7.0266 | 7.305 | 7.5102 | 7.6697 | 7.7876
| 0.45 | 0.96663 | 3.5417 | 4.9377 | 5.8959 | 6.572 | 7.0674 | 7.4416 | 7.7315 | 7.9507 | 8.1149 | 8.2493
| 0.5 | 0.95472 | 3.7283 | 5.2105 | 6.1868 | 6.903 | 7.4317 | 7.8269 | 8.131 | 8.3707 | 8.5435 | 8.6786
| 0.55 | 0.95417 | 3.9357 | 5.4223 | 6.4698 | 7.2227 | 7.7781 | 8.1964 | 8.5204 | 8.7679 | 8.9551 | 9.0986
| 0.6 | 0.94709 | 4.0761 | 5.6466 | 6.7427 | 7.5249 | 8.1026 | 8.551 | 8.8841 | 9.1444 | 9.3429 | 9.4936
| 0.65 | 0.9464 | 4.2165 | 5.8683 | 6.9921 | 7.8104 | 8.4297 | 8.8878 | 9.2381 | 9.5071 | 9.7098 | 9.8679
| 0.7 | 0.93915 | 4.363 | 6.0726 | 7.244 | 8.0931 | 8.7325 | 9.2154 | 9.5838 | 9.86 | 10.078 | 10.2359
| 0.75 | 0.93419 | 4.5036 | 6.2688 | 7.4755 | 8.3656 | 9.0326 | 9.5312 | 9.912 | 10.2023 | 10.4207 | 10.5894
| 0.8 | 0.93572 | 4.6239 | 6.468 | 7.7043 | 8.6278 | 9.3131 | 9.834 | 10.2238 | 10.5279 | 10.7568 | 10.92
| 0.85 | 0.92896 | 4.7763 | 6.6511 | 7.9379 | 8.882 | 9.5931 | 10.1248 | 10.5334 | 10.8434 | 11.0717 | 11.2536
| 0.9 | 0.9315 | 4.9022 | 6.828 | 8.1529 | 9.1326 | 9.8591 | 10.4129 | 10.8304 | 11.1482 | 11.3905 | 11.5739
| 0.95 | 0.92768 | 5.025 | 6.9965 | 8.3637 | 9.3758 | 10.1214 | 10.686 | 11.1221 | 11.447 | 11.6996 | 11.8817
| 1 | 0.92 | 5.1478 | 7.1686 | 8.5684 | 9.6076 | 10.3763 | 10.9594 | 11.3996 | 11.7301 | 11.9971 | 12.1884
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.018094 | 0.017918 | 0.019047 | 0.0214 | 0.023689 | 0.025519 | 0.027793 | 0.03316 | 0.033109 | 0.03495 | 0.037059
| 0.1 | 0.01929 | 0.02424 | 0.029654 | 0.039731 | 0.040352 | 0.045327 | 0.055674 | 0.056939 | 0.062861 | 0.068783 | 0.071744
| 0.15 | 0.012725 | 0.029043 | 0.040053 | 0.048728 | 0.057708 | 0.063874 | 0.072796 | 0.074969 | 0.080485 | 0.086562 | 0.089475
| 0.2 | 0.011184 | 0.030519 | 0.050568 | 0.066475 | 0.075063 | 0.082421 | 0.089918 | 0.092999 | 0.098109 | 0.10434 | 0.10721
| 0.25 | 0.0078307 | 0.03984 | 0.061576 | 0.077335 | 0.092419 | 0.10097 | 0.10704 | 0.11103 | 0.11573 | 0.12212 | 0.12494
| 0.3 | 0.0040949 | 0.041708 | 0.070647 | 0.088195 | 0.10977 | 0.11952 | 0.12416 | 0.12906 | 0.13336 | 0.13718 | 0.13751
| 0.35 | 0.0032426 | 0.052304 | 0.079718 | 0.099055 | 0.12084 | 0.12965 | 0.13673 | 0.14268 | 0.14586 | 0.15169 | 0.15279
| 0.4 | 0.0022728 | 0.051461 | 0.08879 | 0.10992 | 0.12918 | 0.14026 | 0.14792 | 0.15534 | 0.15984 | 0.16236 | 0.16751
| 0.45 | 0.001252 | 0.056597 | 0.097861 | 0.12078 | 0.13843 | 0.15168 | 0.15912 | 0.16673 | 0.17176 | 0.17548 | 0.17858
| 0.5 | 8.2397e-05 | 0.061732 | 0.10693 | 0.1328 | 0.15055 | 0.15903 | 0.16936 | 0.17551 | 0.18334 | 0.18805 | 0.19043
| 0.55 | 0.00058713 | 0.066867 | 0.10942 | 0.13861 | 0.15425 | 0.16768 | 0.17919 | 0.18578 | 0.19267 | 0.19932 | 0.20273
| 0.6 | -0.0013396 | 0.072003 | 0.11844 | 0.14342 | 0.16244 | 0.17633 | 0.18797 | 0.19816 | 0.20271 | 0.20852 | 0.21256
| 0.65 | -0.00081036 | 0.077138 | 0.12154 | 0.14846 | 0.16958 | 0.18689 | 0.19751 | 0.20664 | 0.21356 | 0.21921 | 0.2235
| 0.7 | -0.0013952 | 0.082273 | 0.13062 | 0.15712 | 0.1776 | 0.19555 | 0.20666 | 0.21785 | 0.22334 | 0.22974 | 0.23091
| 0.75 | -0.0039209 | 0.084544 | 0.13562 | 0.16364 | 0.18575 | 0.20225 | 0.21561 | 0.22665 | 0.23332 | 0.23834 | 0.2421
| 0.8 | -0.0025234 | 0.080393 | 0.14245 | 0.17026 | 0.19338 | 0.21102 | 0.22429 | 0.23406 | 0.23962 | 0.24702 | 0.25203
| 0.85 | -0.0032108 | 0.086124 | 0.14707 | 0.17491 | 0.20101 | 0.21875 | 0.23266 | 0.24329 | 0.24998 | 0.25549 | 0.25961
| 0.9 | -0.0037316 | 0.092085 | 0.14946 | 0.18151 | 0.20675 | 0.22566 | 0.24131 | 0.24884 | 0.25809 | 0.26327 | 0.2692
| 0.95 | -0.0037417 | 0.098045 | 0.15222 | 0.18842 | 0.21407 | 0.23301 | 0.24667 | 0.25744 | 0.26724 | 0.27306 | 0.27781
| 1 | -0.0023712 | 0.10258 | 0.15663 | 0.19392 | 0.21983 | 0.24095 | 0.25452 | 0.26412 | 0.27581 | 0.28091 | 0.28383
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.00016021 | -0.0062161 | -0.010434 | -0.013385 | -0.01559 | -0.017083 | -0.018061 | -0.019045 | -0.019676 | -0.020052 | -0.020373
| 0.1 | 0.001009 | -0.009562 | -0.016451 | -0.020874 | -0.02398 | -0.026485 | -0.026685 | -0.028077 | -0.028838 | -0.029098 | -0.029807
| 0.15 | 0.00091995 | -0.012905 | -0.021478 | -0.026232 | -0.027886 | -0.031199 | -0.032881 | -0.034192 | -0.0346 | -0.035558 | -0.036154
| 0.2 | 0.00062681 | -0.015957 | -0.025008 | -0.029619 | -0.0321 | -0.036274 | -0.037549 | -0.039125 | -0.039598 | -0.040997 | -0.041408
| 0.25 | 0.00043437 | -0.0184 | -0.025624 | -0.031887 | -0.035344 | -0.041348 | -0.041758 | -0.043534 | -0.044596 | -0.045803 | -0.04718
| 0.3 | 0.00013067 | -0.020537 | -0.029118 | -0.034442 | -0.039265 | -0.04389 | -0.046377 | -0.048818 | -0.049459 | -0.050216 | -0.051258
| 0.35 | 0.00020022 | -0.022317 | -0.03094 | -0.037402 | -0.043197 | -0.046825 | -0.049257 | -0.051644 | -0.053262 | -0.05461 | -0.055346
| 0.4 | -0.00011299 | -0.024539 | -0.032653 | -0.040661 | -0.045883 | -0.049946 | -0.053168 | -0.055031 | -0.056896 | -0.058631 | -0.059675
| 0.45 | -0.00035398 | -0.025328 | -0.03466 | -0.042952 | -0.04842 | -0.052884 | -0.056058 | -0.058502 | -0.060653 | -0.061849 | -0.063232
| 0.5 | -0.0001539 | -0.026117 | -0.036668 | -0.044972 | -0.050991 | -0.055524 | -0.059461 | -0.061787 | -0.063864 | -0.065511 | -0.066789
| 0.55 | -0.00037583 | -0.026675 | -0.038342 | -0.047105 | -0.053771 | -0.058527 | -0.062275 | -0.064861 | -0.06719 | -0.068864 | -0.069883
| 0.6 | -0.00046807 | -0.028897 | -0.040039 | -0.049585 | -0.055794 | -0.0611 | -0.065033 | -0.067949 | -0.069943 | -0.071847 | -0.073122
| 0.65 | -0.00040653 | -0.030112 | -0.041545 | -0.051323 | -0.058205 | -0.063693 | -0.067748 | -0.07082 | -0.073018 | -0.07484 | -0.076292
| 0.7 | -0.00046441 | -0.029546 | -0.043577 | -0.05307 | -0.060759 | -0.065977 | -0.070352 | -0.07341 | -0.07598 | -0.077719 | -0.079234
| 0.75 | -0.00060899 | -0.030808 | -0.04475 | -0.055078 | -0.062845 | -0.068385 | -0.07288 | -0.07622 | -0.078552 | -0.080423 | -0.081826
| 0.8 | -0.0008259 | -0.032069 | -0.046035 | -0.056871 | -0.064927 | -0.070806 | -0.075304 | -0.078542 | -0.081437 | -0.083469 | -0.084738
| 0.85 | -0.00061212 | -0.03333 | -0.047992 | -0.058741 | -0.067044 | -0.072798 | -0.077625 | -0.080986 | -0.083824 | -0.08592 | -0.087582
| 0.9 | -0.00077799 | -0.034591 | -0.049144 | -0.060445 | -0.068971 | -0.074942 | -0.07977 | -0.083494 | -0.086352 | -0.088391 | -0.09022
| 0.95 | -0.00074801 | -0.034881 | -0.050421 | -0.062124 | -0.070779 | -0.076866 | -0.081898 | -0.085823 | -0.088661 | -0.09115 | -0.092682
| 1 | -0.00074398 | -0.035171 | -0.052011 | -0.064002 | -0.072762 | -0.079168 | -0.08411 | -0.088027 | -0.091211 | -0.093001 | -0.094959
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87)
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87)
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87)

## CLASS4_OOP (hidden)
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
| 0.05 | 2.89 | 2.9354 | 2.968 | 2.9956 | 3.0094 | 3.0151 | 3.0143 | 3.0081 | 2.9978 | 2.9842 | 2.97
| 0.1 | 2.95 | 3.0293 | 3.1056 | 3.1554 | 3.1796 | 3.1863 | 3.1804 | 3.1656 | 3.1447 | 3.1194 | 3.09
| 0.15 | 2.95 | 3.0595 | 3.1526 | 3.2173 | 3.2468 | 3.2532 | 3.2446 | 3.2283 | 3.2072 | 3.1814 | 3.15
| 0.2 | 2.92 | 3.0702 | 3.1849 | 3.2541 | 3.2871 | 3.2959 | 3.2886 | 3.2706 | 3.2455 | 3.2157 | 3.18
| 0.25 | 2.89 | 3.063 | 3.2016 | 3.279 | 3.314 | 3.3225 | 3.314 | 3.2945 | 3.2676 | 3.2358 | 3.2
| 0.3 | 2.84 | 3.0485 | 3.2071 | 3.2914 | 3.3293 | 3.3387 | 3.3302 | 3.31 | 3.2821 | 3.2493 | 3.21
| 0.35 | 2.79 | 3.0315 | 3.2069 | 3.2977 | 3.3388 | 3.3496 | 3.3413 | 3.3209 | 3.2926 | 3.2593 | 3.22
| 0.4 | 2.74 | 3.0143 | 3.2038 | 3.3009 | 3.345 | 3.3572 | 3.3495 | 3.3294 | 3.3012 | 3.2679 | 3.23
| 0.45 | 2.69 | 2.9981 | 3.1997 | 3.3024 | 3.3493 | 3.3629 | 3.3563 | 3.3368 | 3.309 | 3.2758 | 3.24
| 0.5 | 2.65 | 2.9838 | 3.195 | 3.3028 | 3.3523 | 3.3678 | 3.3625 | 3.3438 | 3.3163 | 3.2831 | 3.25
| 0.55 | 2.61 | 2.9705 | 3.1903 | 3.3025 | 3.3548 | 3.3724 | 3.3685 | 3.3504 | 3.3231 | 3.2895 | 3.25
| 0.6 | 2.57 | 2.9583 | 3.1856 | 3.3019 | 3.3573 | 3.3771 | 3.3743 | 3.3566 | 3.329 | 3.2951 | 3.26
| 0.65 | 2.53 | 2.9471 | 3.1811 | 3.3013 | 3.3599 | 3.3818 | 3.3797 | 3.362 | 3.3342 | 3.2998 | 3.26
| 0.7 | 2.5 | 2.9369 | 3.1766 | 3.3009 | 3.3629 | 3.3863 | 3.3847 | 3.3668 | 3.3385 | 3.3038 | 3.26
| 0.75 | 2.47 | 2.9275 | 3.1724 | 3.301 | 3.366 | 3.3906 | 3.389 | 3.3708 | 3.3423 | 3.3072 | 3.27
| 0.8 | 2.44 | 2.9189 | 3.1685 | 3.3014 | 3.3692 | 3.3945 | 3.3927 | 3.3743 | 3.3455 | 3.3101 | 3.27
| 0.85 | 2.42 | 2.911 | 3.1648 | 3.3023 | 3.3722 | 3.3978 | 3.396 | 3.3773 | 3.3482 | 3.3126 | 3.27
| 0.9 | 2.1 | 2.9037 | 3.1616 | 3.3035 | 3.3751 | 3.4008 | 3.3988 | 3.3799 | 3.3506 | 3.3148 | 3.28
| 0.95 | 2.37 | 2.897 | 3.1588 | 3.3049 | 3.3776 | 3.4034 | 3.4012 | 3.3822 | 3.3527 | 3.3168 | 3.28
| 1 | 2.35 | 2.8906 | 3.1564 | 3.3064 | 3.3798 | 3.4056 | 3.4033 | 3.3842 | 3.3547 | 3.3187 | 3.28
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 4.0967 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1
| 0.05 | 3.1779 | 3.1084 | 3.0493 | 2.9926 | 2.9371 | 2.8834 | 2.8329 | 2.7828 | 2.7341 | 2.6876 | 2.6428
| 0.1 | 2.8174 | 2.7312 | 2.6528 | 2.5777 | 2.5063 | 2.4386 | 2.3762 | 2.3162 | 2.2594 | 2.207 | 2.1569
| 0.15 | 2.5998 | 2.4925 | 2.3996 | 2.3145 | 2.2367 | 2.1642 | 2.0984 | 2.0361 | 1.9786 | 1.9258 | 1.8764
| 0.2 | 2.4596 | 2.3238 | 2.2196 | 2.1291 | 2.0478 | 1.9738 | 1.9069 | 1.8446 | 1.7876 | 1.7355 | 1.6877
| 0.25 | 2.3625 | 2.197 | 2.0825 | 1.9895 | 1.9065 | 1.8311 | 1.7638 | 1.7017 | 1.6452 | 1.5942 | 1.5474
| 0.3 | 2.2907 | 2.0957 | 1.9747 | 1.8792 | 1.794 | 1.7175 | 1.6492 | 1.5876 | 1.5324 | 1.4823 | 1.4368
| 0.35 | 2.2372 | 2.0125 | 1.8862 | 1.7871 | 1.6999 | 1.6219 | 1.554 | 1.4932 | 1.4395 | 1.3903 | 1.3467
| 0.4 | 2.1956 | 1.9405 | 1.8111 | 1.7084 | 1.6197 | 1.5415 | 1.4733 | 1.4133 | 1.361 | 1.3138 | 1.2713
| 0.45 | 2.1608 | 1.8793 | 1.7461 | 1.6394 | 1.5486 | 1.4708 | 1.4037 | 1.3451 | 1.294 | 1.2483 | 1.2073
| 0.5 | 2.1334 | 1.826 | 1.688 | 1.5783 | 1.4864 | 1.4085 | 1.3426 | 1.2856 | 1.2358 | 1.1918 | 1.1519
| 0.55 | 2.1109 | 1.7781 | 1.636 | 1.5228 | 1.43 | 1.3533 | 1.2889 | 1.2335 | 1.1846 | 1.1419 | 1.1037
| 0.6 | 2.0906 | 1.7357 | 1.5887 | 1.4728 | 1.38 | 1.3042 | 1.2415 | 1.1867 | 1.1393 | 1.0979 | 1.0607
| 0.65 | 2.0742 | 1.6975 | 1.545 | 1.4269 | 1.334 | 1.2607 | 1.1981 | 1.1449 | 1.099 | 1.0586 | 1.0226
| 0.7 | 2.06 | 1.6627 | 1.5038 | 1.385 | 1.2933 | 1.2199 | 1.1587 | 1.1077 | 1.063 | 1.0237 | 0.98839
| 0.75 | 2.0466 | 1.6298 | 1.4667 | 1.3464 | 1.2554 | 1.1833 | 1.1238 | 1.0735 | 1.0298 | 0.99127 | 0.95742
| 0.8 | 2.0361 | 1.5997 | 1.4314 | 1.3109 | 1.2209 | 1.1499 | 1.0917 | 1.0422 | 0.99964 | 0.96215 | 0.92903
| 0.85 | 2.0264 | 1.5722 | 1.399 | 1.2778 | 1.1891 | 1.1194 | 1.0619 | 1.0135 | 0.97198 | 0.93558 | 0.90326
| 0.9 | 2.0168 | 1.5457 | 1.3682 | 1.2474 | 1.1595 | 1.0902 | 1.0342 | 0.98726 | 0.94649 | 0.91122 | 0.87956
| 0.95 | 2.0091 | 1.5203 | 1.3393 | 1.2186 | 1.1317 | 1.064 | 1.0095 | 0.96322 | 0.92325 | 0.88863 | 0.85795
| 1 | 2.0024 | 1.4966 | 1.3122 | 1.1916 | 1.1062 | 1.04 | 0.98544 | 0.94031 | 0.90178 | 0.86723 | 0.83723
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.007553 | 0.011488 | 0.014658 | 0.017448 | 0.019928 | 0.022015 | 0.023406 | 0.025256 | 0.026553 | 0.027747 | 0.028669
| 0.1 | 0.0092734 | 0.01538 | 0.019468 | 0.022343 | 0.024664 | 0.026462 | 0.027788 | 0.029104 | 0.029922 | 0.030642 | 0.031227
| 0.15 | 0.0064225 | 0.016011 | 0.020566 | 0.02373 | 0.026228 | 0.028004 | 0.029254 | 0.030168 | 0.030712 | 0.031232 | 0.031374
| 0.2 | 0.0038195 | 0.015723 | 0.021077 | 0.025082 | 0.027581 | 0.029205 | 0.030387 | 0.030891 | 0.031016 | 0.031161 | 0.031044
| 0.25 | 0.0010306 | 0.015829 | 0.021919 | 0.026354 | 0.028819 | 0.030086 | 0.030772 | 0.030813 | 0.030805 | 0.030553 | 0.030181
| 0.3 | -0.0015557 | 0.015845 | 0.023158 | 0.027308 | 0.02943 | 0.03026 | 0.030453 | 0.030461 | 0.030157 | 0.02966 | 0.029169
| 0.35 | -0.0030228 | 0.015835 | 0.02422 | 0.028002 | 0.029761 | 0.030169 | 0.030057 | 0.029668 | 0.029387 | 0.028708 | 0.028247
| 0.4 | -0.0048595 | 0.016248 | 0.024977 | 0.028531 | 0.029623 | 0.029859 | 0.029468 | 0.029028 | 0.028333 | 0.027701 | 0.027158
| 0.45 | -0.0061188 | 0.016951 | 0.025615 | 0.028686 | 0.029351 | 0.029167 | 0.028843 | 0.028063 | 0.027339 | 0.02678 | 0.025959
| 0.5 | -0.0070983 | 0.017419 | 0.025913 | 0.028565 | 0.028954 | 0.028702 | 0.027852 | 0.02722 | 0.026492 | 0.025788 | 0.025279
| 0.55 | -0.0078917 | 0.017897 | 0.026471 | 0.028537 | 0.028472 | 0.027933 | 0.027159 | 0.026567 | 0.025691 | 0.024912 | 0.024319
| 0.6 | -0.0086252 | 0.018578 | 0.026733 | 0.028191 | 0.028071 | 0.027391 | 0.026492 | 0.025749 | 0.024828 | 0.02414 | 0.023467
| 0.65 | -0.0092179 | 0.019121 | 0.026606 | 0.027903 | 0.027514 | 0.026699 | 0.025707 | 0.02483 | 0.024127 | 0.023474 | 0.022679
| 0.7 | -0.0095541 | 0.019592 | 0.026771 | 0.027677 | 0.027024 | 0.026073 | 0.025233 | 0.024274 | 0.023609 | 0.022754 | 0.02205
| 0.75 | -0.010091 | 0.019998 | 0.026595 | 0.027254 | 0.026489 | 0.025454 | 0.024476 | 0.023657 | 0.022879 | 0.022114 | 0.021515
| 0.8 | -0.010728 | 0.020497 | 0.026647 | 0.026878 | 0.026023 | 0.024929 | 0.023834 | 0.022973 | 0.022265 | 0.021511 | 0.020951
| 0.85 | -0.0107 | 0.020902 | 0.026565 | 0.026504 | 0.02535 | 0.024364 | 0.02341 | 0.022536 | 0.02163 | 0.020985 | 0.020349
| 0.9 | -0.010979 | 0.021257 | 0.026298 | 0.026142 | 0.024856 | 0.023928 | 0.022896 | 0.022006 | 0.021238 | 0.020705 | 0.020015
| 0.95 | -0.011493 | 0.021515 | 0.025966 | 0.025552 | 0.024384 | 0.023338 | 0.022403 | 0.021435 | 0.020703 | 0.020077 | 0.01965
| 1 | -0.01174 | 0.021713 | 0.026092 | 0.025219 | 0.023919 | 0.022944 | 0.021968 | 0.021072 | 0.020419 | 0.019839 | 0.019187
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.004533 | 0.0049978 | 0.0054219 | 0.0058156 | 0.0061512 | 0.0064492 | 0.0067189 | 0.0069519 | 0.0071266 | 0.0072911 | 0.0074224
| 0.1 | 0.0054313 | 0.0062014 | 0.0066621 | 0.0069687 | 0.0071814 | 0.0073343 | 0.0074621 | 0.0075512 | 0.0076087 | 0.0076554 | 0.0076666
| 0.15 | 0.0051788 | 0.0063427 | 0.006764 | 0.006994 | 0.0071507 | 0.0072528 | 0.0073098 | 0.0073488 | 0.007364 | 0.0073439 | 0.0073065
| 0.2 | 0.0045818 | 0.006211 | 0.0066295 | 0.006813 | 0.0069627 | 0.0070585 | 0.0071213 | 0.0071385 | 0.0071271 | 0.0070695 | 0.0070151
| 0.25 | 0.0040538 | 0.0060123 | 0.0064332 | 0.0066618 | 0.0068473 | 0.006962 | 0.0070037 | 0.0069765 | 0.0069159 | 0.0068588 | 0.0067606
| 0.3 | 0.0035815 | 0.0058765 | 0.0062595 | 0.0066096 | 0.0067998 | 0.0068796 | 0.0068838 | 0.0068291 | 0.0067247 | 0.006631 | 0.0065097
| 0.35 | 0.0031997 | 0.0057095 | 0.0061625 | 0.0065732 | 0.006761 | 0.0067961 | 0.006749 | 0.0066464 | 0.0065276 | 0.006398 | 0.0062678
| 0.4 | 0.0028146 | 0.0055616 | 0.0061482 | 0.0065723 | 0.0067035 | 0.0066795 | 0.0065789 | 0.0064575 | 0.0063217 | 0.0061799 | 0.0060238
| 0.45 | 0.0025174 | 0.0054457 | 0.0061302 | 0.0065391 | 0.0066161 | 0.0065356 | 0.0064197 | 0.0062475 | 0.0061178 | 0.005957 | 0.0058126
| 0.5 | 0.0022894 | 0.0053365 | 0.0061494 | 0.0064854 | 0.0065156 | 0.0063937 | 0.0062531 | 0.0060718 | 0.0059163 | 0.0057587 | 0.0056167
| 0.55 | 0.0020439 | 0.0052631 | 0.0061651 | 0.0064466 | 0.006417 | 0.0062655 | 0.006082 | 0.0059101 | 0.0057353 | 0.0055619 | 0.0054337
| 0.6 | 0.0018807 | 0.0052219 | 0.0061399 | 0.0063593 | 0.0062979 | 0.0061182 | 0.0059327 | 0.0057442 | 0.0055658 | 0.0054031 | 0.0052432
| 0.65 | 0.0017187 | 0.0051891 | 0.0061331 | 0.0062917 | 0.0061649 | 0.005985 | 0.005794 | 0.0055891 | 0.0054073 | 0.0052502 | 0.0050875
| 0.7 | 0.0016097 | 0.0051617 | 0.0061092 | 0.0061984 | 0.0060521 | 0.0058543 | 0.0056473 | 0.0054458 | 0.0052614 | 0.0051046 | 0.0049514
| 0.75 | 0.0014367 | 0.0051775 | 0.0060814 | 0.0061136 | 0.0059399 | 0.0057112 | 0.0055034 | 0.0053061 | 0.0051203 | 0.0049576 | 0.0048073
| 0.8 | 0.0013217 | 0.0051736 | 0.006036 | 0.0060173 | 0.0058315 | 0.0056032 | 0.0053772 | 0.0051693 | 0.0049965 | 0.0048236 | 0.0046865
| 0.85 | 0.0012441 | 0.0052128 | 0.0059908 | 0.0059286 | 0.0057164 | 0.0054852 | 0.0052612 | 0.005053 | 0.0048744 | 0.0047034 | 0.0045581
| 0.9 | 0.0011494 | 0.0052142 | 0.0059313 | 0.0058506 | 0.0056077 | 0.0053764 | 0.0051416 | 0.0049362 | 0.0047679 | 0.0046148 | 0.0044521
| 0.95 | 0.0010569 | 0.0052215 | 0.0058886 | 0.0057569 | 0.0055104 | 0.0052682 | 0.0050195 | 0.0048302 | 0.0046694 | 0.0044985 | 0.0043632
| 1 | 0.00097184 | 0.0052571 | 0.0058327 | 0.0056814 | 0.0054124 | 0.0051444 | 0.0049303 | 0.0047258 | 0.0045489 | 0.0044069 | 0.0042626
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.3303 | 1.595 | 1.8077 | 1.9804 | 2.1238 | 2.2412 | 2.333 | 2.4162 | 2.4846 | 2.5465 | 2.5945
| 0.1 | 1.3099 | 1.8945 | 2.3271 | 2.6754 | 2.8983 | 3.1154 | 3.2468 | 3.3916 | 3.4725 | 3.5554 | 3.6386
| 0.15 | 1.2265 | 2.1201 | 2.6755 | 3.1432 | 3.4309 | 3.8207 | 4.0589 | 4.1374 | 4.2604 | 4.3601 | 4.4386
| 0.2 | 1.1409 | 2.3179 | 3.0895 | 3.6323 | 4.0686 | 4.3795 | 4.6111 | 4.7952 | 4.7198 | 5.0505 | 5.1272
| 0.25 | 1.0779 | 2.5194 | 3.42 | 4.0632 | 4.5321 | 4.8999 | 5.1627 | 5.3784 | 5.535 | 5.6494 | 5.7433
| 0.3 | 1.0416 | 2.6924 | 3.7343 | 4.4801 | 5.0078 | 5.3814 | 5.6802 | 5.9014 | 6.0728 | 6.1927 | 6.2923
| 0.35 | 1.0094 | 2.869 | 4.0312 | 4.8395 | 5.376 | 5.8131 | 6.1301 | 6.3747 | 6.5503 | 6.6801 | 6.7954
| 0.4 | 0.9811 | 3.0504 | 4.3237 | 5.1776 | 5.7874 | 6.2297 | 6.5539 | 6.8097 | 6.9928 | 7.1398 | 7.2427
| 0.45 | 0.96786 | 3.2045 | 4.5722 | 5.486 | 6.1407 | 6.606 | 6.9457 | 7.2117 | 7.4135 | 7.5706 | 7.6765
| 0.5 | 0.95197 | 3.3618 | 4.8348 | 5.7945 | 6.4615 | 6.9575 | 7.3181 | 7.6 | 7.8066 | 7.9597 | 8.0831
| 0.55 | 0.93558 | 3.5334 | 5.0713 | 6.0649 | 6.7802 | 7.2816 | 7.6663 | 7.9528 | 8.1769 | 8.339 | 8.4632
| 0.6 | 0.93149 | 3.6679 | 5.3027 | 6.3355 | 7.0705 | 7.5975 | 7.9976 | 8.2894 | 8.5267 | 8.7017 | 8.8312
| 0.65 | 0.91954 | 3.83 | 5.5088 | 6.5915 | 7.3386 | 7.8981 | 8.3097 | 8.6241 | 8.8674 | 9.0486 | 9.1873
| 0.7 | 0.90895 | 3.9732 | 5.7226 | 6.8252 | 7.6042 | 8.173 | 8.6076 | 8.9402 | 9.1879 | 9.3762 | 9.5287
| 0.75 | 0.90932 | 4.1067 | 5.9182 | 7.0583 | 7.8612 | 8.4517 | 8.9039 | 9.2433 | 9.5012 | 9.6958 | 9.8481
| 0.8 | 0.89962 | 4.2544 | 6.1002 | 7.2702 | 8.1029 | 8.705 | 9.1861 | 9.5373 | 9.8059 | 10.0074 | 10.1624
| 0.85 | 0.89052 | 4.3877 | 6.2803 | 7.4634 | 8.3412 | 8.977 | 9.4559 | 9.8205 | 10.0982 | 10.3117 | 10.4741
| 0.9 | 0.89299 | 4.5156 | 6.4435 | 7.6846 | 8.5698 | 9.2192 | 9.717 | 10.0979 | 10.3832 | 10.6083 | 10.7738
| 0.95 | 0.88494 | 4.6383 | 6.6193 | 7.8825 | 8.7883 | 9.458 | 9.9778 | 10.368 | 10.6655 | 10.8862 | 11.0609
| 1 | 0.87925 | 4.7584 | 6.7847 | 8.0812 | 9.006 | 9.7025 | 10.2246 | 10.6272 | 10.93 | 11.1614 | 11.3426
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0031316 | -0.0011301 | 0.00043156 | 0.0026968 | 0.0052471 | 0.00707 | 0.010407 | 0.01101 | 0.013108 | 0.015041 | 0.016065
| 0.1 | 0.00091112 | 0.0051015 | 0.010143 | 0.014242 | 0.018472 | 0.026652 | 0.024401 | 0.027987 | 0.03353 | 0.036052 | 0.036331
| 0.15 | 0.00036667 | 0.0085789 | 0.01799 | 0.022431 | 0.030361 | 0.038817 | 0.042472 | 0.045341 | 0.053218 | 0.053544 | 0.057008
| 0.2 | -0.0043506 | 0.012341 | 0.025837 | 0.033967 | 0.044719 | 0.054949 | 0.060544 | 0.061712 | 0.072543 | 0.076639 | 0.084946
| 0.25 | -0.0071191 | 0.015663 | 0.033684 | 0.041088 | 0.059078 | 0.070148 | 0.078616 | 0.085807 | 0.090672 | 0.096033 | 0.096247
| 0.3 | -0.0082421 | 0.018986 | 0.041531 | 0.057399 | 0.073436 | 0.085346 | 0.096688 | 0.10535 | 0.10367 | 0.10906 | 0.1162
| 0.35 | -0.011983 | 0.022308 | 0.049378 | 0.073404 | 0.087795 | 0.10055 | 0.11383 | 0.11789 | 0.12008 | 0.12333 | 0.12317
| 0.4 | -0.011744 | 0.02563 | 0.057225 | 0.087784 | 0.10215 | 0.11549 | 0.12132 | 0.12821 | 0.13139 | 0.13545 | 0.13701
| 0.45 | -0.013185 | 0.028953 | 0.065072 | 0.091954 | 0.11356 | 0.12515 | 0.13403 | 0.13995 | 0.14403 | 0.14727 | 0.14895
| 0.5 | -0.014475 | 0.032275 | 0.072919 | 0.1028 | 0.12334 | 0.13398 | 0.14171 | 0.14691 | 0.15317 | 0.15565 | 0.15884
| 0.55 | -0.015788 | 0.035598 | 0.080877 | 0.11309 | 0.13295 | 0.14302 | 0.15116 | 0.1574 | 0.16326 | 0.16647 | 0.16836
| 0.6 | -0.016881 | 0.03892 | 0.092317 | 0.12134 | 0.14108 | 0.15209 | 0.16062 | 0.16503 | 0.16945 | 0.17579 | 0.17653
| 0.65 | -0.016695 | 0.042242 | 0.096022 | 0.12763 | 0.14651 | 0.15943 | 0.16717 | 0.17291 | 0.17754 | 0.1835 | 0.18536
| 0.7 | -0.017475 | 0.045565 | 0.10334 | 0.1351 | 0.15341 | 0.16689 | 0.17733 | 0.18216 | 0.18818 | 0.1905 | 0.19395
| 0.75 | -0.018148 | 0.049467 | 0.10655 | 0.13981 | 0.16034 | 0.17365 | 0.18285 | 0.18973 | 0.19592 | 0.19815 | 0.20277
| 0.8 | -0.01688 | 0.054094 | 0.11294 | 0.14529 | 0.16627 | 0.18039 | 0.18926 | 0.19592 | 0.20291 | 0.20757 | 0.21005
| 0.85 | -0.018734 | 0.05201 | 0.12141 | 0.1518 | 0.17171 | 0.18641 | 0.19691 | 0.20435 | 0.20883 | 0.21341 | 0.21664
| 0.9 | -0.019411 | 0.057161 | 0.12602 | 0.15922 | 0.17741 | 0.19333 | 0.2038 | 0.21083 | 0.21508 | 0.22319 | 0.22568
| 0.95 | -0.018059 | 0.065486 | 0.12968 | 0.16327 | 0.18233 | 0.19803 | 0.2098 | 0.21693 | 0.22105 | 0.22751 | 0.23416
| 1 | -0.018236 | 0.073812 | 0.13847 | 0.16858 | 0.18937 | 0.2046 | 0.21562 | 0.22191 | 0.22963 | 0.23704 | 0.2389
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0016675 | -0.0047474 | -0.0069572 | -0.0085816 | -0.0098708 | -0.010733 | -0.01148 | -0.012005 | -0.012328 | -0.012582 | -0.012842
| 0.1 | 0.00084407 | -0.0054089 | -0.0098573 | -0.012762 | -0.014495 | -0.016603 | -0.016892 | -0.017956 | -0.018515 | -0.018636 | -0.019036
| 0.15 | 0.0017766 | -0.0068689 | -0.01216 | -0.016544 | -0.019473 | -0.020068 | -0.021296 | -0.021571 | -0.022524 | -0.02329 | -0.023089
| 0.2 | 0.0022557 | -0.0099008 | -0.013714 | -0.019184 | -0.02156 | -0.023534 | -0.025381 | -0.025776 | -0.026172 | -0.028324 | -0.027038
| 0.25 | 0.001929 | -0.010488 | -0.015268 | -0.021824 | -0.023647 | -0.026404 | -0.028654 | -0.029237 | -0.029821 | -0.031249 | -0.030986
| 0.3 | 0.0017152 | -0.012978 | -0.017471 | -0.024464 | -0.025735 | -0.029274 | -0.031143 | -0.032018 | -0.032542 | -0.033364 | -0.033328
| 0.35 | 0.0013198 | -0.013399 | -0.021087 | -0.026139 | -0.027822 | -0.030742 | -0.032565 | -0.034141 | -0.034551 | -0.035388 | -0.035857
| 0.4 | 0.0013603 | -0.014459 | -0.022596 | -0.027002 | -0.030336 | -0.03282 | -0.034739 | -0.036112 | -0.037224 | -0.037547 | -0.038564
| 0.45 | 0.0012511 | -0.01552 | -0.024876 | -0.028819 | -0.032271 | -0.034536 | -0.036347 | -0.037971 | -0.039065 | -0.039779 | -0.040626
| 0.5 | 0.00080866 | -0.016722 | -0.025733 | -0.02947 | -0.033577 | -0.036102 | -0.038218 | -0.039708 | -0.041163 | -0.041849 | -0.042762
| 0.55 | 0.00091992 | -0.017875 | -0.026389 | -0.031222 | -0.034861 | -0.037942 | -0.040088 | -0.041536 | -0.042852 | -0.043924 | -0.044657
| 0.6 | 0.00067612 | -0.019824 | -0.027148 | -0.032342 | -0.036196 | -0.03892 | -0.041559 | -0.043297 | -0.044725 | -0.045882 | -0.046674
| 0.65 | 0.00054623 | -0.020158 | -0.027919 | -0.033319 | -0.03771 | -0.040524 | -0.043403 | -0.045224 | -0.046646 | -0.047726 | -0.048551
| 0.7 | 0.0002636 | -0.020774 | -0.028741 | -0.034555 | -0.038658 | -0.042008 | -0.044813 | -0.047115 | -0.048469 | -0.049647 | -0.0507
| 0.75 | 0.00041474 | -0.021479 | -0.029702 | -0.035541 | -0.039828 | -0.043595 | -0.046418 | -0.048703 | -0.050293 | -0.051258 | -0.052363
| 0.8 | 0.00037067 | -0.022301 | -0.03077 | -0.036489 | -0.041001 | -0.045019 | -0.048067 | -0.050342 | -0.051755 | -0.053229 | -0.054097
| 0.85 | 0.00017807 | -0.023595 | -0.031304 | -0.03748 | -0.043274 | -0.046268 | -0.049522 | -0.051701 | -0.053577 | -0.055197 | -0.055832
| 0.9 | 7.7039e-05 | -0.023425 | -0.031828 | -0.038364 | -0.043834 | -0.047662 | -0.051084 | -0.053271 | -0.054987 | -0.05654 | -0.05772
| 0.95 | 6.642e-05 | -0.024236 | -0.032659 | -0.039466 | -0.045016 | -0.049315 | -0.052643 | -0.054822 | -0.056631 | -0.058187 | -0.059227
| 1 | -9.495e-06 | -0.025742 | -0.033421 | -0.040356 | -0.04619 | -0.050544 | -0.054003 | -0.056286 | -0.058455 | -0.059616 | -0.060631
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41)
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41)
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41)

## CLASS5_OOP (hidden)
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
| 0.05 | 2.8929 | 2.9331 | 2.9647 | 2.987 | 3.001 | 3.0078 | 3.0087 | 3.0048 | 2.997 | 2.9862 | 2.973
| 0.1 | 2.9215 | 3.0172 | 3.0914 | 3.1392 | 3.1651 | 3.1746 | 3.1722 | 3.1612 | 3.144 | 3.1225 | 3.0978
| 0.15 | 2.9203 | 3.0261 | 3.1381 | 3.204 | 3.2366 | 3.2468 | 3.2419 | 3.2268 | 3.2047 | 3.1779 | 3.1478
| 0.2 | 2.8873 | 3.0318 | 3.1552 | 3.2349 | 3.2727 | 3.2839 | 3.278 | 3.2609 | 3.2364 | 3.2069 | 3.1743
| 0.25 | 2.8389 | 3.026 | 3.1605 | 3.2508 | 3.2928 | 3.3053 | 3.2995 | 3.2818 | 3.2564 | 3.2259 | 3.192
| 0.3 | 2.785 | 3.0142 | 3.1649 | 3.2591 | 3.3049 | 3.3194 | 3.3145 | 3.2971 | 3.2715 | 3.2406 | 3.206
| 0.35 | 2.7306 | 3.0001 | 3.169 | 3.2635 | 3.3133 | 3.3302 | 3.3266 | 3.3097 | 3.2841 | 3.2527 | 3.2175
| 0.4 | 2.6783 | 2.9858 | 3.1701 | 3.266 | 3.32 | 3.3394 | 3.337 | 3.3204 | 3.2946 | 3.2627 | 3.2269
| 0.45 | 2.6291 | 2.972 | 3.1693 | 3.2695 | 3.326 | 3.3476 | 3.346 | 3.3295 | 3.3034 | 3.271 | 3.2346
| 0.5 | 2.5836 | 2.9591 | 3.1674 | 3.2721 | 3.3316 | 3.3549 | 3.3538 | 3.3373 | 3.3108 | 3.2779 | 3.2409
| 0.55 | 2.5417 | 2.9472 | 3.1648 | 3.2738 | 3.3368 | 3.3613 | 3.3605 | 3.3438 | 3.3169 | 3.2836 | 3.2462
| 0.6 | 2.5034 | 2.9363 | 3.1618 | 3.275 | 3.3416 | 3.367 | 3.3662 | 3.3493 | 3.3221 | 3.2884 | 3.2506
| 0.65 | 2.4684 | 2.9263 | 3.1586 | 3.2762 | 3.3459 | 3.3718 | 3.3711 | 3.354 | 3.3265 | 3.2926 | 3.2545
| 0.7 | 2.4363 | 2.9171 | 3.1554 | 3.2785 | 3.3498 | 3.3761 | 3.3753 | 3.358 | 3.3304 | 3.2962 | 3.2579
| 0.75 | 2.407 | 2.9087 | 3.1523 | 3.2806 | 3.3532 | 3.3797 | 3.379 | 3.3616 | 3.3338 | 3.2995 | 3.261
| 0.8 | 2.3801 | 2.9009 | 3.1494 | 3.2827 | 3.3561 | 3.3829 | 3.3822 | 3.3648 | 3.3369 | 3.3025 | 3.2639
| 0.85 | 2.3555 | 2.8936 | 3.1468 | 3.2846 | 3.3587 | 3.3857 | 3.3851 | 3.3677 | 3.3398 | 3.3052 | 3.2664
| 0.9 | 2.3328 | 2.8869 | 3.1444 | 3.2862 | 3.361 | 3.3882 | 3.3877 | 3.3703 | 3.3424 | 3.3077 | 3.2688
| 0.95 | 2.3119 | 2.8806 | 3.1424 | 3.2877 | 3.363 | 3.3905 | 3.3901 | 3.3728 | 3.3448 | 3.31 | 3.271
| 1 | 2.2926 | 2.8748 | 3.1406 | 3.2891 | 3.3648 | 3.3926 | 3.3924 | 3.3751 | 3.3471 | 3.3122 | 3.273
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7
| 0.05 | 3.7843 | 3.7102 | 3.6368 | 3.5644 | 3.4938 | 3.4257 | 3.3609 | 3.3004 | 3.2404 | 3.1834 | 3.129
| 0.1 | 3.3726 | 3.2618 | 3.1592 | 3.0638 | 2.9745 | 2.8918 | 2.8151 | 2.7421 | 2.6745 | 2.6106 | 2.5511
| 0.15 | 3.1249 | 2.9781 | 2.8577 | 2.752 | 2.6555 | 2.5679 | 2.4878 | 2.4117 | 2.3435 | 2.2789 | 2.2201
| 0.2 | 2.9619 | 2.777 | 2.6458 | 2.5335 | 2.4339 | 2.3421 | 2.2606 | 2.1848 | 2.1157 | 2.0524 | 1.9942
| 0.25 | 2.8498 | 2.6263 | 2.485 | 2.3683 | 2.2648 | 2.1702 | 2.088 | 2.0122 | 1.9446 | 1.8828 | 1.8275
| 0.3 | 2.7687 | 2.5058 | 2.3567 | 2.235 | 2.1273 | 2.0326 | 1.9489 | 1.8748 | 1.8085 | 1.7489 | 1.6947
| 0.35 | 2.7051 | 2.4068 | 2.2505 | 2.1229 | 2.0123 | 1.9171 | 1.8345 | 1.7626 | 1.6968 | 1.64 | 1.5884
| 0.4 | 2.6571 | 2.3232 | 2.1594 | 2.0261 | 1.9144 | 1.8192 | 1.7385 | 1.6667 | 1.6043 | 1.5486 | 1.4989
| 0.45 | 2.6185 | 2.2503 | 2.0793 | 1.941 | 1.8291 | 1.7346 | 1.6553 | 1.5863 | 1.5257 | 1.4712 | 1.4234
| 0.5 | 2.5872 | 2.1871 | 2.0072 | 1.8664 | 1.7534 | 1.6611 | 1.5832 | 1.5153 | 1.4571 | 1.4041 | 1.3583
| 0.55 | 2.5588 | 2.1303 | 1.9417 | 1.7997 | 1.6873 | 1.5953 | 1.5201 | 1.4535 | 1.3971 | 1.3458 | 1.3011
| 0.6 | 2.5367 | 2.0796 | 1.8827 | 1.739 | 1.6274 | 1.5377 | 1.4632 | 1.3989 | 1.3437 | 1.2949 | 1.2504
| 0.65 | 2.5179 | 2.0322 | 1.8293 | 1.6842 | 1.573 | 1.4849 | 1.412 | 1.3498 | 1.2961 | 1.2482 | 1.2061
| 0.7 | 2.5001 | 1.9891 | 1.7798 | 1.6339 | 1.5244 | 1.4383 | 1.3667 | 1.3057 | 1.2534 | 1.2067 | 1.1653
| 0.75 | 2.4855 | 1.9492 | 1.7344 | 1.5879 | 1.4804 | 1.3951 | 1.3253 | 1.2655 | 1.2147 | 1.169 | 1.1288
| 0.8 | 2.4731 | 1.9117 | 1.6909 | 1.5454 | 1.4396 | 1.3559 | 1.2869 | 1.2292 | 1.179 | 1.1346 | 1.0961
| 0.85 | 2.4603 | 1.876 | 1.6524 | 1.5068 | 1.4016 | 1.3193 | 1.2517 | 1.1958 | 1.1463 | 1.1041 | 1.0662
| 0.9 | 2.4511 | 1.8429 | 1.6157 | 1.4701 | 1.3668 | 1.2861 | 1.2204 | 1.1651 | 1.1164 | 1.075 | 1.0378
| 0.95 | 2.4419 | 1.8115 | 1.5809 | 1.4364 | 1.3339 | 1.2547 | 1.1907 | 1.136 | 1.0888 | 1.048 | 1.0123
| 1 | 2.434 | 1.7818 | 1.5489 | 1.4053 | 1.3033 | 1.2263 | 1.163 | 1.1091 | 1.0633 | 1.0233 | 0.98792
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.019632 | 0.02195 | 0.023995 | 0.025839 | 0.027401 | 0.028784 | 0.030355 | 0.031291 | 0.032193 | 0.032828 | 0.033447
| 0.1 | 0.022063 | 0.025541 | 0.027818 | 0.029654 | 0.030988 | 0.032011 | 0.033218 | 0.03382 | 0.034002 | 0.03433 | 0.034566
| 0.15 | 0.020575 | 0.025526 | 0.028277 | 0.030282 | 0.031818 | 0.032921 | 0.033912 | 0.034292 | 0.03419 | 0.034218 | 0.034086
| 0.2 | 0.017421 | 0.024865 | 0.028467 | 0.030887 | 0.032591 | 0.033548 | 0.034058 | 0.033972 | 0.033716 | 0.033636 | 0.033241
| 0.25 | 0.014878 | 0.024323 | 0.028761 | 0.031594 | 0.033037 | 0.033623 | 0.033684 | 0.033233 | 0.032959 | 0.032586 | 0.032001
| 0.3 | 0.012646 | 0.024 | 0.029158 | 0.032068 | 0.033013 | 0.033098 | 0.032976 | 0.032391 | 0.031718 | 0.031306 | 0.030553
| 0.35 | 0.011007 | 0.02376 | 0.029765 | 0.032222 | 0.032706 | 0.032394 | 0.032045 | 0.031324 | 0.030782 | 0.030013 | 0.029308
| 0.4 | 0.0095018 | 0.023718 | 0.030171 | 0.032067 | 0.032169 | 0.031715 | 0.031262 | 0.030278 | 0.029644 | 0.028878 | 0.02805
| 0.45 | 0.008128 | 0.024145 | 0.030259 | 0.031782 | 0.031655 | 0.030949 | 0.030092 | 0.029276 | 0.028402 | 0.027536 | 0.026924
| 0.5 | 0.0067351 | 0.024397 | 0.030206 | 0.031415 | 0.030943 | 0.030014 | 0.029202 | 0.028267 | 0.0275 | 0.026812 | 0.025912
| 0.55 | 0.0062198 | 0.024735 | 0.030217 | 0.030892 | 0.030297 | 0.029351 | 0.0283 | 0.027584 | 0.02644 | 0.025827 | 0.025073
| 0.6 | 0.0054262 | 0.024863 | 0.030098 | 0.030504 | 0.029585 | 0.028583 | 0.02744 | 0.026613 | 0.025683 | 0.025038 | 0.024185
| 0.65 | 0.0043688 | 0.025287 | 0.029933 | 0.029853 | 0.028802 | 0.027762 | 0.026667 | 0.025808 | 0.024917 | 0.024308 | 0.02357
| 0.7 | 0.003791 | 0.025535 | 0.029691 | 0.029218 | 0.02828 | 0.02703 | 0.02607 | 0.025113 | 0.024422 | 0.02348 | 0.022898
| 0.75 | 0.0036128 | 0.025768 | 0.029181 | 0.028701 | 0.027589 | 0.026339 | 0.02535 | 0.024462 | 0.023681 | 0.023011 | 0.022312
| 0.8 | 0.0028346 | 0.025796 | 0.028983 | 0.028196 | 0.02703 | 0.025785 | 0.02471 | 0.023718 | 0.02304 | 0.022228 | 0.021689
| 0.85 | 0.002371 | 0.0258 | 0.02889 | 0.027746 | 0.026481 | 0.025114 | 0.024149 | 0.023268 | 0.022531 | 0.021749 | 0.021227
| 0.9 | 0.0019773 | 0.026098 | 0.02846 | 0.027274 | 0.025794 | 0.024686 | 0.023695 | 0.022644 | 0.021945 | 0.021237 | 0.020635
| 0.95 | 0.0017631 | 0.026025 | 0.027977 | 0.02682 | 0.025283 | 0.024107 | 0.023129 | 0.022209 | 0.021511 | 0.020863 | 0.02029
| 1 | 0.0014708 | 0.026136 | 0.027758 | 0.026226 | 0.024846 | 0.02362 | 0.022604 | 0.021759 | 0.021102 | 0.020348 | 0.019796
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0044966 | 0.0048532 | 0.0052124 | 0.0055266 | 0.0058132 | 0.0060703 | 0.0063326 | 0.0065346 | 0.0066876 | 0.0068123 | 0.0069344
| 0.1 | 0.0052173 | 0.0058439 | 0.0062315 | 0.0064587 | 0.0066571 | 0.0068049 | 0.0069534 | 0.0070182 | 0.0070707 | 0.0071104 | 0.0070982
| 0.15 | 0.0049006 | 0.0059165 | 0.0063324 | 0.0065507 | 0.0066584 | 0.0067497 | 0.0068377 | 0.0068761 | 0.0068706 | 0.006843 | 0.0068207
| 0.2 | 0.0043464 | 0.0058134 | 0.0062117 | 0.0064132 | 0.0065355 | 0.0066206 | 0.0067124 | 0.0067135 | 0.006673 | 0.0066039 | 0.0065504
| 0.25 | 0.0038952 | 0.005666 | 0.0060622 | 0.0063119 | 0.0064848 | 0.0065337 | 0.0066036 | 0.006538 | 0.0064647 | 0.0064182 | 0.0063215
| 0.3 | 0.0034852 | 0.0055338 | 0.0059624 | 0.0062442 | 0.0064433 | 0.0064467 | 0.006448 | 0.006339 | 0.0062627 | 0.0061684 | 0.0060444
| 0.35 | 0.003173 | 0.0053975 | 0.0058909 | 0.0062387 | 0.0063571 | 0.0063529 | 0.0062964 | 0.0061921 | 0.0060682 | 0.00594 | 0.0058343
| 0.4 | 0.0028021 | 0.0052908 | 0.0058643 | 0.0062149 | 0.0062663 | 0.0062388 | 0.0061348 | 0.0059903 | 0.0058826 | 0.0057579 | 0.0056144
| 0.45 | 0.0025466 | 0.0052075 | 0.0058449 | 0.0061316 | 0.0061775 | 0.006089 | 0.0059742 | 0.0058286 | 0.0056898 | 0.0055229 | 0.0053956
| 0.5 | 0.0023743 | 0.005115 | 0.0058368 | 0.006076 | 0.0060819 | 0.0059577 | 0.0058248 | 0.0056675 | 0.0055107 | 0.0053553 | 0.0052256
| 0.55 | 0.0021796 | 0.0050477 | 0.0058498 | 0.0060248 | 0.0059707 | 0.0058407 | 0.0056675 | 0.0055004 | 0.0053386 | 0.0051847 | 0.0050534
| 0.6 | 0.0019619 | 0.0050452 | 0.0057891 | 0.0059394 | 0.0058697 | 0.0056867 | 0.005533 | 0.0053646 | 0.0051821 | 0.0050398 | 0.0048929
| 0.65 | 0.0018673 | 0.0050154 | 0.005763 | 0.0058644 | 0.0057307 | 0.0055694 | 0.0053775 | 0.0051887 | 0.005052 | 0.0048767 | 0.0047264
| 0.7 | 0.001742 | 0.0050036 | 0.0057348 | 0.0057861 | 0.0056544 | 0.0054537 | 0.0052607 | 0.0050777 | 0.0048997 | 0.0047481 | 0.0046015
| 0.75 | 0.0016232 | 0.0049845 | 0.0056891 | 0.0057023 | 0.0055279 | 0.0053339 | 0.0051258 | 0.0049491 | 0.0047865 | 0.0046042 | 0.0044617
| 0.8 | 0.0015272 | 0.0050033 | 0.0056455 | 0.00562 | 0.0054378 | 0.0052135 | 0.005007 | 0.0048259 | 0.0046385 | 0.0044924 | 0.0043656
| 0.85 | 0.0014252 | 0.0049971 | 0.0056175 | 0.0055412 | 0.0053442 | 0.005095 | 0.0048858 | 0.004731 | 0.0045088 | 0.0043834 | 0.0042591
| 0.9 | 0.0013517 | 0.0050052 | 0.0055572 | 0.0054441 | 0.0052205 | 0.0050026 | 0.0048029 | 0.0046051 | 0.0044453 | 0.0042868 | 0.0041537
| 0.95 | 0.0013115 | 0.005029 | 0.005501 | 0.0053901 | 0.0051359 | 0.0049007 | 0.0046814 | 0.0044928 | 0.0043499 | 0.0042007 | 0.0040497
| 1 | 0.0012049 | 0.00501 | 0.0054438 | 0.0053055 | 0.0050285 | 0.0047818 | 0.0045901 | 0.0044066 | 0.0042479 | 0.0041044 | 0.0039772
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.4332 | 1.6302 | 1.7873 | 1.9175 | 2.0252 | 2.1148 | 2.1927 | 2.2462 | 2.2994 | 2.3448 | 2.3831
| 0.1 | 1.448 | 1.9044 | 2.2436 | 2.5044 | 2.709 | 2.8708 | 3.0073 | 3.0975 | 3.1829 | 3.265 | 3.3082
| 0.15 | 1.3967 | 2.1059 | 2.6167 | 2.9814 | 3.2791 | 3.5115 | 3.6782 | 3.7897 | 3.9006 | 3.9847 | 4.0517
| 0.2 | 1.3504 | 2.2883 | 2.9287 | 3.4014 | 3.7398 | 4.0278 | 4.2063 | 4.3899 | 4.5149 | 4.612 | 4.6858
| 0.25 | 1.3039 | 2.4557 | 3.2243 | 3.7867 | 4.2004 | 4.5064 | 4.7343 | 4.9137 | 5.0564 | 5.1633 | 5.2856
| 0.3 | 1.2666 | 2.6104 | 3.5357 | 4.1372 | 4.5965 | 4.9399 | 5.1865 | 5.3869 | 5.4441 | 5.647 | 5.7315
| 0.35 | 1.2445 | 2.8021 | 3.8645 | 4.4615 | 4.9607 | 5.3214 | 5.5884 | 5.8201 | 5.98 | 6.0939 | 6.1952
| 0.4 | 1.2194 | 2.927 | 3.968 | 4.7963 | 5.2966 | 5.6923 | 5.9857 | 6.2139 | 6.377 | 6.5173 | 6.6238
| 0.45 | 1.1996 | 3.0787 | 4.1359 | 5.0367 | 5.6093 | 6.0298 | 6.3375 | 6.5889 | 6.7685 | 6.9056 | 7.0098
| 0.5 | 1.1795 | 3.2011 | 4.4439 | 5.2755 | 5.8871 | 6.3493 | 6.6814 | 6.9371 | 7.1251 | 7.2779 | 7.393
| 0.55 | 1.1732 | 3.3682 | 4.6613 | 5.4744 | 6.1802 | 6.6491 | 7.0042 | 7.2712 | 7.4764 | 7.6236 | 7.7463
| 0.6 | 1.1594 | 3.4877 | 4.856 | 5.7905 | 6.4364 | 6.9375 | 7.3065 | 7.5863 | 7.8009 | 7.9674 | 8.0881
| 0.65 | 1.1475 | 3.6072 | 5.0499 | 6.0095 | 6.6986 | 7.2109 | 7.5932 | 7.8828 | 8.1164 | 8.2833 | 8.4177
| 0.7 | 1.1441 | 3.6572 | 5.2274 | 6.2271 | 6.9466 | 7.4778 | 7.8777 | 8.1793 | 8.4247 | 8.597 | 8.7251
| 0.75 | 1.1349 | 3.8509 | 5.3933 | 6.4374 | 7.1761 | 7.731 | 8.1496 | 8.4612 | 8.7157 | 8.8938 | 9.0305
| 0.8 | 1.1259 | 3.9688 | 5.5786 | 6.6287 | 7.4066 | 7.9799 | 8.4076 | 8.7345 | 8.9857 | 9.18 | 9.3316
| 0.85 | 1.1258 | 4.0905 | 5.7406 | 6.8317 | 7.6234 | 8.2141 | 8.6583 | 9.0024 | 9.2584 | 9.4634 | 9.6178
| 0.9 | 1.1186 | 4.2005 | 5.8902 | 7.0147 | 7.8384 | 8.4476 | 8.909 | 9.2627 | 9.5249 | 9.7334 | 9.8899
| 0.95 | 1.111 | 4.2812 | 6.0443 | 7.1966 | 8.0385 | 8.6698 | 9.1516 | 9.5101 | 9.7848 | 9.9987 | 10.1671
| 1 | 1.1055 | 4.4105 | 6.1909 | 7.3787 | 8.2356 | 8.8923 | 9.384 | 9.7508 | 10.0399 | 10.257 | 10.4291
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0028631 | 0.0044895 | 0.0071654 | 0.0095546 | 0.011494 | 0.014053 | 0.014042 | 0.016006 | 0.018254 | 0.019194 | 0.021049
| 0.1 | 0.0078716 | 0.012915 | 0.017927 | 0.022702 | 0.025513 | 0.029139 | 0.029061 | 0.034888 | 0.035522 | 0.042832 | 0.044057
| 0.15 | 0.0043909 | 0.016493 | 0.025215 | 0.030257 | 0.039494 | 0.04037 | 0.044113 | 0.047662 | 0.053761 | 0.056079 | 0.058403
| 0.2 | 0.0026229 | 0.01958 | 0.031389 | 0.039194 | 0.050924 | 0.052439 | 0.055794 | 0.060436 | 0.065165 | 0.067949 | 0.068772
| 0.25 | -0.00068726 | 0.022997 | 0.037563 | 0.052217 | 0.062355 | 0.064024 | 0.067475 | 0.07321 | 0.07657 | 0.07982 | 0.087815
| 0.3 | -0.0042262 | 0.02514 | 0.043737 | 0.060543 | 0.073785 | 0.07561 | 0.079156 | 0.085983 | 0.087975 | 0.095 | 0.097507
| 0.35 | -0.0065501 | 0.027767 | 0.04991 | 0.068869 | 0.085215 | 0.087195 | 0.090837 | 0.098757 | 0.099379 | 0.10301 | 0.11196
| 0.4 | -0.0090186 | 0.03113 | 0.056084 | 0.077195 | 0.094265 | 0.09878 | 0.10252 | 0.11019 | 0.11078 | 0.11586 | 0.11808
| 0.45 | -0.011253 | 0.034493 | 0.062258 | 0.08552 | 0.099951 | 0.10854 | 0.11184 | 0.11702 | 0.11892 | 0.12303 | 0.12388
| 0.5 | -0.011269 | 0.037855 | 0.069043 | 0.093846 | 0.10725 | 0.11511 | 0.12027 | 0.12472 | 0.12667 | 0.131 | 0.13316
| 0.55 | -0.014043 | 0.041218 | 0.075828 | 0.10023 | 0.11309 | 0.1211 | 0.12611 | 0.13133 | 0.13452 | 0.13701 | 0.14402
| 0.6 | -0.015065 | 0.044581 | 0.082613 | 0.10496 | 0.11834 | 0.1271 | 0.13331 | 0.13695 | 0.14324 | 0.14552 | 0.14868
| 0.65 | -0.014658 | 0.047944 | 0.089399 | 0.10957 | 0.12359 | 0.13403 | 0.13917 | 0.14313 | 0.15024 | 0.15314 | 0.15654
| 0.7 | -0.015353 | 0.047989 | 0.094637 | 0.11659 | 0.12884 | 0.13914 | 0.14626 | 0.15052 | 0.15627 | 0.16065 | 0.1635
| 0.75 | -0.018331 | 0.054977 | 0.10009 | 0.11919 | 0.13409 | 0.14374 | 0.15154 | 0.15628 | 0.16122 | 0.16643 | 0.16973
| 0.8 | -0.017702 | 0.060018 | 0.10066 | 0.1227 | 0.13934 | 0.14912 | 0.15629 | 0.16131 | 0.16705 | 0.17089 | 0.17589
| 0.85 | -0.017681 | 0.062248 | 0.10331 | 0.12785 | 0.14286 | 0.15456 | 0.16223 | 0.16951 | 0.1733 | 0.17813 | 0.18281
| 0.9 | -0.018461 | 0.063757 | 0.10856 | 0.13137 | 0.14614 | 0.15909 | 0.16858 | 0.17347 | 0.17863 | 0.18333 | 0.18729
| 0.95 | -0.018625 | 0.068737 | 0.10743 | 0.1349 | 0.15065 | 0.1619 | 0.17231 | 0.1796 | 0.18684 | 0.19158 | 0.19274
| 1 | -0.019752 | 0.073718 | 0.11634 | 0.13712 | 0.15426 | 0.16787 | 0.17637 | 0.18505 | 0.19053 | 0.19465 | 0.19962
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.001435 | -0.0035249 | -0.0050363 | -0.006189 | -0.0070237 | -0.0076683 | -0.0083587 | -0.0087523 | -0.0090917 | -0.0092115 | -0.0094223
| 0.1 | -8.4615e-05 | -0.0044703 | -0.0073308 | -0.0093827 | -0.010847 | -0.011686 | -0.013042 | -0.013 | -0.014075 | -0.014454 | -0.014458
| 0.15 | 0.00053958 | -0.0054237 | -0.0095808 | -0.012316 | -0.013575 | -0.014146 | -0.01586 | -0.017606 | -0.016188 | -0.017779 | -0.018161
| 0.2 | 0.00094464 | -0.006517 | -0.012009 | -0.013821 | -0.016541 | -0.016606 | -0.018678 | -0.019965 | -0.019118 | -0.019839 | -0.021736
| 0.25 | 0.00065823 | -0.0075648 | -0.012859 | -0.015326 | -0.018235 | -0.019066 | -0.020679 | -0.022323 | -0.022863 | -0.0219 | -0.023432
| 0.3 | 0.00069724 | -0.0090191 | -0.01371 | -0.017677 | -0.018751 | -0.021237 | -0.022126 | -0.023128 | -0.023865 | -0.02418 | -0.025128
| 0.35 | 0.00034797 | -0.0090663 | -0.01456 | -0.018511 | -0.021241 | -0.022487 | -0.023791 | -0.024675 | -0.025528 | -0.026417 | -0.026824
| 0.4 | 0.00046628 | -0.010581 | -0.015411 | -0.019687 | -0.022025 | -0.02379 | -0.025456 | -0.026357 | -0.027001 | -0.028027 | -0.028522
| 0.45 | 0.00038893 | -0.011241 | -0.016261 | -0.021335 | -0.023541 | -0.025124 | -0.026898 | -0.027826 | -0.028965 | -0.029638 | -0.029837
| 0.5 | 7.1138e-05 | -0.01182 | -0.017112 | -0.022096 | -0.024531 | -0.026351 | -0.028214 | -0.0291 | -0.030502 | -0.031093 | -0.031608
| 0.55 | 3.4691e-06 | -0.012556 | -0.017962 | -0.023059 | -0.025775 | -0.027507 | -0.029712 | -0.030682 | -0.031874 | -0.032585 | -0.033293
| 0.6 | 0.00022568 | -0.013439 | -0.018813 | -0.024218 | -0.026712 | -0.028799 | -0.030669 | -0.031875 | -0.033338 | -0.033622 | -0.034774
| 0.65 | -8.7082e-05 | -0.014322 | -0.019663 | -0.024789 | -0.027856 | -0.029908 | -0.032165 | -0.033354 | -0.034529 | -0.035537 | -0.036099
| 0.7 | -0.00013008 | -0.014102 | -0.020514 | -0.025734 | -0.028584 | -0.030905 | -0.033315 | -0.034511 | -0.036011 | -0.036807 | -0.037377
| 0.75 | -0.00014363 | -0.015161 | -0.021364 | -0.026204 | -0.029519 | -0.032377 | -0.034446 | -0.036148 | -0.037009 | -0.038418 | -0.039032
| 0.8 | -0.00022051 | -0.016059 | -0.022215 | -0.02728 | -0.030564 | -0.033394 | -0.035601 | -0.037126 | -0.038275 | -0.039292 | -0.039905
| 0.85 | -0.00020386 | -0.016177 | -0.023065 | -0.027855 | -0.031482 | -0.034449 | -0.036478 | -0.038131 | -0.039748 | -0.04049 | -0.041197
| 0.9 | -0.0002619 | -0.017788 | -0.023938 | -0.028533 | -0.032809 | -0.035465 | -0.037328 | -0.039411 | -0.040782 | -0.041707 | -0.042516
| 0.95 | -0.00044485 | -0.017952 | -0.024016 | -0.02907 | -0.033299 | -0.036297 | -0.038706 | -0.040657 | -0.041916 | -0.04304 | -0.043672
| 1 | -0.00023002 | -0.018189 | -0.024788 | -0.029926 | -0.034356 | -0.037492 | -0.039635 | -0.04158 | -0.043138 | -0.043988 | -0.044827
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04)
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04)
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04)

## CLASS6_OOP (hidden)
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
| 0.05 | 2.8582 | 2.8772 | 2.8906 | 2.899 | 2.903 | 2.9033 | 2.9005 | 2.895 | 2.8874 | 2.8781 | 2.8673
| 0.1 | 2.9195 | 2.9768 | 3.0221 | 3.0512 | 3.067 | 3.0724 | 3.0698 | 3.061 | 3.0476 | 3.0306 | 3.011
| 0.15 | 2.9506 | 3.0239 | 3.0918 | 3.1346 | 3.1563 | 3.1621 | 3.1562 | 3.143 | 3.1256 | 3.104 | 3.0792
| 0.2 | 2.9537 | 3.0423 | 3.135 | 3.1902 | 3.2163 | 3.2221 | 3.2139 | 3.1961 | 3.1718 | 3.1457 | 3.1179
| 0.25 | 2.9371 | 3.053 | 3.158 | 3.2229 | 3.2522 | 3.2581 | 3.2486 | 3.2287 | 3.2053 | 3.1805 | 3.1522
| 0.3 | 2.9087 | 3.0539 | 3.1695 | 3.2425 | 3.2748 | 3.2812 | 3.271 | 3.2548 | 3.2327 | 3.2055 | 3.1748
| 0.35 | 2.8734 | 3.0485 | 3.1745 | 3.2545 | 3.2895 | 3.2967 | 3.2916 | 3.2756 | 3.2518 | 3.223 | 3.1906
| 0.4 | 2.8347 | 3.0394 | 3.1803 | 3.2619 | 3.3006 | 3.3129 | 3.3076 | 3.2907 | 3.2659 | 3.2358 | 3.2023
| 0.45 | 2.7946 | 3.0285 | 3.184 | 3.2707 | 3.3122 | 3.3251 | 3.3196 | 3.3021 | 3.2766 | 3.2458 | 3.2114
| 0.5 | 2.7546 | 3.0168 | 3.1855 | 3.2774 | 3.3209 | 3.3344 | 3.3289 | 3.3111 | 3.2852 | 3.2539 | 3.219
| 0.55 | 2.7156 | 3.005 | 3.1855 | 3.2819 | 3.3273 | 3.3416 | 3.3364 | 3.3186 | 3.2924 | 3.2608 | 3.2255
| 0.6 | 2.6779 | 2.9934 | 3.1845 | 3.285 | 3.3323 | 3.3475 | 3.3427 | 3.3249 | 3.2987 | 3.2669 | 3.2314
| 0.65 | 2.6419 | 2.9822 | 3.1827 | 3.2871 | 3.3362 | 3.3524 | 3.3481 | 3.3306 | 3.3044 | 3.2724 | 3.2366
| 0.7 | 2.6079 | 2.9715 | 3.1805 | 3.2884 | 3.3394 | 3.3567 | 3.353 | 3.3358 | 3.3096 | 3.2775 | 3.2414
| 0.75 | 2.5757 | 2.9615 | 3.178 | 3.2892 | 3.3421 | 3.3606 | 3.3576 | 3.3406 | 3.3144 | 3.2821 | 3.2458
| 0.8 | 2.5454 | 2.952 | 3.1754 | 3.2897 | 3.3446 | 3.3642 | 3.3618 | 3.345 | 3.3188 | 3.2864 | 3.2498
| 0.85 | 2.5169 | 2.9431 | 3.1726 | 3.29 | 3.3468 | 3.3676 | 3.3658 | 3.3492 | 3.323 | 3.2903 | 3.2535
| 0.9 | 2.4901 | 2.9348 | 3.1698 | 3.2902 | 3.3489 | 3.3709 | 3.3696 | 3.3531 | 3.3267 | 3.2939 | 3.2567
| 0.95 | 2.465 | 2.927 | 3.167 | 3.2903 | 3.351 | 3.374 | 3.3731 | 3.3567 | 3.3302 | 3.2971 | 3.2597
| 1 | 2.4414 | 2.9196 | 3.1642 | 3.2905 | 3.3531 | 3.377 | 3.3765 | 3.3601 | 3.3334 | 3.3 | 3.2623
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7
| 0.05 | 3.723 | 3.6703 | 3.6169 | 3.5641 | 3.5124 | 3.4611 | 3.4131 | 3.3642 | 3.317 | 3.2711 | 3.2267
| 0.1 | 3.3408 | 3.2675 | 3.1938 | 3.1207 | 3.0494 | 2.9807 | 2.9167 | 2.8542 | 2.7951 | 2.7391 | 2.6857
| 0.15 | 3.0917 | 3.0026 | 2.915 | 2.8303 | 2.7498 | 2.6736 | 2.6035 | 2.5361 | 2.4738 | 2.4156 | 2.3601
| 0.2 | 2.9141 | 2.8102 | 2.7113 | 2.6185 | 2.533 | 2.4544 | 2.3816 | 2.3123 | 2.2497 | 2.1907 | 2.136
| 0.25 | 2.7846 | 2.6609 | 2.5537 | 2.4562 | 2.3681 | 2.2868 | 2.2131 | 2.144 | 2.0806 | 2.0224 | 1.9694
| 0.3 | 2.6865 | 2.5417 | 2.4273 | 2.3268 | 2.2358 | 2.1534 | 2.0791 | 2.0102 | 1.9474 | 1.8896 | 1.837
| 0.35 | 2.61 | 2.4438 | 2.3217 | 2.2189 | 2.1272 | 2.0428 | 1.9679 | 1.8991 | 1.8373 | 1.7805 | 1.7285
| 0.4 | 2.5471 | 2.3603 | 2.2327 | 2.1278 | 2.0342 | 1.9487 | 1.8739 | 1.805 | 1.7441 | 1.6888 | 1.6378
| 0.45 | 2.4973 | 2.2884 | 2.1564 | 2.048 | 1.9523 | 1.8676 | 1.7919 | 1.7239 | 1.664 | 1.6092 | 1.559
| 0.5 | 2.4556 | 2.2241 | 2.0888 | 1.977 | 1.8806 | 1.7942 | 1.719 | 1.6531 | 1.5934 | 1.5398 | 1.4922
| 0.55 | 2.4213 | 2.1681 | 2.029 | 1.914 | 1.8157 | 1.7302 | 1.6552 | 1.5892 | 1.5308 | 1.4789 | 1.4318
| 0.6 | 2.39 | 2.1177 | 1.9745 | 1.857 | 1.7571 | 1.6715 | 1.5977 | 1.532 | 1.4756 | 1.4245 | 1.3781
| 0.65 | 2.3649 | 2.0728 | 1.9242 | 1.8044 | 1.7037 | 1.6188 | 1.5455 | 1.4818 | 1.4258 | 1.3754 | 1.3306
| 0.7 | 2.3428 | 2.031 | 1.8774 | 1.7564 | 1.6555 | 1.5707 | 1.4988 | 1.4361 | 1.38 | 1.3311 | 1.2882
| 0.75 | 2.3234 | 1.992 | 1.8355 | 1.7118 | 1.6108 | 1.526 | 1.4545 | 1.3931 | 1.3384 | 1.291 | 1.2482
| 0.8 | 2.305 | 1.9567 | 1.7962 | 1.67 | 1.5686 | 1.4858 | 1.4152 | 1.3542 | 1.3013 | 1.2548 | 1.2126
| 0.85 | 2.2896 | 1.924 | 1.7585 | 1.6317 | 1.53 | 1.4476 | 1.3783 | 1.3186 | 1.2663 | 1.2206 | 1.1797
| 0.9 | 2.2763 | 1.8934 | 1.7239 | 1.5951 | 1.4951 | 1.4129 | 1.3443 | 1.2854 | 1.2344 | 1.1892 | 1.1485
| 0.95 | 2.2641 | 1.8639 | 1.6904 | 1.5611 | 1.4612 | 1.3806 | 1.3122 | 1.2548 | 1.2044 | 1.1608 | 1.1207
| 1 | 2.2518 | 1.837 | 1.6594 | 1.5298 | 1.4298 | 1.3491 | 1.283 | 1.2264 | 1.1768 | 1.1331 | 1.0946
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.010661 | -0.0066727 | -0.0029551 | 0.00054142 | 0.0037525 | 0.0067127 | 0.0093375 | 0.011692 | 0.013843 | 0.015806 | 0.017523
| 0.1 | -0.0048872 | 0.0006843 | 0.0054592 | 0.0095274 | 0.012815 | 0.015711 | 0.018057 | 0.019957 | 0.021589 | 0.023013 | 0.024162
| 0.15 | -0.0037427 | 0.0040366 | 0.0095835 | 0.013735 | 0.016875 | 0.019493 | 0.021369 | 0.022819 | 0.024166 | 0.025288 | 0.025893
| 0.2 | -0.005264 | 0.0056799 | 0.011662 | 0.015646 | 0.018778 | 0.021133 | 0.022837 | 0.024031 | 0.025077 | 0.025856 | 0.026365
| 0.25 | -0.0068703 | 0.006204 | 0.012873 | 0.017033 | 0.019951 | 0.022275 | 0.023673 | 0.025149 | 0.025786 | 0.026506 | 0.026754
| 0.3 | -0.0088631 | 0.0069535 | 0.013323 | 0.017978 | 0.021072 | 0.023228 | 0.024833 | 0.025535 | 0.02631 | 0.026785 | 0.026742
| 0.35 | -0.01131 | 0.0072282 | 0.01427 | 0.018989 | 0.022223 | 0.024291 | 0.025468 | 0.026018 | 0.026493 | 0.026825 | 0.026597
| 0.4 | -0.013183 | 0.0075196 | 0.015122 | 0.019921 | 0.023177 | 0.024967 | 0.025971 | 0.026347 | 0.026455 | 0.026567 | 0.02635
| 0.45 | -0.014387 | 0.0076084 | 0.015973 | 0.020776 | 0.023943 | 0.025448 | 0.026109 | 0.026504 | 0.026597 | 0.026357 | 0.026115
| 0.5 | -0.015818 | 0.0079471 | 0.016767 | 0.02178 | 0.024403 | 0.025762 | 0.026284 | 0.026503 | 0.026022 | 0.025912 | 0.025604
| 0.55 | -0.017494 | 0.0084838 | 0.017319 | 0.022626 | 0.024952 | 0.026155 | 0.026278 | 0.026039 | 0.025806 | 0.025355 | 0.025095
| 0.6 | -0.018537 | 0.0086691 | 0.018111 | 0.023193 | 0.025078 | 0.025958 | 0.026141 | 0.025706 | 0.025464 | 0.025137 | 0.024419
| 0.65 | -0.019147 | 0.0089047 | 0.018927 | 0.02362 | 0.025262 | 0.026017 | 0.025806 | 0.025718 | 0.025099 | 0.024554 | 0.023878
| 0.7 | -0.020352 | 0.0093081 | 0.019685 | 0.023823 | 0.025463 | 0.025781 | 0.025497 | 0.025197 | 0.024427 | 0.024148 | 0.023485
| 0.75 | -0.021071 | 0.0097767 | 0.020285 | 0.024127 | 0.025317 | 0.025518 | 0.025237 | 0.024761 | 0.023986 | 0.02347 | 0.022958
| 0.8 | -0.021829 | 0.010388 | 0.020822 | 0.024405 | 0.025326 | 0.02534 | 0.024876 | 0.024192 | 0.023804 | 0.022976 | 0.022391
| 0.85 | -0.022402 | 0.010804 | 0.021204 | 0.024667 | 0.025268 | 0.025061 | 0.024568 | 0.023728 | 0.02319 | 0.022718 | 0.021931
| 0.9 | -0.022926 | 0.011119 | 0.021503 | 0.024537 | 0.025109 | 0.024825 | 0.024062 | 0.023435 | 0.022821 | 0.022115 | 0.02166
| 0.95 | -0.023313 | 0.011658 | 0.021992 | 0.024667 | 0.024853 | 0.024376 | 0.023703 | 0.022802 | 0.022369 | 0.021645 | 0.021081
| 1 | -0.023779 | 0.012215 | 0.021975 | 0.024591 | 0.024682 | 0.023942 | 0.023424 | 0.022514 | 0.021876 | 0.021071 | 0.020532
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0041682 | 0.0043367 | 0.004519 | 0.0047099 | 0.0048212 | 0.0049963 | 0.0051298 | 0.0052804 | 0.0054705 | 0.0055733 | 0.0056722
| 0.1 | 0.0048907 | 0.0050977 | 0.0052972 | 0.0054685 | 0.0056133 | 0.0056894 | 0.0057965 | 0.0059024 | 0.0059608 | 0.0060056 | 0.0060346
| 0.15 | 0.0049518 | 0.0052722 | 0.005499 | 0.0056294 | 0.0057371 | 0.0057747 | 0.0058417 | 0.0058784 | 0.0058826 | 0.0059001 | 0.0058747
| 0.2 | 0.0047886 | 0.0052443 | 0.0054715 | 0.0055971 | 0.005646 | 0.0056802 | 0.0057239 | 0.0057002 | 0.0057023 | 0.0056571 | 0.005623
| 0.25 | 0.0044632 | 0.0051321 | 0.0053789 | 0.0054581 | 0.0055169 | 0.0055235 | 0.0055542 | 0.005517 | 0.0054955 | 0.005434 | 0.0053859
| 0.3 | 0.0041511 | 0.0050154 | 0.0052685 | 0.0053473 | 0.0053521 | 0.0053853 | 0.0053794 | 0.0053676 | 0.0053196 | 0.0052726 | 0.0052226
| 0.35 | 0.003908 | 0.0048938 | 0.0051149 | 0.005208 | 0.0052768 | 0.0052745 | 0.0052628 | 0.0052345 | 0.005165 | 0.0051036 | 0.0050651
| 0.4 | 0.0036435 | 0.0047852 | 0.0050058 | 0.0051157 | 0.0051834 | 0.0052036 | 0.0051872 | 0.0051121 | 0.0050487 | 0.0049829 | 0.0048743
| 0.45 | 0.0033715 | 0.0047012 | 0.004896 | 0.0050645 | 0.0051118 | 0.0051056 | 0.0050665 | 0.0050111 | 0.0049141 | 0.0048225 | 0.0047425
| 0.5 | 0.0031707 | 0.0046108 | 0.0048233 | 0.0049644 | 0.0050466 | 0.0050201 | 0.0049787 | 0.0048983 | 0.00477 | 0.0047045 | 0.0046075
| 0.55 | 0.0030198 | 0.0045014 | 0.0047967 | 0.0049344 | 0.0049652 | 0.0049515 | 0.0048952 | 0.0047623 | 0.0046725 | 0.0045766 | 0.0044868
| 0.6 | 0.0028645 | 0.0044147 | 0.0047269 | 0.0048976 | 0.0049247 | 0.0048679 | 0.0047802 | 0.0046579 | 0.0045706 | 0.0044488 | 0.0043795
| 0.65 | 0.0026798 | 0.0043673 | 0.0046898 | 0.0048515 | 0.0048393 | 0.0047718 | 0.0047018 | 0.0045655 | 0.0044793 | 0.0043629 | 0.0042326
| 0.7 | 0.0025983 | 0.0043038 | 0.0046465 | 0.0048111 | 0.0047791 | 0.0046838 | 0.0046068 | 0.0044558 | 0.0043603 | 0.0042509 | 0.0041642
| 0.75 | 0.0024824 | 0.0042515 | 0.0046124 | 0.0047788 | 0.004744 | 0.0046381 | 0.0045026 | 0.0043879 | 0.004286 | 0.004162 | 0.004048
| 0.8 | 0.0023835 | 0.0041796 | 0.0046073 | 0.004702 | 0.0046419 | 0.0045488 | 0.0044347 | 0.0043009 | 0.0041652 | 0.0040726 | 0.0039276
| 0.85 | 0.0023176 | 0.0041593 | 0.0045705 | 0.0046695 | 0.0046034 | 0.0044746 | 0.0043477 | 0.0042267 | 0.0040919 | 0.0039713 | 0.003861
| 0.9 | 0.0021984 | 0.0041213 | 0.0045624 | 0.0046177 | 0.004511 | 0.0043939 | 0.0042715 | 0.0041411 | 0.004008 | 0.0038889 | 0.0037852
| 0.95 | 0.0021262 | 0.0040879 | 0.0045305 | 0.0045583 | 0.0044609 | 0.0043188 | 0.0041861 | 0.0040587 | 0.0039343 | 0.0038167 | 0.0036818
| 1 | 0.0020447 | 0.0040656 | 0.0045061 | 0.0044979 | 0.0044166 | 0.0042563 | 0.0041477 | 0.0039653 | 0.0038624 | 0.0037483 | 0.0036227
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.4903 | 1.6209 | 1.7319 | 1.8253 | 1.9071 | 1.9733 | 2.0245 | 2.0718 | 2.1158 | 2.1528 | 2.1847
| 0.1 | 1.601 | 1.9268 | 2.1814 | 2.3864 | 2.5454 | 2.6756 | 2.785 | 2.8708 | 2.9435 | 2.9922 | 3.0506
| 0.15 | 1.5883 | 2.127 | 2.5244 | 2.8419 | 3.0813 | 3.247 | 3.4052 | 3.5182 | 3.5959 | 3.6722 | 3.7526
| 0.2 | 1.5509 | 2.2899 | 2.8185 | 3.2084 | 3.5091 | 3.7994 | 3.9143 | 4.1015 | 4.1984 | 4.2278 | 4.3039
| 0.25 | 1.5031 | 2.4406 | 3.0819 | 3.5558 | 3.9126 | 4.1244 | 4.3728 | 4.554 | 4.6527 | 4.7834 | 4.8398
| 0.3 | 1.4564 | 2.6163 | 3.2951 | 3.8767 | 4.2869 | 4.5471 | 4.7356 | 5.0009 | 5.1303 | 5.2368 | 5.3211
| 0.35 | 1.4148 | 2.7048 | 3.5676 | 4.1444 | 4.6355 | 4.9679 | 5.2773 | 5.4052 | 5.5824 | 5.6716 | 5.7817
| 0.4 | 1.3846 | 2.9013 | 3.7884 | 4.4642 | 4.9639 | 5.2406 | 5.6038 | 5.8095 | 5.9767 | 6.1 | 6.1954
| 0.45 | 1.3535 | 2.9492 | 4.0013 | 4.7416 | 5.2685 | 5.665 | 5.949 | 6.1726 | 6.3462 | 6.4746 | 6.5742
| 0.5 | 1.3265 | 3.0577 | 4.2049 | 4.9955 | 5.5591 | 5.9734 | 6.2798 | 6.5164 | 6.6911 | 6.836 | 6.937
| 0.55 | 1.3036 | 3.168 | 4.4022 | 5.2392 | 5.8222 | 6.2711 | 6.5853 | 6.8424 | 7.0252 | 7.1705 | 7.2792
| 0.6 | 1.2903 | 3.2465 | 4.5766 | 5.4717 | 6.0886 | 6.55 | 6.8871 | 7.142 | 7.3432 | 7.4899 | 7.6026
| 0.65 | 1.2735 | 3.3893 | 4.8079 | 5.6921 | 6.336 | 6.8193 | 7.1632 | 7.4368 | 7.6428 | 7.7946 | 7.9131
| 0.7 | 1.2571 | 3.5069 | 4.9246 | 5.8963 | 6.5699 | 7.0744 | 7.4372 | 7.7187 | 7.932 | 8.0913 | 8.215
| 0.75 | 1.2425 | 3.6372 | 5.1168 | 6.1075 | 6.8118 | 7.317 | 7.6895 | 7.9803 | 8.2051 | 8.3755 | 8.5055
| 0.8 | 1.2378 | 3.7201 | 5.2787 | 6.3021 | 7.0275 | 7.5559 | 7.9489 | 8.2426 | 8.4789 | 8.6553 | 8.7806
| 0.85 | 1.2257 | 3.8332 | 5.4343 | 6.5011 | 7.2367 | 7.781 | 8.1872 | 8.498 | 8.7298 | 8.9187 | 9.0533
| 0.9 | 1.2149 | 3.9333 | 5.5896 | 6.6766 | 7.446 | 8.0045 | 8.4211 | 8.7408 | 8.9841 | 9.1654 | 9.3075
| 0.95 | 1.2061 | 4.0561 | 5.749 | 6.8507 | 7.6432 | 8.2222 | 8.6482 | 8.9781 | 9.2276 | 9.4215 | 9.5575
| 1 | 1.2059 | 4.1427 | 5.8845 | 7.0314 | 7.8339 | 8.4238 | 8.8713 | 9.213 | 9.4668 | 9.6605 | 9.8052
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.023371 | -0.019987 | -0.015913 | -0.013444 | -0.010041 | -0.0067524 | -0.0046334 | -0.0020859 | 0.00050047 | 0.003071 | 0.0050557
| 0.1 | -0.021021 | -0.014847 | -0.0091611 | -0.003508 | 0.0010274 | 0.0081778 | 0.0088793 | 0.011324 | 0.012526 | 0.016956 | 0.021502
| 0.15 | -0.021084 | -0.010282 | -0.0016696 | 0.0065332 | 0.010876 | 0.018656 | 0.021474 | 0.024733 | 0.024551 | 0.025329 | 0.033935
| 0.2 | -0.022132 | -0.0060352 | 0.0058219 | 0.014939 | 0.022991 | 0.029943 | 0.03407 | 0.037438 | 0.036576 | 0.042537 | 0.046368
| 0.25 | -0.027205 | -0.0060377 | 0.011325 | 0.023044 | 0.032502 | 0.036726 | 0.046665 | 0.050142 | 0.049187 | 0.053788 | 0.061933
| 0.3 | -0.031357 | -0.0017135 | 0.018354 | 0.029028 | 0.042736 | 0.051761 | 0.057741 | 0.062847 | 0.064771 | 0.070831 | 0.081578
| 0.35 | -0.033005 | 0.00031274 | 0.023285 | 0.038453 | 0.05297 | 0.061272 | 0.068437 | 0.074981 | 0.080355 | 0.08417 | 0.092117
| 0.4 | -0.035808 | -0.0051778 | 0.028216 | 0.047879 | 0.062707 | 0.073911 | 0.079133 | 0.087244 | 0.089337 | 0.09751 | 0.10105
| 0.45 | -0.039937 | 0.0009599 | 0.034179 | 0.057304 | 0.071162 | 0.08634 | 0.092485 | 0.098308 | 0.10148 | 0.10851 | 0.11031
| 0.5 | -0.042294 | 0.0050034 | 0.040475 | 0.068948 | 0.079391 | 0.092428 | 0.10198 | 0.1087 | 0.11488 | 0.11731 | 0.11982
| 0.55 | -0.042467 | 0.0046088 | 0.046772 | 0.074296 | 0.090437 | 0.10386 | 0.11133 | 0.11658 | 0.12368 | 0.12474 | 0.12933
| 0.6 | -0.043606 | 0.0079407 | 0.053069 | 0.079094 | 0.098212 | 0.11103 | 0.11972 | 0.12639 | 0.13136 | 0.13456 | 0.13541
| 0.65 | -0.047123 | 0.0086024 | 0.059365 | 0.087773 | 0.1068 | 0.11903 | 0.12733 | 0.13517 | 0.13924 | 0.14053 | 0.14326
| 0.7 | -0.046108 | 0.013738 | 0.065662 | 0.095989 | 0.11575 | 0.12782 | 0.13494 | 0.13936 | 0.14529 | 0.15089 | 0.15071
| 0.75 | -0.046866 | 0.014868 | 0.071959 | 0.10227 | 0.12253 | 0.13318 | 0.14144 | 0.1455 | 0.15161 | 0.15476 | 0.15683
| 0.8 | -0.048439 | 0.018825 | 0.076606 | 0.11174 | 0.12858 | 0.13891 | 0.14835 | 0.15437 | 0.15799 | 0.16245 | 0.16487
| 0.85 | -0.048778 | 0.016005 | 0.085915 | 0.11769 | 0.13714 | 0.14582 | 0.15394 | 0.15893 | 0.16346 | 0.16675 | 0.16828
| 0.9 | -0.049446 | 0.023868 | 0.090116 | 0.12134 | 0.1435 | 0.152 | 0.16002 | 0.16694 | 0.16927 | 0.17203 | 0.1755
| 0.95 | -0.049744 | 0.031731 | 0.092986 | 0.12474 | 0.14523 | 0.1564 | 0.16412 | 0.16877 | 0.17655 | 0.17759 | 0.17996
| 1 | -0.050552 | 0.03424 | 0.098726 | 0.13044 | 0.1498 | 0.16063 | 0.17044 | 0.17529 | 0.18087 | 0.1833 | 0.18402
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0018549 | -0.0030959 | -0.0041023 | -0.0049054 | -0.0052577 | -0.0057591 | -0.0061612 | -0.0064896 | -0.0069228 | -0.0071505 | -0.0073457
| 0.1 | -0.00064836 | -0.0036325 | -0.0056861 | -0.0072769 | -0.008587 | -0.0092827 | -0.0098762 | -0.010462 | -0.010684 | -0.011197 | -0.01109
| 0.15 | 0.00038427 | -0.0041459 | -0.0069051 | -0.0086441 | -0.010348 | -0.011446 | -0.01228 | -0.012477 | -0.013889 | -0.013661 | -0.013483
| 0.2 | 0.00083302 | -0.0047245 | -0.0083531 | -0.009259 | -0.012108 | -0.013279 | -0.014229 | -0.014493 | -0.015627 | -0.016125 | -0.015875
| 0.25 | 0.0013773 | -0.0053032 | -0.0087943 | -0.010936 | -0.014213 | -0.014795 | -0.016177 | -0.016508 | -0.017365 | -0.017366 | -0.018268
| 0.3 | 0.0014568 | -0.0060074 | -0.01041 | -0.012614 | -0.016766 | -0.017731 | -0.017916 | -0.018524 | -0.018872 | -0.019583 | -0.019877
| 0.35 | 0.0014275 | -0.0067116 | -0.012139 | -0.014699 | -0.017808 | -0.019283 | -0.019607 | -0.02054 | -0.020736 | -0.021349 | -0.021646
| 0.4 | 0.0013575 | -0.007085 | -0.012758 | -0.01615 | -0.018849 | -0.020103 | -0.020814 | -0.021757 | -0.022126 | -0.023115 | -0.02307
| 0.45 | 0.0015749 | -0.0074584 | -0.01378 | -0.017602 | -0.01989 | -0.020923 | -0.022024 | -0.022933 | -0.023406 | -0.02431 | -0.02448
| 0.5 | 0.001489 | -0.0083044 | -0.013601 | -0.01858 | -0.020673 | -0.022367 | -0.023119 | -0.024374 | -0.024952 | -0.025118 | -0.025443
| 0.55 | 0.0012229 | -0.0091504 | -0.015434 | -0.019251 | -0.021627 | -0.023019 | -0.024345 | -0.025075 | -0.026026 | -0.026316 | -0.026993
| 0.6 | 0.0012188 | -0.0099964 | -0.015804 | -0.019921 | -0.022341 | -0.023965 | -0.025177 | -0.026155 | -0.02727 | -0.02771 | -0.027784
| 0.65 | 0.0013029 | -0.011399 | -0.016174 | -0.02047 | -0.023222 | -0.024897 | -0.02605 | -0.02697 | -0.027894 | -0.028443 | -0.02911
| 0.7 | 0.0010954 | -0.011326 | -0.017694 | -0.021 | -0.024145 | -0.025841 | -0.02636 | -0.028025 | -0.028926 | -0.029472 | -0.029909
| 0.75 | 0.0011325 | -0.011873 | -0.0182 | -0.022092 | -0.024733 | -0.026375 | -0.02794 | -0.028779 | -0.029687 | -0.030413 | -0.031065
| 0.8 | 0.00099249 | -0.01242 | -0.018909 | -0.022787 | -0.025435 | -0.027234 | -0.02872 | -0.029689 | -0.030782 | -0.03144 | -0.032057
| 0.85 | 0.00073147 | -0.012704 | -0.019272 | -0.023128 | -0.025989 | -0.028062 | -0.029567 | -0.03079 | -0.031574 | -0.032538 | -0.033055
| 0.9 | 0.00096609 | -0.013019 | -0.019773 | -0.023834 | -0.026667 | -0.028865 | -0.030447 | -0.031626 | -0.032527 | -0.033367 | -0.033965
| 0.95 | 0.00094492 | -0.013754 | -0.020376 | -0.024165 | -0.027294 | -0.029626 | -0.031275 | -0.032478 | -0.033428 | -0.034286 | -0.035108
| 1 | 0.00084441 | -0.01449 | -0.020633 | -0.024785 | -0.027779 | -0.030271 | -0.031689 | -0.033524 | -0.034459 | -0.03472 | -0.035658
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76)
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76)
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76)

## CLASS7_OOP (hidden)
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
| 0.05 | 2.8602 | 2.8942 | 2.9195 | 2.9381 | 2.9506 | 2.9576 | 2.96 | 2.9584 | 2.9536 | 2.9421 | 2.9328
| 0.1 | 2.9145 | 2.9798 | 3.0347 | 3.0735 | 3.0958 | 3.1052 | 3.1051 | 3.0977 | 3.0851 | 3.067 | 3.0475
| 0.15 | 2.9068 | 3.0128 | 3.0928 | 3.144 | 3.1718 | 3.1826 | 3.1811 | 3.1708 | 3.1542 | 3.1321 | 3.1079
| 0.2 | 2.8786 | 3.0169 | 3.1238 | 3.1879 | 3.2208 | 3.2322 | 3.2291 | 3.2159 | 3.1959 | 3.1705 | 3.1425
| 0.25 | 2.8361 | 3.0083 | 3.1392 | 3.2138 | 3.2506 | 3.2628 | 3.2588 | 3.2439 | 3.2218 | 3.1944 | 3.1641
| 0.3 | 2.7861 | 2.9945 | 3.1463 | 3.2297 | 3.2699 | 3.283 | 3.2786 | 3.2629 | 3.2397 | 3.2111 | 3.1795
| 0.35 | 2.7339 | 2.9791 | 3.1488 | 3.2396 | 3.2828 | 3.297 | 3.2929 | 3.277 | 3.2532 | 3.224 | 3.1916
| 0.4 | 2.6826 | 2.9637 | 3.1488 | 3.2458 | 3.2919 | 3.3076 | 3.3042 | 3.2884 | 3.2645 | 3.2349 | 3.2019
| 0.45 | 2.6335 | 2.949 | 3.1472 | 3.2497 | 3.2988 | 3.3161 | 3.3136 | 3.2982 | 3.2742 | 3.2443 | 3.2108
| 0.5 | 2.5874 | 2.9354 | 3.1447 | 3.2523 | 3.3044 | 3.3236 | 3.322 | 3.3069 | 3.2828 | 3.2525 | 3.2185
| 0.55 | 2.5445 | 2.923 | 3.1417 | 3.2541 | 3.3093 | 3.3303 | 3.3295 | 3.3146 | 3.2903 | 3.2597 | 3.2252
| 0.6 | 2.5049 | 2.9116 | 3.1385 | 3.2556 | 3.3139 | 3.3365 | 3.3364 | 3.3215 | 3.297 | 3.266 | 3.231
| 0.65 | 2.4683 | 2.9011 | 3.1352 | 3.257 | 3.3182 | 3.3422 | 3.3425 | 3.3276 | 3.3028 | 3.2714 | 3.236
| 0.7 | 2.4346 | 2.8916 | 3.1321 | 3.2585 | 3.3223 | 3.3474 | 3.3481 | 3.3331 | 3.3079 | 3.2762 | 3.2403
| 0.75 | 2.4037 | 2.8828 | 3.1293 | 3.26 | 3.3262 | 3.3522 | 3.353 | 3.3378 | 3.3124 | 3.2803 | 3.2441
| 0.8 | 2.3752 | 2.8748 | 3.1267 | 3.2617 | 3.3299 | 3.3566 | 3.3575 | 3.3421 | 3.3164 | 3.284 | 3.2474
| 0.85 | 2.3489 | 2.8673 | 3.1244 | 3.2634 | 3.3333 | 3.3605 | 3.3614 | 3.3459 | 3.3199 | 3.2872 | 3.2504
| 0.9 | 2.3246 | 2.8604 | 3.1224 | 3.2651 | 3.3365 | 3.3641 | 3.3649 | 3.3492 | 3.323 | 3.2902 | 3.2531
| 0.95 | 2.3022 | 2.854 | 3.1208 | 3.2669 | 3.3394 | 3.3673 | 3.3681 | 3.3522 | 3.3259 | 3.2928 | 3.2556
| 1 | 2.2814 | 2.8481 | 3.1194 | 3.2686 | 3.3421 | 3.3702 | 3.371 | 3.355 | 3.3285 | 3.2953 | 3.2579
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
| 0.05 | 4.3213 | 4.2354 | 4.1609 | 4.0877 | 4.0157 | 3.946 | 3.8786 | 3.816 | 3.7534 | 3.7105 | 3.653
| 0.1 | 3.8805 | 3.7655 | 3.6607 | 3.5624 | 3.468 | 3.3803 | 3.2984 | 3.2209 | 3.1474 | 3.0868 | 3.0216
| 0.15 | 3.601 | 3.4562 | 3.334 | 3.2221 | 3.1194 | 3.0244 | 2.9373 | 2.8554 | 2.7791 | 2.7137 | 2.6474
| 0.2 | 3.4116 | 3.2348 | 3.0987 | 2.9798 | 2.8706 | 2.7717 | 2.6824 | 2.5984 | 2.5223 | 2.4556 | 2.3903
| 0.25 | 3.2746 | 3.0656 | 2.9182 | 2.793 | 2.681 | 2.5793 | 2.4874 | 2.4031 | 2.3273 | 2.2611 | 2.1964
| 0.3 | 3.175 | 2.9283 | 2.7732 | 2.6431 | 2.5269 | 2.4229 | 2.3309 | 2.2472 | 2.1715 | 2.1061 | 2.0449
| 0.35 | 3.0983 | 2.8163 | 2.653 | 2.5172 | 2.3974 | 2.2923 | 2.2006 | 2.117 | 2.0434 | 1.9798 | 1.9194
| 0.4 | 3.0378 | 2.7211 | 2.5488 | 2.4087 | 2.2864 | 2.1802 | 2.0892 | 2.0077 | 1.9356 | 1.8728 | 1.8154
| 0.45 | 2.9867 | 2.6386 | 2.459 | 2.3134 | 2.189 | 2.0836 | 1.993 | 1.9127 | 1.8423 | 1.7824 | 1.7251
| 0.5 | 2.9467 | 2.5662 | 2.3783 | 2.2275 | 2.1031 | 1.9977 | 1.9086 | 1.8305 | 1.7619 | 1.7025 | 1.6479
| 0.55 | 2.913 | 2.5008 | 2.3055 | 2.1513 | 2.0262 | 1.9221 | 1.8347 | 1.758 | 1.6909 | 1.6335 | 1.5799
| 0.6 | 2.8848 | 2.4428 | 2.2393 | 2.082 | 1.9572 | 1.8542 | 1.7681 | 1.6937 | 1.628 | 1.5713 | 1.5202
| 0.65 | 2.8582 | 2.3896 | 2.1789 | 2.0196 | 1.8952 | 1.7933 | 1.7089 | 1.6351 | 1.5718 | 1.516 | 1.4663
| 0.7 | 2.8372 | 2.3411 | 2.1221 | 1.9618 | 1.8379 | 1.7379 | 1.6538 | 1.5822 | 1.5211 | 1.4671 | 1.4185
| 0.75 | 2.8189 | 2.2953 | 2.0697 | 1.909 | 1.7857 | 1.6869 | 1.6056 | 1.5347 | 1.4745 | 1.4221 | 1.3747
| 0.8 | 2.8026 | 2.2526 | 2.0217 | 1.8594 | 1.7373 | 1.6405 | 1.5596 | 1.4918 | 1.4323 | 1.3806 | 1.3349
| 0.85 | 2.7862 | 2.2133 | 1.9769 | 1.8148 | 1.6926 | 1.5973 | 1.5188 | 1.4514 | 1.3937 | 1.3436 | 1.2978
| 0.9 | 2.7733 | 2.1754 | 1.9352 | 1.7721 | 1.6519 | 1.5573 | 1.4801 | 1.4148 | 1.3572 | 1.3084 | 1.2641
| 0.95 | 2.7621 | 2.1405 | 1.8947 | 1.7324 | 1.6131 | 1.521 | 1.4448 | 1.3805 | 1.3244 | 1.2764 | 1.233
| 1 | 2.7517 | 2.107 | 1.8572 | 1.695 | 1.5784 | 1.4867 | 1.4114 | 1.3484 | 1.2941 | 1.246 | 1.2038
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0076713 | -0.0020717 | 0.002518 | 0.0067827 | 0.010577 | 0.013827 | 0.015985 | 0.018377 | 0.021122 | 0.02276 | 0.024352
| 0.1 | -0.00038332 | 0.0081292 | 0.013888 | 0.018299 | 0.021545 | 0.024107 | 0.025864 | 0.028029 | 0.029419 | 0.030613 | 0.03152
| 0.15 | -0.00036067 | 0.011801 | 0.017887 | 0.021697 | 0.024693 | 0.02663 | 0.028255 | 0.029853 | 0.030904 | 0.031702 | 0.032413
| 0.2 | -0.0031334 | 0.013075 | 0.019197 | 0.022689 | 0.025495 | 0.0277 | 0.029463 | 0.0307 | 0.031615 | 0.03215 | 0.032686
| 0.25 | -0.0053982 | 0.013428 | 0.019415 | 0.02339 | 0.026416 | 0.02879 | 0.030452 | 0.031555 | 0.032214 | 0.032528 | 0.032684
| 0.3 | -0.0081922 | 0.013774 | 0.019322 | 0.024256 | 0.027807 | 0.029985 | 0.031205 | 0.031947 | 0.032303 | 0.032293 | 0.03235
| 0.35 | -0.010648 | 0.013674 | 0.020031 | 0.025432 | 0.02885 | 0.030695 | 0.031669 | 0.0321 | 0.032141 | 0.032171 | 0.031902
| 0.4 | -0.013184 | 0.01367 | 0.021092 | 0.026485 | 0.02961 | 0.031255 | 0.031765 | 0.032013 | 0.031811 | 0.031509 | 0.031168
| 0.45 | -0.015106 | 0.013623 | 0.022002 | 0.027293 | 0.030232 | 0.031524 | 0.031691 | 0.031703 | 0.031228 | 0.030756 | 0.030455
| 0.5 | -0.016117 | 0.013522 | 0.022918 | 0.028044 | 0.030493 | 0.031418 | 0.031326 | 0.031204 | 0.03089 | 0.029987 | 0.029567
| 0.55 | -0.017554 | 0.01358 | 0.023808 | 0.02878 | 0.030715 | 0.031006 | 0.031058 | 0.030625 | 0.030053 | 0.029394 | 0.028894
| 0.6 | -0.019071 | 0.013906 | 0.024323 | 0.028968 | 0.030788 | 0.030957 | 0.030708 | 0.030065 | 0.029436 | 0.028663 | 0.028134
| 0.65 | -0.02014 | 0.014445 | 0.025121 | 0.029443 | 0.030585 | 0.030602 | 0.030215 | 0.029627 | 0.028762 | 0.028039 | 0.027384
| 0.7 | -0.02107 | 0.014756 | 0.025715 | 0.029543 | 0.030313 | 0.030277 | 0.029711 | 0.028941 | 0.02821 | 0.027441 | 0.0267
| 0.75 | -0.021391 | 0.015163 | 0.026154 | 0.029641 | 0.030242 | 0.029948 | 0.029109 | 0.028252 | 0.027319 | 0.026659 | 0.026027
| 0.8 | -0.022358 | 0.015692 | 0.026553 | 0.029369 | 0.029805 | 0.029364 | 0.028705 | 0.027935 | 0.026877 | 0.025924 | 0.02524
| 0.85 | -0.023086 | 0.016279 | 0.026923 | 0.029335 | 0.02972 | 0.029 | 0.028116 | 0.027206 | 0.026233 | 0.025592 | 0.024865
| 0.9 | -0.0236 | 0.016936 | 0.027003 | 0.029418 | 0.029291 | 0.028482 | 0.027498 | 0.026527 | 0.02578 | 0.024891 | 0.024158
| 0.95 | -0.023703 | 0.017286 | 0.027184 | 0.029195 | 0.02895 | 0.028191 | 0.027154 | 0.02618 | 0.025149 | 0.024447 | 0.023714
| 1 | -0.024519 | 0.017935 | 0.027476 | 0.028983 | 0.028584 | 0.027519 | 0.026706 | 0.02575 | 0.024743 | 0.024099 | 0.023288
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0030957 | 0.003461 | 0.0037728 | 0.004063 | 0.0043107 | 0.0045503 | 0.0048197 | 0.004981 | 0.0051296 | 0.0052367 | 0.0053106
| 0.1 | 0.0036702 | 0.004374 | 0.0047908 | 0.0050666 | 0.0052851 | 0.0054232 | 0.005594 | 0.0057007 | 0.0057387 | 0.0057823 | 0.005861
| 0.15 | 0.0036208 | 0.0046526 | 0.005098 | 0.0053368 | 0.0054521 | 0.0055659 | 0.0056682 | 0.0056867 | 0.0057285 | 0.0057466 | 0.0057512
| 0.2 | 0.0032701 | 0.0047424 | 0.0051067 | 0.0053131 | 0.0054229 | 0.005511 | 0.0056106 | 0.0056278 | 0.0056288 | 0.0056187 | 0.0056121
| 0.25 | 0.0028241 | 0.0047213 | 0.0051053 | 0.0052374 | 0.0053901 | 0.0054819 | 0.0055617 | 0.0055303 | 0.0055309 | 0.0054946 | 0.0054421
| 0.3 | 0.0024934 | 0.0045991 | 0.0049927 | 0.0052146 | 0.0053796 | 0.005455 | 0.0054963 | 0.005441 | 0.0054181 | 0.0053433 | 0.0052846
| 0.35 | 0.0022403 | 0.0045329 | 0.004926 | 0.0052293 | 0.0053772 | 0.0054045 | 0.0054074 | 0.0053572 | 0.0052736 | 0.0051877 | 0.0051087
| 0.4 | 0.0019897 | 0.0044466 | 0.0048631 | 0.0052117 | 0.0053143 | 0.0053087 | 0.0052742 | 0.0052181 | 0.0051271 | 0.0050389 | 0.0049598
| 0.45 | 0.0017877 | 0.0043882 | 0.0048494 | 0.0051739 | 0.0052682 | 0.0052339 | 0.0051544 | 0.0050915 | 0.0049758 | 0.0048728 | 0.0047843
| 0.5 | 0.0015461 | 0.0043253 | 0.0048496 | 0.0051671 | 0.0052061 | 0.0051497 | 0.0050657 | 0.0049446 | 0.0048148 | 0.0047379 | 0.0046033
| 0.55 | 0.0014623 | 0.0042652 | 0.0048731 | 0.0050952 | 0.0051404 | 0.0050475 | 0.0049474 | 0.00484 | 0.0047119 | 0.0045866 | 0.0044893
| 0.6 | 0.0013165 | 0.0041984 | 0.0048623 | 0.0050652 | 0.0050709 | 0.0049525 | 0.0048466 | 0.0047191 | 0.0045723 | 0.0044735 | 0.0043576
| 0.65 | 0.0012088 | 0.004171 | 0.004855 | 0.0050058 | 0.0049871 | 0.0048692 | 0.0047362 | 0.0045976 | 0.0044645 | 0.0043308 | 0.004215
| 0.7 | 0.0011063 | 0.0041662 | 0.0048275 | 0.0049462 | 0.0049083 | 0.0047688 | 0.0046187 | 0.0044629 | 0.0043318 | 0.0042076 | 0.0040926
| 0.75 | 0.001028 | 0.0041446 | 0.0048279 | 0.0049188 | 0.004817 | 0.0046787 | 0.004532 | 0.004383 | 0.0042591 | 0.0041173 | 0.0040199
| 0.8 | 0.0009475 | 0.0041389 | 0.0047779 | 0.0048526 | 0.004744 | 0.0045992 | 0.0044197 | 0.0042716 | 0.0041342 | 0.0040192 | 0.0039005
| 0.85 | 0.00087977 | 0.0041411 | 0.004767 | 0.0047973 | 0.0046604 | 0.0045139 | 0.0043258 | 0.0041789 | 0.004029 | 0.0039277 | 0.0038241
| 0.9 | 0.00087583 | 0.0041331 | 0.0047414 | 0.0047317 | 0.0045739 | 0.004413 | 0.004233 | 0.0040868 | 0.0039491 | 0.0038461 | 0.0037318
| 0.95 | 0.00081736 | 0.0041405 | 0.0046855 | 0.0046588 | 0.0044953 | 0.0043199 | 0.0041493 | 0.0040018 | 0.0038802 | 0.0037499 | 0.0036567
| 1 | 0.00070777 | 0.0041416 | 0.0046549 | 0.0046088 | 0.0044192 | 0.0042388 | 0.0040962 | 0.0039291 | 0.0037928 | 0.0036919 | 0.0035736
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.4044 | 1.5599 | 1.6875 | 1.7931 | 1.882 | 1.9572 | 2.0199 | 2.0661 | 2.1127 | 2.1363 | 2.1686
| 0.1 | 1.4522 | 1.8093 | 2.0854 | 2.2996 | 2.4703 | 2.6085 | 2.7135 | 2.8047 | 2.8896 | 2.9369 | 2.987
| 0.15 | 1.4211 | 1.9837 | 2.3978 | 2.7126 | 2.9722 | 3.1645 | 3.2974 | 3.4346 | 3.522 | 3.587 | 3.6343
| 0.2 | 1.3767 | 2.1357 | 2.6885 | 3.0776 | 3.3829 | 3.6337 | 3.7939 | 4.0023 | 4.0711 | 4.1574 | 4.2215
| 0.25 | 1.3425 | 2.276 | 2.9304 | 3.4358 | 3.8111 | 4.0926 | 4.2431 | 4.4409 | 4.5824 | 4.651 | 4.6613
| 0.3 | 1.3076 | 2.4173 | 3.1867 | 3.719 | 4.123 | 4.4643 | 4.6946 | 4.8139 | 4.9676 | 5.0458 | 5.1087
| 0.35 | 1.2781 | 2.5576 | 3.4067 | 4.0355 | 4.3741 | 4.7572 | 4.9932 | 5.1914 | 5.3577 | 5.467 | 5.5553
| 0.4 | 1.2534 | 2.6694 | 3.6615 | 4.2604 | 4.707 | 5.091 | 5.3458 | 5.5649 | 5.729 | 5.8411 | 5.9292
| 0.45 | 1.2397 | 2.8062 | 3.8711 | 4.5053 | 4.9982 | 5.3961 | 5.6805 | 5.8928 | 6.0766 | 6.1745 | 6.2962
| 0.5 | 1.2229 | 2.9375 | 4.0137 | 4.7501 | 5.2758 | 5.6829 | 5.9772 | 6.2126 | 6.3933 | 6.5191 | 6.6343
| 0.55 | 1.2071 | 3.0336 | 4.1723 | 4.9704 | 5.5434 | 5.9638 | 6.2711 | 6.5212 | 6.7012 | 6.8253 | 6.9447
| 0.6 | 1.1934 | 3.147 | 4.3472 | 5.1974 | 5.7809 | 6.2212 | 6.5429 | 6.8037 | 6.9898 | 7.1423 | 7.2489
| 0.65 | 1.1883 | 3.2559 | 4.5265 | 5.393 | 5.9976 | 6.4639 | 6.807 | 7.0743 | 7.2791 | 7.4169 | 7.5412
| 0.7 | 1.1784 | 3.3648 | 4.7078 | 5.5815 | 6.221 | 6.6847 | 7.0544 | 7.3317 | 7.5517 | 7.7035 | 7.8334
| 0.75 | 1.1686 | 3.4699 | 4.86 | 5.7719 | 6.343 | 6.9328 | 7.3029 | 7.5894 | 7.8072 | 7.9709 | 8.1025
| 0.8 | 1.161 | 3.5792 | 5.0091 | 5.955 | 6.6384 | 7.1496 | 7.5301 | 7.832 | 8.0638 | 8.2278 | 8.3602
| 0.85 | 1.1594 | 3.6775 | 5.1533 | 6.1309 | 6.8322 | 7.3598 | 7.7626 | 8.0621 | 8.311 | 8.4844 | 8.6135
| 0.9 | 1.1517 | 3.7757 | 5.2818 | 6.2896 | 7.0303 | 7.5659 | 7.9786 | 8.2959 | 8.5436 | 8.7276 | 8.8636
| 0.95 | 1.1438 | 3.8694 | 5.4234 | 6.4642 | 7.2084 | 7.7743 | 8.1942 | 8.5232 | 8.7682 | 8.965 | 9.1065
| 1 | 1.1382 | 3.8653 | 5.5639 | 6.6249 | 7.3961 | 7.9701 | 8.401 | 8.7396 | 8.9994 | 9.1939 | 9.3411
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0012522 | -0.00012407 | 0.0012379 | 0.0029483 | 0.0047839 | 0.0065812 | 0.010021 | 0.011678 | 0.011523 | 0.012747 | 0.014075
| 0.1 | 0.0046071 | 0.0071665 | 0.010329 | 0.01364 | 0.01622 | 0.019458 | 0.023411 | 0.024681 | 0.026876 | 0.030948 | 0.030647
| 0.15 | 0.0051005 | 0.011617 | 0.016392 | 0.02297 | 0.025292 | 0.03169 | 0.034776 | 0.034789 | 0.039553 | 0.041746 | 0.042323
| 0.2 | 0.0045028 | 0.013931 | 0.023033 | 0.031684 | 0.033421 | 0.041108 | 0.04402 | 0.045747 | 0.051247 | 0.053267 | 0.05306
| 0.25 | -4.2346e-05 | 0.017103 | 0.029356 | 0.037545 | 0.041551 | 0.050526 | 0.055065 | 0.056704 | 0.062941 | 0.064787 | 0.065673
| 0.3 | -0.0022571 | 0.016269 | 0.03373 | 0.043405 | 0.04968 | 0.059944 | 0.066386 | 0.067662 | 0.074635 | 0.076307 | 0.0775
| 0.35 | -0.0044227 | 0.017206 | 0.038105 | 0.049266 | 0.05781 | 0.069362 | 0.077706 | 0.078619 | 0.086329 | 0.087828 | 0.089326
| 0.4 | -0.0046357 | 0.023513 | 0.04248 | 0.055126 | 0.065939 | 0.07878 | 0.088246 | 0.089577 | 0.098024 | 0.099348 | 0.10115
| 0.45 | -0.006776 | 0.024454 | 0.046855 | 0.060987 | 0.074069 | 0.088198 | 0.098785 | 0.10053 | 0.10859 | 0.11087 | 0.11298
| 0.5 | -0.0093046 | 0.025395 | 0.051229 | 0.066848 | 0.082198 | 0.099413 | 0.10703 | 0.11149 | 0.11291 | 0.11429 | 0.11772
| 0.55 | -0.011233 | 0.026336 | 0.055604 | 0.072708 | 0.090327 | 0.10723 | 0.11473 | 0.12203 | 0.12337 | 0.12409 | 0.12649
| 0.6 | -0.010424 | 0.027278 | 0.059979 | 0.080453 | 0.10048 | 0.11368 | 0.12374 | 0.12787 | 0.12965 | 0.13388 | 0.13644
| 0.65 | -0.01072 | 0.028219 | 0.063346 | 0.089848 | 0.1093 | 0.12045 | 0.12762 | 0.13406 | 0.13696 | 0.13848 | 0.14169
| 0.7 | -0.011788 | 0.02916 | 0.069244 | 0.095835 | 0.11738 | 0.12524 | 0.1339 | 0.13922 | 0.14376 | 0.14469 | 0.148
| 0.75 | -0.0143 | 0.02639 | 0.072009 | 0.10227 | 0.12275 | 0.13589 | 0.14032 | 0.14558 | 0.1486 | 0.15049 | 0.15165
| 0.8 | -0.013344 | 0.03025 | 0.077895 | 0.1087 | 0.12903 | 0.13812 | 0.14656 | 0.14988 | 0.15404 | 0.15629 | 0.15698
| 0.85 | -0.014577 | 0.028235 | 0.083139 | 0.11391 | 0.13351 | 0.14281 | 0.15102 | 0.15604 | 0.15947 | 0.16342 | 0.16359
| 0.9 | -0.014382 | 0.029444 | 0.090483 | 0.11939 | 0.13475 | 0.1472 | 0.15548 | 0.16016 | 0.16339 | 0.16775 | 0.17033
| 0.95 | -0.01706 | 0.030654 | 0.094966 | 0.1241 | 0.13921 | 0.15218 | 0.16124 | 0.16744 | 0.16754 | 0.17234 | 0.17572
| 1 | -0.015472 | 0.03406 | 0.10624 | 0.12962 | 0.14434 | 0.15587 | 0.16564 | 0.17116 | 0.17276 | 0.17795 | 0.17907
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0007853 | -0.0021679 | -0.0032469 | -0.0041511 | -0.0048194 | -0.0053784 | -0.0059595 | -0.0063258 | -0.0066344 | -0.0067292 | -0.0066908
| 0.1 | 0.00020754 | -0.0027432 | -0.004737 | -0.0061672 | -0.0072531 | -0.0080794 | -0.0089495 | -0.0093583 | -0.0095464 | -0.010058 | -0.010218
| 0.15 | 0.00068884 | -0.0032223 | -0.0058908 | -0.0079322 | -0.0095895 | -0.0099835 | -0.010955 | -0.011307 | -0.012364 | -0.013229 | -0.012479
| 0.2 | 0.0011796 | -0.0040299 | -0.0072425 | -0.01047 | -0.011443 | -0.012145 | -0.012534 | -0.012797 | -0.013841 | -0.015272 | -0.014741
| 0.25 | 0.0014929 | -0.0046847 | -0.0088264 | -0.010956 | -0.012466 | -0.013111 | -0.014009 | -0.014288 | -0.015319 | -0.01629 | -0.017002
| 0.3 | 0.0016873 | -0.0052103 | -0.0095245 | -0.011771 | -0.013488 | -0.014077 | -0.015515 | -0.015778 | -0.016796 | -0.017308 | -0.01796
| 0.35 | 0.0014274 | -0.0059047 | -0.010311 | -0.012367 | -0.01393 | -0.015044 | -0.016869 | -0.017269 | -0.017785 | -0.018325 | -0.018918
| 0.4 | 0.0015382 | -0.0065079 | -0.011097 | -0.012963 | -0.014371 | -0.016091 | -0.01767 | -0.018236 | -0.018748 | -0.019074 | -0.019159
| 0.45 | 0.0015196 | -0.007437 | -0.01184 | -0.013559 | -0.015337 | -0.016966 | -0.018471 | -0.019217 | -0.019592 | -0.019964 | -0.020327
| 0.5 | 0.0017675 | -0.008075 | -0.012443 | -0.014155 | -0.016302 | -0.017771 | -0.019221 | -0.020134 | -0.02043 | -0.021026 | -0.021078
| 0.55 | 0.0015853 | -0.0080839 | -0.013052 | -0.014751 | -0.017595 | -0.018484 | -0.019608 | -0.020707 | -0.021509 | -0.021814 | -0.022042
| 0.6 | 0.0015852 | -0.0084095 | -0.013661 | -0.01632 | -0.017818 | -0.019196 | -0.020342 | -0.021526 | -0.022075 | -0.022725 | -0.023126
| 0.65 | 0.0016244 | -0.009106 | -0.014118 | -0.016513 | -0.018642 | -0.019817 | -0.02128 | -0.022164 | -0.023305 | -0.023333 | -0.024262
| 0.7 | 0.0016206 | -0.0098024 | -0.014501 | -0.016602 | -0.019075 | -0.020559 | -0.021856 | -0.023009 | -0.023901 | -0.024323 | -0.025162
| 0.75 | 0.0016187 | -0.010224 | -0.014774 | -0.017915 | -0.019703 | -0.021154 | -0.022723 | -0.023741 | -0.024597 | -0.025404 | -0.025358
| 0.8 | 0.0016431 | -0.010277 | -0.015048 | -0.018118 | -0.020232 | -0.021764 | -0.02345 | -0.024548 | -0.025523 | -0.026145 | -0.02633
| 0.85 | 0.0015997 | -0.010329 | -0.01549 | -0.018901 | -0.020997 | -0.022372 | -0.024263 | -0.025157 | -0.026299 | -0.026995 | -0.027054
| 0.9 | 0.0014346 | -0.010588 | -0.015932 | -0.018944 | -0.021246 | -0.023142 | -0.024951 | -0.025992 | -0.027022 | -0.027609 | -0.028074
| 0.95 | 0.0014732 | -0.010847 | -0.016105 | -0.019455 | -0.021685 | -0.023788 | -0.025266 | -0.026721 | -0.027402 | -0.028213 | -0.02862
| 1 | 0.0016686 | -0.011106 | -0.016852 | -0.019879 | -0.022271 | -0.024387 | -0.026035 | -0.027425 | -0.028145 | -0.028741 | -0.029425
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41)
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41)
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41)

## CLASS8_OOP (hidden)
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
| 0.05 | 2.8182 | 2.8325 | 2.8424 | 2.8484 | 2.8508 | 2.8502 | 2.8471 | 2.8418 | 2.8349 | 2.8266 | 2.8173
| 0.1 | 2.9084 | 2.9558 | 2.9924 | 3.0168 | 3.0302 | 3.0346 | 3.0317 | 3.0232 | 3.0103 | 2.994 | 2.9752
| 0.15 | 2.932 | 3.0124 | 3.074 | 3.1136 | 3.1341 | 3.1401 | 3.1351 | 3.1223 | 3.1037 | 3.081 | 3.0553
| 0.2 | 2.9346 | 3.0346 | 3.1195 | 3.171 | 3.1961 | 3.2023 | 3.1953 | 3.1792 | 3.1567 | 3.1298 | 3.0999
| 0.25 | 2.9275 | 3.0413 | 3.1445 | 3.2059 | 3.2346 | 3.2412 | 3.233 | 3.2148 | 3.1898 | 3.1603 | 3.1278
| 0.3 | 2.9076 | 3.043 | 3.1581 | 3.2281 | 3.26 | 3.2672 | 3.2583 | 3.2388 | 3.2122 | 3.181 | 3.1467
| 0.35 | 2.8798 | 3.0421 | 3.1652 | 3.2427 | 3.2774 | 3.2854 | 3.2762 | 3.2559 | 3.2282 | 3.1959 | 3.1605
| 0.4 | 2.8473 | 3.0368 | 3.1686 | 3.2525 | 3.2898 | 3.2986 | 3.2894 | 3.2686 | 3.2405 | 3.2075 | 3.1714
| 0.45 | 2.8126 | 3.029 | 3.1726 | 3.2591 | 3.2988 | 3.3085 | 3.2995 | 3.2788 | 3.2504 | 3.2171 | 3.1806
| 0.5 | 2.7771 | 3.0198 | 3.1758 | 3.2636 | 3.3054 | 3.3162 | 3.3078 | 3.2873 | 3.2589 | 3.2255 | 3.1888
| 0.55 | 2.7418 | 3.0101 | 3.1772 | 3.2665 | 3.3106 | 3.3226 | 3.315 | 3.2948 | 3.2666 | 3.233 | 3.196
| 0.6 | 2.7074 | 3.0002 | 3.1775 | 3.2684 | 3.3147 | 3.3281 | 3.3214 | 3.3017 | 3.2735 | 3.2398 | 3.2025
| 0.65 | 2.6741 | 2.9905 | 3.1768 | 3.2705 | 3.3183 | 3.3332 | 3.3273 | 3.3079 | 3.2798 | 3.2459 | 3.2084
| 0.7 | 2.6423 | 2.9811 | 3.1756 | 3.2725 | 3.3215 | 3.338 | 3.3328 | 3.3137 | 3.2855 | 3.2514 | 3.2136
| 0.75 | 2.6121 | 2.9721 | 3.1739 | 3.2738 | 3.3246 | 3.3424 | 3.3379 | 3.3189 | 3.2906 | 3.2563 | 3.2182
| 0.8 | 2.5834 | 2.9635 | 3.1719 | 3.2747 | 3.3276 | 3.3467 | 3.3426 | 3.3237 | 3.2952 | 3.2607 | 3.2223
| 0.85 | 2.5562 | 2.9554 | 3.1697 | 3.2753 | 3.3305 | 3.3507 | 3.3469 | 3.328 | 3.2994 | 3.2646 | 3.226
| 0.9 | 2.5306 | 2.9477 | 3.1673 | 3.2757 | 3.3333 | 3.3544 | 3.3509 | 3.332 | 3.3032 | 3.2682 | 3.2293
| 0.95 | 2.5064 | 2.9405 | 3.1649 | 3.276 | 3.3361 | 3.3578 | 3.3545 | 3.3355 | 3.3066 | 3.2714 | 3.2323
| 1 | 2.4835 | 2.9336 | 3.1624 | 3.2763 | 3.3387 | 3.361 | 3.3579 | 3.3388 | 3.3097 | 3.2743 | 3.235
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
| 0.05 | 4.2251 | 4.1656 | 4.1056 | 4.0461 | 3.9872 | 3.9298 | 3.8734 | 3.8187 | 3.7683 | 3.7169 | 3.6669
| 0.1 | 3.824 | 3.7376 | 3.652 | 3.5677 | 3.4863 | 3.4083 | 3.3345 | 3.2652 | 3.1983 | 3.1347 | 3.075
| 0.15 | 3.551 | 3.4445 | 3.3421 | 3.2451 | 3.1527 | 3.0668 | 2.9859 | 2.911 | 2.8404 | 2.7733 | 2.7113
| 0.2 | 3.3552 | 3.228 | 3.1128 | 3.0077 | 2.9104 | 2.8203 | 2.7373 | 2.6598 | 2.5877 | 2.5207 | 2.4584
| 0.25 | 3.2071 | 3.0599 | 2.9358 | 2.8247 | 2.7245 | 2.6318 | 2.5474 | 2.4693 | 2.3973 | 2.331 | 2.2686
| 0.3 | 3.0956 | 2.9233 | 2.7918 | 2.6779 | 2.575 | 2.4809 | 2.3957 | 2.3178 | 2.2457 | 2.1802 | 2.1192
| 0.35 | 3.008 | 2.8116 | 2.672 | 2.5566 | 2.4517 | 2.3564 | 2.2705 | 2.1921 | 2.1207 | 2.0553 | 1.9968
| 0.4 | 2.9374 | 2.7164 | 2.5714 | 2.4525 | 2.3454 | 2.2494 | 2.1633 | 2.0848 | 2.0137 | 1.9513 | 1.8921
| 0.45 | 2.8795 | 2.6339 | 2.4847 | 2.3629 | 2.2537 | 2.1557 | 2.0696 | 1.9919 | 1.9219 | 1.8597 | 1.8026
| 0.5 | 2.8301 | 2.5618 | 2.4081 | 2.2822 | 2.1715 | 2.0731 | 1.9868 | 1.9104 | 1.8421 | 1.7811 | 1.7256
| 0.55 | 2.7894 | 2.4978 | 2.3397 | 2.2107 | 2.098 | 1.9992 | 1.9137 | 1.8376 | 1.7712 | 1.7101 | 1.6564
| 0.6 | 2.7548 | 2.4393 | 2.278 | 2.1445 | 2.0304 | 1.9321 | 1.8473 | 1.7732 | 1.7063 | 1.6484 | 1.5948
| 0.65 | 2.7247 | 2.3873 | 2.2211 | 2.0847 | 1.9694 | 1.8723 | 1.7876 | 1.7143 | 1.65 | 1.5919 | 1.5398
| 0.7 | 2.6972 | 2.34 | 2.1695 | 2.0294 | 1.9141 | 1.816 | 1.7327 | 1.6613 | 1.5971 | 1.5411 | 1.4911
| 0.75 | 2.6745 | 2.297 | 2.12 | 1.979 | 1.8625 | 1.7653 | 1.6834 | 1.6125 | 1.5505 | 1.4951 | 1.4454
| 0.8 | 2.6541 | 2.2567 | 2.0749 | 1.9309 | 1.8154 | 1.7188 | 1.6377 | 1.5672 | 1.5069 | 1.4531 | 1.4038
| 0.85 | 2.636 | 2.2191 | 2.0319 | 1.8866 | 1.7701 | 1.6753 | 1.5951 | 1.5264 | 1.467 | 1.4136 | 1.3665
| 0.9 | 2.62 | 2.1842 | 1.992 | 1.8453 | 1.7289 | 1.6351 | 1.5565 | 1.4886 | 1.4294 | 1.3782 | 1.3313
| 0.95 | 2.6041 | 2.1513 | 1.9544 | 1.8066 | 1.6907 | 1.5969 | 1.5196 | 1.4527 | 1.3952 | 1.3449 | 1.299
| 1 | 2.591 | 2.12 | 1.9184 | 1.7699 | 1.6544 | 1.562 | 1.4854 | 1.4201 | 1.3632 | 1.313 | 1.2692
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.017543 | 0.018913 | 0.020431 | 0.021905 | 0.02334 | 0.025252 | 0.026573 | 0.027203 | 0.028265 | 0.029262 | 0.030184
| 0.1 | 0.023517 | 0.025429 | 0.027254 | 0.028715 | 0.030051 | 0.031085 | 0.032032 | 0.032912 | 0.033474 | 0.033893 | 0.034478
| 0.15 | 0.025078 | 0.02763 | 0.029371 | 0.030675 | 0.031709 | 0.032451 | 0.033031 | 0.033514 | 0.033784 | 0.03396 | 0.0342
| 0.2 | 0.024386 | 0.027897 | 0.029708 | 0.03091 | 0.031533 | 0.031996 | 0.032507 | 0.032757 | 0.033037 | 0.033 | 0.032991
| 0.25 | 0.023047 | 0.027487 | 0.029249 | 0.03036 | 0.031008 | 0.031631 | 0.031804 | 0.032077 | 0.032102 | 0.032131 | 0.032111
| 0.3 | 0.021317 | 0.026539 | 0.028812 | 0.029803 | 0.030598 | 0.030928 | 0.031307 | 0.031353 | 0.031444 | 0.031273 | 0.03137
| 0.35 | 0.019607 | 0.026382 | 0.027873 | 0.029287 | 0.030051 | 0.030619 | 0.030772 | 0.030965 | 0.030763 | 0.030725 | 0.03026
| 0.4 | 0.018072 | 0.025757 | 0.02758 | 0.028875 | 0.029823 | 0.030448 | 0.030429 | 0.030481 | 0.030232 | 0.030012 | 0.029658
| 0.45 | 0.016226 | 0.025037 | 0.027301 | 0.028739 | 0.029783 | 0.030155 | 0.030305 | 0.030034 | 0.029625 | 0.02921 | 0.02881
| 0.5 | 0.015011 | 0.024717 | 0.026848 | 0.028611 | 0.029617 | 0.029911 | 0.029821 | 0.02925 | 0.029143 | 0.028492 | 0.028054
| 0.55 | 0.014238 | 0.024227 | 0.026783 | 0.028492 | 0.029416 | 0.029667 | 0.029321 | 0.028824 | 0.028378 | 0.02771 | 0.027214
| 0.6 | 0.013263 | 0.023595 | 0.026891 | 0.028566 | 0.02904 | 0.029147 | 0.028522 | 0.028129 | 0.027774 | 0.027149 | 0.026551
| 0.65 | 0.012022 | 0.023559 | 0.02674 | 0.0285 | 0.028946 | 0.028765 | 0.028197 | 0.027459 | 0.027016 | 0.026542 | 0.025826
| 0.7 | 0.011139 | 0.023243 | 0.026541 | 0.028454 | 0.02876 | 0.028385 | 0.027673 | 0.027113 | 0.026309 | 0.025984 | 0.025248
| 0.75 | 0.010493 | 0.022953 | 0.026676 | 0.028135 | 0.028184 | 0.027655 | 0.02717 | 0.02667 | 0.025896 | 0.025432 | 0.024805
| 0.8 | 0.010186 | 0.022426 | 0.026572 | 0.027866 | 0.027729 | 0.027313 | 0.026804 | 0.025975 | 0.025428 | 0.024905 | 0.024124
| 0.85 | 0.0095625 | 0.02244 | 0.026735 | 0.027644 | 0.027415 | 0.026878 | 0.026174 | 0.025529 | 0.024816 | 0.024382 | 0.023656
| 0.9 | 0.0087907 | 0.022364 | 0.026689 | 0.0273 | 0.027048 | 0.026535 | 0.025868 | 0.025098 | 0.024151 | 0.023724 | 0.02309
| 0.95 | 0.0082925 | 0.022353 | 0.026607 | 0.027074 | 0.026633 | 0.026142 | 0.025152 | 0.024588 | 0.024 | 0.023103 | 0.022691
| 1 | 0.0077832 | 0.022442 | 0.026498 | 0.026821 | 0.026376 | 0.025641 | 0.024826 | 0.024175 | 0.023471 | 0.022824 | 0.02209
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0025564 | 0.0027977 | 0.0030042 | 0.0032212 | 0.0034199 | 0.0036167 | 0.0037935 | 0.0039577 | 0.0041091 | 0.00424 | 0.0043046
| 0.1 | 0.0030158 | 0.0033451 | 0.0036494 | 0.003904 | 0.0041268 | 0.0043027 | 0.0044521 | 0.0045686 | 0.0046531 | 0.0047208 | 0.0048342
| 0.15 | 0.0031127 | 0.0036091 | 0.0039346 | 0.0041867 | 0.0043839 | 0.0045512 | 0.0046196 | 0.0046942 | 0.004773 | 0.0048212 | 0.0048454
| 0.2 | 0.0029746 | 0.0036624 | 0.0040516 | 0.0042848 | 0.0044476 | 0.0045539 | 0.0046118 | 0.0046375 | 0.0046917 | 0.0047064 | 0.0047199
| 0.25 | 0.0027491 | 0.0036623 | 0.0040729 | 0.0043032 | 0.0044106 | 0.0044807 | 0.0045462 | 0.0045533 | 0.0045671 | 0.0046034 | 0.004551
| 0.3 | 0.0024988 | 0.0036191 | 0.0040832 | 0.0042361 | 0.0043575 | 0.0044301 | 0.0044602 | 0.004512 | 0.0044971 | 0.0044913 | 0.0044277
| 0.35 | 0.0022727 | 0.0035728 | 0.0039856 | 0.0041709 | 0.0042824 | 0.0043665 | 0.0044038 | 0.0044234 | 0.004406 | 0.0043833 | 0.0043146
| 0.4 | 0.0020893 | 0.0035358 | 0.0039353 | 0.0041487 | 0.0042541 | 0.0043569 | 0.0043674 | 0.0043551 | 0.0043384 | 0.0042975 | 0.0042373
| 0.45 | 0.0019029 | 0.0034989 | 0.0038757 | 0.0040768 | 0.0042276 | 0.0043053 | 0.0043091 | 0.0042997 | 0.0042373 | 0.0041813 | 0.0041391
| 0.5 | 0.0016728 | 0.0034807 | 0.0038172 | 0.0040775 | 0.0042018 | 0.0042715 | 0.0042566 | 0.004223 | 0.0041759 | 0.0040919 | 0.0040376
| 0.55 | 0.0015218 | 0.0034325 | 0.0038032 | 0.0040608 | 0.0042 | 0.0042333 | 0.0041923 | 0.0041773 | 0.0041007 | 0.0040168 | 0.0039178
| 0.6 | 0.0014229 | 0.0033608 | 0.0037971 | 0.0040773 | 0.004172 | 0.0041983 | 0.0041297 | 0.0041011 | 0.0040182 | 0.0039431 | 0.0038379
| 0.65 | 0.0013011 | 0.0033237 | 0.0037876 | 0.0040705 | 0.0041752 | 0.004134 | 0.00408 | 0.0040072 | 0.0039111 | 0.0038575 | 0.0037566
| 0.7 | 0.001182 | 0.0032922 | 0.0038037 | 0.0040493 | 0.0041342 | 0.0041099 | 0.0040264 | 0.0039375 | 0.003851 | 0.0037739 | 0.0036792
| 0.75 | 0.0010433 | 0.0032724 | 0.0037685 | 0.0040418 | 0.0040721 | 0.0040496 | 0.003957 | 0.0038548 | 0.0037897 | 0.0036786 | 0.0035849
| 0.8 | 0.00099854 | 0.0032408 | 0.0037677 | 0.0040228 | 0.0040524 | 0.0040037 | 0.0039091 | 0.0038237 | 0.0036999 | 0.0035946 | 0.0035447
| 0.85 | 0.00091777 | 0.0032118 | 0.0037908 | 0.0040005 | 0.0040203 | 0.0039262 | 0.0038357 | 0.003725 | 0.0036632 | 0.0035194 | 0.0034405
| 0.9 | 0.00084625 | 0.0031673 | 0.0037979 | 0.0039909 | 0.0039643 | 0.0038715 | 0.0037823 | 0.0036435 | 0.0035657 | 0.0034562 | 0.0033668
| 0.95 | 0.00077456 | 0.0031487 | 0.0038061 | 0.0039551 | 0.0039215 | 0.0038503 | 0.0037137 | 0.0036053 | 0.0034992 | 0.0034072 | 0.0032975
| 1 | 0.00071901 | 0.003147 | 0.0038154 | 0.0039252 | 0.0038801 | 0.0037696 | 0.0036639 | 0.0035419 | 0.0034325 | 0.0033204 | 0.0032442
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.4117 | 1.5265 | 1.6236 | 1.7064 | 1.7769 | 1.8364 | 1.8894 | 1.934 | 1.9645 | 1.9994 | 2.0279
| 0.1 | 1.5227 | 1.807 | 2.0291 | 2.2057 | 2.3493 | 2.463 | 2.5571 | 2.6271 | 2.693 | 2.7457 | 2.7876
| 0.15 | 1.5235 | 1.9901 | 2.3359 | 2.6008 | 2.8169 | 2.9696 | 3.1144 | 3.2068 | 3.2811 | 3.3564 | 3.4027
| 0.2 | 1.4918 | 2.1352 | 2.6189 | 2.9416 | 3.2173 | 3.4297 | 3.579 | 3.7081 | 3.8065 | 3.9962 | 3.9539
| 0.25 | 1.4562 | 2.263 | 2.8613 | 3.1551 | 3.585 | 3.8293 | 3.9903 | 4.1918 | 4.2735 | 4.3894 | 4.3464
| 0.3 | 1.4157 | 2.3897 | 3.0491 | 3.578 | 3.95 | 4.2411 | 4.3156 | 4.5476 | 4.6498 | 4.7826 | 4.8257
| 0.35 | 1.3786 | 2.5047 | 3.278 | 3.7764 | 4.2555 | 4.5211 | 4.6982 | 4.9243 | 5.0504 | 5.1516 | 5.244
| 0.4 | 1.3472 | 2.6406 | 3.4545 | 4.0627 | 4.561 | 4.7825 | 5.0656 | 5.263 | 5.4189 | 5.4468 | 5.6126
| 0.45 | 1.3195 | 2.7504 | 3.631 | 4.3654 | 4.7707 | 5.1307 | 5.3843 | 5.5994 | 5.7461 | 5.8663 | 5.9579
| 0.5 | 1.3058 | 2.8244 | 3.8359 | 4.5306 | 5.0331 | 5.4184 | 5.6909 | 5.9068 | 6.0643 | 6.192 | 6.2881
| 0.55 | 1.2825 | 3.0025 | 4.0041 | 4.737 | 5.2786 | 5.6768 | 5.9662 | 6.1919 | 6.3626 | 6.4817 | 6.5904
| 0.6 | 1.2656 | 3.0368 | 4.1743 | 4.953 | 5.5118 | 5.9231 | 6.2264 | 6.474 | 6.6413 | 6.7794 | 6.8795
| 0.65 | 1.2467 | 3.1342 | 4.3289 | 5.1604 | 5.7363 | 6.1772 | 6.4831 | 6.7364 | 6.918 | 7.0599 | 7.1599
| 0.7 | 1.2405 | 3.2329 | 4.4874 | 5.3535 | 5.9468 | 6.3986 | 6.7242 | 6.9845 | 7.1753 | 7.3217 | 7.4347
| 0.75 | 1.2272 | 3.3282 | 4.6629 | 5.5342 | 6.1568 | 6.6242 | 6.9596 | 7.2294 | 7.4292 | 7.5749 | 7.6927
| 0.8 | 1.215 | 3.4232 | 4.8098 | 5.7121 | 6.3551 | 6.8334 | 7.191 | 7.4605 | 7.6706 | 7.8252 | 7.9427
| 0.85 | 1.2035 | 3.5252 | 4.9504 | 5.8789 | 6.556 | 7.0354 | 7.4016 | 7.6886 | 7.9058 | 8.0612 | 8.1911
| 0.9 | 1.1952 | 3.6162 | 5.0873 | 6.0514 | 6.7326 | 7.2393 | 7.6176 | 7.9037 | 8.1295 | 8.298 | 8.4137
| 0.95 | 1.1927 | 3.7042 | 5.2199 | 6.2054 | 6.9143 | 7.4274 | 7.8184 | 8.1089 | 8.3497 | 8.5201 | 8.6447
| 1 | 1.183 | 3.725 | 5.3362 | 6.3637 | 7.0865 | 7.6198 | 8.018 | 8.3247 | 8.5644 | 8.7382 | 8.8727
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0044477 | 0.0045792 | 0.0044699 | 0.0054261 | 0.0059469 | 0.0053588 | 0.0054164 | 0.0083319 | 0.0097078 | 0.010194 | 0.010983
| 0.1 | 0.013469 | 0.01322 | 0.014607 | 0.015231 | 0.016699 | 0.01784 | 0.019465 | 0.022568 | 0.023628 | 0.022369 | 0.026239
| 0.15 | 0.018379 | 0.019359 | 0.021035 | 0.022886 | 0.028037 | 0.028225 | 0.028525 | 0.030526 | 0.034106 | 0.033301 | 0.034731
| 0.2 | 0.020184 | 0.02323 | 0.029762 | 0.027418 | 0.03335 | 0.034273 | 0.035458 | 0.037841 | 0.041502 | 0.041363 | 0.043132
| 0.25 | 0.019124 | 0.024471 | 0.032701 | 0.03195 | 0.038662 | 0.040322 | 0.042391 | 0.045156 | 0.048898 | 0.049425 | 0.051533
| 0.3 | 0.01911 | 0.025712 | 0.035641 | 0.036483 | 0.043974 | 0.04637 | 0.049324 | 0.05247 | 0.056294 | 0.057487 | 0.059934
| 0.35 | 0.01703 | 0.026954 | 0.038581 | 0.041015 | 0.049287 | 0.052418 | 0.056257 | 0.059785 | 0.06369 | 0.065549 | 0.068334
| 0.4 | 0.014132 | 0.028195 | 0.041521 | 0.045548 | 0.054599 | 0.058467 | 0.06319 | 0.0671 | 0.071086 | 0.073611 | 0.076735
| 0.45 | 0.01479 | 0.029436 | 0.04446 | 0.05008 | 0.059911 | 0.064515 | 0.070123 | 0.074415 | 0.078482 | 0.081673 | 0.085136
| 0.5 | 0.012295 | 0.030678 | 0.0474 | 0.054613 | 0.065224 | 0.070564 | 0.077056 | 0.081729 | 0.085878 | 0.089735 | 0.091931
| 0.55 | 0.0093476 | 0.031919 | 0.05034 | 0.059145 | 0.074903 | 0.078846 | 0.083989 | 0.088274 | 0.093274 | 0.097797 | 0.097139
| 0.6 | 0.0078389 | 0.03316 | 0.05328 | 0.063678 | 0.079907 | 0.084875 | 0.091607 | 0.093727 | 0.10067 | 0.10179 | 0.10235
| 0.65 | 0.0084306 | 0.034402 | 0.056219 | 0.06821 | 0.083987 | 0.09063 | 0.096392 | 0.099368 | 0.1066 | 0.10552 | 0.10756
| 0.7 | 0.0075077 | 0.035643 | 0.059159 | 0.072743 | 0.08793 | 0.096979 | 0.09993 | 0.10495 | 0.10776 | 0.11112 | 0.11277
| 0.75 | 0.006964 | 0.036884 | 0.062099 | 0.077275 | 0.091872 | 0.099025 | 0.10623 | 0.1093 | 0.1142 | 0.11588 | 0.11797
| 0.8 | 0.0034 | 0.038126 | 0.065039 | 0.082805 | 0.098272 | 0.10385 | 0.11055 | 0.11183 | 0.11939 | 0.12136 | 0.12318
| 0.85 | 0.0030979 | 0.039367 | 0.067978 | 0.085341 | 0.099042 | 0.10653 | 0.11481 | 0.11758 | 0.12328 | 0.1292 | 0.12839
| 0.9 | 0.0038918 | 0.040608 | 0.070918 | 0.091407 | 0.10433 | 0.11184 | 0.11824 | 0.12222 | 0.1265 | 0.13207 | 0.1336
| 0.95 | 0.0036052 | 0.04185 | 0.073858 | 0.092788 | 0.10607 | 0.11802 | 0.1206 | 0.12578 | 0.13077 | 0.13604 | 0.13881
| 1 | 0.0027186 | 0.043091 | 0.078002 | 0.098195 | 0.10863 | 0.11984 | 0.12576 | 0.13217 | 0.13444 | 0.13815 | 0.14116
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0013866 | -0.0021897 | -0.0029077 | -0.0034282 | -0.0038202 | -0.0041091 | -0.0043748 | -0.00457 | -0.0048097 | -0.0048972 | -0.0047844
| 0.1 | -0.00069863 | -0.00271 | -0.004129 | -0.0051562 | -0.0058695 | -0.0064295 | -0.0068139 | -0.0074445 | -0.0074012 | -0.007383 | -0.007713
| 0.15 | -2.76e-05 | -0.0030148 | -0.0050508 | -0.0064348 | -0.0071414 | -0.0081024 | -0.0094302 | -0.0091645 | -0.009374 | -0.010105 | -0.0099738
| 0.2 | 0.00042327 | -0.0034244 | -0.0058656 | -0.0075644 | -0.0087558 | -0.0096046 | -0.01025 | -0.010465 | -0.010953 | -0.011329 | -0.011231
| 0.25 | 0.00053678 | -0.0038624 | -0.0066088 | -0.0085934 | -0.0099306 | -0.01096 | -0.011626 | -0.011765 | -0.012532 | -0.012372 | -0.012487
| 0.3 | 0.00067109 | -0.0049519 | -0.0069044 | -0.0096108 | -0.01047 | -0.01214 | -0.012741 | -0.013066 | -0.013687 | -0.013415 | -0.013744
| 0.35 | 0.00069948 | -0.0053748 | -0.0077229 | -0.01053 | -0.011546 | -0.013153 | -0.013855 | -0.014366 | -0.014753 | -0.014458 | -0.015001
| 0.4 | 0.00044877 | -0.0057978 | -0.0085414 | -0.011185 | -0.012622 | -0.014477 | -0.014911 | -0.015249 | -0.015629 | -0.015501 | -0.016068
| 0.45 | 0.00044717 | -0.0062207 | -0.0097954 | -0.011841 | -0.013698 | -0.01508 | -0.015264 | -0.016071 | -0.016558 | -0.016607 | -0.017232
| 0.5 | 0.00060627 | -0.0066436 | -0.010449 | -0.012496 | -0.014377 | -0.015381 | -0.015968 | -0.017087 | -0.017241 | -0.017294 | -0.017948
| 0.55 | 0.000576 | -0.0070665 | -0.011177 | -0.013151 | -0.014683 | -0.016003 | -0.016278 | -0.017442 | -0.017943 | -0.018265 | -0.018575
| 0.6 | 0.00030643 | -0.0074894 | -0.011906 | -0.013914 | -0.015437 | -0.016548 | -0.017285 | -0.01838 | -0.018293 | -0.019158 | -0.019202
| 0.65 | 0.00031652 | -0.0079124 | -0.012635 | -0.014288 | -0.015941 | -0.017105 | -0.017779 | -0.018858 | -0.019145 | -0.019891 | -0.019816
| 0.7 | 0.00021668 | -0.0083353 | -0.012498 | -0.014961 | -0.016643 | -0.017862 | -0.018532 | -0.020143 | -0.019707 | -0.020431 | -0.020601
| 0.75 | 0.00043081 | -0.0087582 | -0.012531 | -0.015291 | -0.016982 | -0.017941 | -0.019416 | -0.02015 | -0.020668 | -0.021112 | -0.021642
| 0.8 | 0.00018251 | -0.0091811 | -0.013187 | -0.015583 | -0.01749 | -0.018621 | -0.019807 | -0.020412 | -0.021266 | -0.021715 | -0.022045
| 0.85 | 0.00016481 | -0.009604 | -0.013469 | -0.016236 | -0.017744 | -0.019388 | -0.020383 | -0.021783 | -0.021786 | -0.022266 | -0.02268
| 0.9 | 0.00014352 | -0.010027 | -0.013918 | -0.016448 | -0.018176 | -0.019911 | -0.020992 | -0.021924 | -0.022583 | -0.02293 | -0.023373
| 0.95 | 0.00012006 | -0.01045 | -0.01437 | -0.016971 | -0.018959 | -0.020098 | -0.021617 | -0.022158 | -0.023057 | -0.023683 | -0.024077
| 1 | 8.299e-05 | -0.010873 | -0.014417 | -0.017374 | -0.018991 | -0.020693 | -0.021953 | -0.022717 | -0.023537 | -0.02448 | -0.024566
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47)
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47)
-)-
𝑅𝑅𝑅𝑉=〖𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47)
-)-
𝑡𝑑=〖𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47)

## CLASS7_LS>= (hidden)
If Iload/Isc x 5.6569 ≥1 | [12 empty] | If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 |  | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0121 | 1.0241 | 1.0331 | 1.0396 | 1.044 | 1.0465 | 1.0474 | 1.0468 | 1.0451 | 1.0411 | 1.0378 |  | 0.05 | 1.0121 | 1.0241 | 1.0331 | 1.0396 | 1.044 | 1.0465 | 1.0474 | 1.0468 | 1.0451 | 1.0411 | 1.0378
| 0.1 | 1.0313 | 1.0544 | 1.0738 | 1.0876 | 1.0954 | 1.0988 | 1.0987 | 1.0961 | 1.0916 | 1.0852 | 1.0784 |  | 0.1 | 1.0313 | 1.0544 | 1.0738 | 1.0876 | 1.0954 | 1.0988 | 1.0987 | 1.0961 | 1.0916 | 1.0852 | 1.0784
| 0.15 | 1.0285 | 1.0661 | 1.0944 | 1.1125 | 1.1223 | 1.1262 | 1.1256 | 1.122 | 1.1161 | 1.1083 | 1.0997 |  | 0.15 | 1.0285 | 1.0661 | 1.0944 | 1.1125 | 1.1223 | 1.1262 | 1.1256 | 1.122 | 1.1161 | 1.1083 | 1.0997
| 0.2 | 1.0186 | 1.0675 | 1.1054 | 1.128 | 1.1397 | 1.1437 | 1.1426 | 1.1379 | 1.1308 | 1.1219 | 1.112 |  | 0.2 | 1.0186 | 1.0675 | 1.1054 | 1.128 | 1.1397 | 1.1437 | 1.1426 | 1.1379 | 1.1308 | 1.1219 | 1.112
| 0.25 | 1.0036 | 1.0645 | 1.1108 | 1.1372 | 1.1502 | 1.1545 | 1.1531 | 1.1479 | 1.14 | 1.1303 | 1.1196 |  | 0.25 | 1.0036 | 1.0645 | 1.1108 | 1.1372 | 1.1502 | 1.1545 | 1.1531 | 1.1479 | 1.14 | 1.1303 | 1.1196
| 0.3 | 0.98584 | 1.0596 | 1.1133 | 1.1428 | 1.157 | 1.1617 | 1.1601 | 1.1546 | 1.1463 | 1.1362 | 1.125 |  | 0.3 | 0.98584 | 1.0596 | 1.1133 | 1.1428 | 1.157 | 1.1617 | 1.1601 | 1.1546 | 1.1463 | 1.1362 | 1.125
| 0.35 | 0.96739 | 1.0541 | 1.1142 | 1.1463 | 1.1616 | 1.1666 | 1.1652 | 1.1596 | 1.1511 | 1.1408 | 1.1294 |  | 0.35 | 0.96739 | 1.0541 | 1.1142 | 1.1463 | 1.1616 | 1.1666 | 1.1652 | 1.1596 | 1.1511 | 1.1408 | 1.1294
| 0.4 | 0.94923 | 1.0487 | 1.1142 | 1.1485 | 1.1648 | 1.1704 | 1.1692 | 1.1636 | 1.1551 | 1.1447 | 1.133 |  | 0.4 | 0.94923 | 1.0487 | 1.1142 | 1.1485 | 1.1648 | 1.1704 | 1.1692 | 1.1636 | 1.1551 | 1.1447 | 1.133
| 0.45 | 0.93186 | 1.0435 | 1.1136 | 1.1499 | 1.1673 | 1.1734 | 1.1725 | 1.1671 | 1.1586 | 1.148 | 1.1361 |  | 0.45 | 0.93186 | 1.0435 | 1.1136 | 1.1499 | 1.1673 | 1.1734 | 1.1725 | 1.1671 | 1.1586 | 1.148 | 1.1361
| 0.5 | 0.91555 | 1.0387 | 1.1127 | 1.1508 | 1.1692 | 1.176 | 1.1755 | 1.1701 | 1.1616 | 1.1509 | 1.1389 |  | 0.5 | 0.91555 | 1.0387 | 1.1127 | 1.1508 | 1.1692 | 1.176 | 1.1755 | 1.1701 | 1.1616 | 1.1509 | 1.1389
| 0.55 | 0.90037 | 1.0343 | 1.1117 | 1.1515 | 1.171 | 1.1784 | 1.1781 | 1.1729 | 1.1643 | 1.1534 | 1.1412 |  | 0.55 | 0.90037 | 1.0343 | 1.1117 | 1.1515 | 1.171 | 1.1784 | 1.1781 | 1.1729 | 1.1643 | 1.1534 | 1.1412
| 0.6 | 0.88633 | 1.0302 | 1.1105 | 1.152 | 1.1726 | 1.1806 | 1.1806 | 1.1753 | 1.1666 | 1.1557 | 1.1433 |  | 0.6 | 0.88633 | 1.0302 | 1.1105 | 1.152 | 1.1726 | 1.1806 | 1.1806 | 1.1753 | 1.1666 | 1.1557 | 1.1433
| 0.65 | 0.8734 | 1.0266 | 1.1094 | 1.1525 | 1.1741 | 1.1826 | 1.1827 | 1.1775 | 1.1687 | 1.1576 | 1.145 |  | 0.65 | 0.8734 | 1.0266 | 1.1094 | 1.1525 | 1.1741 | 1.1826 | 1.1827 | 1.1775 | 1.1687 | 1.1576 | 1.145
| 0.7 | 0.86149 | 1.0232 | 1.1083 | 1.153 | 1.1756 | 1.1845 | 1.1847 | 1.1794 | 1.1705 | 1.1593 | 1.1466 |  | 0.7 | 0.86149 | 1.0232 | 1.1083 | 1.153 | 1.1756 | 1.1845 | 1.1847 | 1.1794 | 1.1705 | 1.1593 | 1.1466
| 0.75 | 0.85053 | 1.0201 | 1.1073 | 1.1536 | 1.177 | 1.1862 | 1.1865 | 1.1811 | 1.1721 | 1.1607 | 1.1479 |  | 0.75 | 0.85053 | 1.0201 | 1.1073 | 1.1536 | 1.177 | 1.1862 | 1.1865 | 1.1811 | 1.1721 | 1.1607 | 1.1479
| 0.8 | 0.84044 | 1.0172 | 1.1064 | 1.1541 | 1.1783 | 1.1877 | 1.188 | 1.1826 | 1.1735 | 1.162 | 1.1491 |  | 0.8 | 0.84044 | 1.0172 | 1.1064 | 1.1541 | 1.1783 | 1.1877 | 1.188 | 1.1826 | 1.1735 | 1.162 | 1.1491
| 0.85 | 0.83114 | 1.0146 | 1.1055 | 1.1547 | 1.1795 | 1.1891 | 1.1894 | 1.1839 | 1.1747 | 1.1632 | 1.1501 |  | 0.85 | 0.83114 | 1.0146 | 1.1055 | 1.1547 | 1.1795 | 1.1891 | 1.1894 | 1.1839 | 1.1747 | 1.1632 | 1.1501
| 0.9 | 0.82255 | 1.0122 | 1.1049 | 1.1554 | 1.1806 | 1.1904 | 1.1907 | 1.1851 | 1.1758 | 1.1642 | 1.1511 |  | 0.9 | 0.82255 | 1.0122 | 1.1049 | 1.1554 | 1.1806 | 1.1904 | 1.1907 | 1.1851 | 1.1758 | 1.1642 | 1.1511
| 0.95 | 0.81461 | 1.0099 | 1.1043 | 1.156 | 1.1816 | 1.1915 | 1.1918 | 1.1862 | 1.1769 | 1.1652 | 1.152 |  | 0.95 | 0.81461 | 1.0099 | 1.1043 | 1.156 | 1.1816 | 1.1915 | 1.1918 | 1.1862 | 1.1769 | 1.1652 | 1.152
| 1 | 0.80726 | 1.0078 | 1.1038 | 1.1566 | 1.1826 | 1.1925 | 1.1928 | 1.1872 | 1.1778 | 1.166 | 1.1528 |  | 1 | 0.80726 | 1.0078 | 1.1038 | 1.1566 | 1.1826 | 1.1925 | 1.1928 | 1.1872 | 1.1778 | 1.166 | 1.1528
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 |  | 0 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| 0.05 | 1.5278 | 1.4974 | 1.4711 | 1.4452 | 1.4198 | 1.3951 | 1.3713 | 1.3492 | 1.327 | 1.3119 | 1.2915 |  | 0.05 | 1.5278 | 1.4974 | 1.4711 | 1.4452 | 1.4198 | 1.3951 | 1.3713 | 1.3492 | 1.327 | 1.3119 | 1.2915
| 0.1 | 1.372 | 1.3313 | 1.2943 | 1.2595 | 1.2261 | 1.1951 | 1.1662 | 1.1388 | 1.1128 | 1.0914 | 1.0683 |  | 0.1 | 1.372 | 1.3313 | 1.2943 | 1.2595 | 1.2261 | 1.1951 | 1.1662 | 1.1388 | 1.1128 | 1.0914 | 1.0683
| 0.15 | 1.2732 | 1.222 | 1.1787 | 1.1392 | 1.1029 | 1.0693 | 1.0385 | 1.0095 | 0.98255 | 0.95943 | 0.936 |  | 0.15 | 1.2732 | 1.222 | 1.1787 | 1.1392 | 1.1029 | 1.0693 | 1.0385 | 1.0095 | 0.98255 | 0.95943 | 0.936
| 0.2 | 1.2062 | 1.1437 | 1.0956 | 1.0535 | 1.0149 | 0.97994 | 0.94837 | 0.91866 | 0.89175 | 0.86819 | 0.84511 |  | 0.2 | 1.2062 | 1.1437 | 1.0956 | 1.0535 | 1.0149 | 0.97994 | 0.94837 | 0.91866 | 0.89175 | 0.86819 | 0.84511
| 0.25 | 1.1578 | 1.0839 | 1.0317 | 0.98748 | 0.94789 | 0.91194 | 0.87944 | 0.84961 | 0.82282 | 0.79942 | 0.77653 |  | 0.25 | 1.1578 | 1.0839 | 1.0317 | 0.98748 | 0.94789 | 0.91194 | 0.87944 | 0.84961 | 0.82282 | 0.79942 | 0.77653
| 0.3 | 1.1225 | 1.0353 | 0.98046 | 0.93448 | 0.8934 | 0.85662 | 0.82409 | 0.79452 | 0.76776 | 0.74461 | 0.72297 |  | 0.3 | 1.1225 | 1.0353 | 0.98046 | 0.93448 | 0.8934 | 0.85662 | 0.82409 | 0.79452 | 0.76776 | 0.74461 | 0.72297
| 0.35 | 1.0954 | 0.99573 | 0.93796 | 0.88995 | 0.84761 | 0.81046 | 0.77804 | 0.74848 | 0.72246 | 0.69998 | 0.67863 |  | 0.35 | 1.0954 | 0.99573 | 0.93796 | 0.88995 | 0.84761 | 0.81046 | 0.77804 | 0.74848 | 0.72246 | 0.69998 | 0.67863
| 0.4 | 1.074 | 0.96206 | 0.90112 | 0.85161 | 0.80837 | 0.7708 | 0.73863 | 0.70985 | 0.68432 | 0.66215 | 0.64183 |  | 0.4 | 1.074 | 0.96206 | 0.90112 | 0.85161 | 0.80837 | 0.7708 | 0.73863 | 0.70985 | 0.68432 | 0.66215 | 0.64183
| 0.45 | 1.0559 | 0.93289 | 0.8694 | 0.81792 | 0.77392 | 0.73668 | 0.70464 | 0.67623 | 0.65136 | 0.63017 | 0.60992 |  | 0.45 | 1.0559 | 0.93289 | 0.8694 | 0.81792 | 0.77392 | 0.73668 | 0.70464 | 0.67623 | 0.65136 | 0.63017 | 0.60992
| 0.5 | 1.0418 | 0.90729 | 0.84085 | 0.78755 | 0.74354 | 0.70628 | 0.67478 | 0.64717 | 0.62294 | 0.60192 | 0.58264 |  | 0.5 | 1.0418 | 0.90729 | 0.84085 | 0.78755 | 0.74354 | 0.70628 | 0.67478 | 0.64717 | 0.62294 | 0.60192 | 0.58264
| 0.55 | 1.0299 | 0.88416 | 0.81511 | 0.76058 | 0.71637 | 0.67957 | 0.64866 | 0.62156 | 0.59783 | 0.57751 | 0.55859 |  | 0.55 | 1.0299 | 0.88416 | 0.81511 | 0.76058 | 0.71637 | 0.67957 | 0.64866 | 0.62156 | 0.59783 | 0.57751 | 0.55859
| 0.6 | 1.0199 | 0.86367 | 0.7917 | 0.7361 | 0.69198 | 0.65557 | 0.62511 | 0.59883 | 0.5756 | 0.55555 | 0.53747 |  | 0.6 | 1.0199 | 0.86367 | 0.7917 | 0.7361 | 0.69198 | 0.65557 | 0.62511 | 0.59883 | 0.5756 | 0.55555 | 0.53747
| 0.65 | 1.0105 | 0.84486 | 0.77035 | 0.71405 | 0.67005 | 0.63403 | 0.60418 | 0.5781 | 0.55572 | 0.53599 | 0.51843 |  | 0.65 | 1.0105 | 0.84486 | 0.77035 | 0.71405 | 0.67005 | 0.63403 | 0.60418 | 0.5781 | 0.55572 | 0.53599 | 0.51843
| 0.7 | 1.0031 | 0.82769 | 0.75029 | 0.69359 | 0.64979 | 0.61442 | 0.58469 | 0.55938 | 0.53777 | 0.51868 | 0.5015 |  | 0.7 | 1.0031 | 0.82769 | 0.75029 | 0.69359 | 0.64979 | 0.61442 | 0.58469 | 0.55938 | 0.53777 | 0.51868 | 0.5015
| 0.75 | 0.99662 | 0.81151 | 0.73175 | 0.67495 | 0.63134 | 0.59643 | 0.56768 | 0.5426 | 0.5213 | 0.50278 | 0.48602 |  | 0.75 | 0.99662 | 0.81151 | 0.73175 | 0.67495 | 0.63134 | 0.59643 | 0.56768 | 0.5426 | 0.5213 | 0.50278 | 0.48602
| 0.8 | 0.99088 | 0.79642 | 0.71479 | 0.65741 | 0.61422 | 0.57999 | 0.5514 | 0.52742 | 0.50638 | 0.48811 | 0.47195 |  | 0.8 | 0.99088 | 0.79642 | 0.71479 | 0.65741 | 0.61422 | 0.57999 | 0.5514 | 0.52742 | 0.50638 | 0.48811 | 0.47195
| 0.85 | 0.98508 | 0.78252 | 0.69896 | 0.64163 | 0.59841 | 0.56472 | 0.53699 | 0.51315 | 0.49274 | 0.47502 | 0.45883 |  | 0.85 | 0.98508 | 0.78252 | 0.69896 | 0.64163 | 0.59841 | 0.56472 | 0.53699 | 0.51315 | 0.49274 | 0.47502 | 0.45883
| 0.9 | 0.98053 | 0.76912 | 0.68418 | 0.62654 | 0.58404 | 0.55057 | 0.52331 | 0.50022 | 0.47984 | 0.4626 | 0.44694 |  | 0.9 | 0.98053 | 0.76912 | 0.68418 | 0.62654 | 0.58404 | 0.55057 | 0.52331 | 0.50022 | 0.47984 | 0.4626 | 0.44694
| 0.95 | 0.97654 | 0.75676 | 0.66988 | 0.61248 | 0.57031 | 0.53776 | 0.51082 | 0.48807 | 0.46826 | 0.45128 | 0.43592 |  | 0.95 | 0.97654 | 0.75676 | 0.66988 | 0.61248 | 0.57031 | 0.53776 | 0.51082 | 0.48807 | 0.46826 | 0.45128 | 0.43592
| 1 | 0.97287 | 0.74495 | 0.65661 | 0.59926 | 0.55803 | 0.52562 | 0.49901 | 0.47675 | 0.45753 | 0.44053 | 0.42561 |  | 1 | 0.97287 | 0.74495 | 0.65661 | 0.59926 | 0.55803 | 0.52562 | 0.49901 | 0.47675 | 0.45753 | 0.44053 | 0.42561
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0027122 | -0.00073244 | 0.00089025 | 0.002398 | 0.0037395 | 0.0048885 | 0.0056514 | 0.0064972 | 0.0074678 | 0.008047 | 0.0086098 |  | 0.05 | -0.0027122 | -0.00073244 | 0.00089025 | 0.002398 | 0.0037395 | 0.0048885 | 0.0056514 | 0.0064972 | 0.0074678 | 0.008047 | 0.0086098
| 0.1 | -0.00013552 | 0.0028741 | 0.0049102 | 0.0064696 | 0.0076174 | 0.0085232 | 0.0091444 | 0.0099098 | 0.010401 | 0.010823 | 0.011144 |  | 0.1 | -0.00013552 | 0.0028741 | 0.0049102 | 0.0064696 | 0.0076174 | 0.0085232 | 0.0091444 | 0.0099098 | 0.010401 | 0.010823 | 0.011144
| 0.15 | -0.00012752 | 0.0041723 | 0.0063241 | 0.0076711 | 0.0087304 | 0.0094152 | 0.0099896 | 0.010555 | 0.010926 | 0.011208 | 0.01146 |  | 0.15 | -0.00012752 | 0.0041723 | 0.0063241 | 0.0076711 | 0.0087304 | 0.0094152 | 0.0099896 | 0.010555 | 0.010926 | 0.011208 | 0.01146
| 0.2 | -0.0011078 | 0.0046225 | 0.0067872 | 0.0080219 | 0.009014 | 0.0097936 | 0.010417 | 0.010854 | 0.011177 | 0.011367 | 0.011556 |  | 0.2 | -0.0011078 | 0.0046225 | 0.0067872 | 0.0080219 | 0.009014 | 0.0097936 | 0.010417 | 0.010854 | 0.011177 | 0.011367 | 0.011556
| 0.25 | -0.0019085 | 0.0047474 | 0.0068641 | 0.0082698 | 0.0093396 | 0.010179 | 0.010766 | 0.011156 | 0.011389 | 0.0115 | 0.011555 |  | 0.25 | -0.0019085 | 0.0047474 | 0.0068641 | 0.0082698 | 0.0093396 | 0.010179 | 0.010766 | 0.011156 | 0.011389 | 0.0115 | 0.011555
| 0.3 | -0.0028964 | 0.0048697 | 0.0068312 | 0.0085759 | 0.0098314 | 0.010601 | 0.011033 | 0.011295 | 0.011421 | 0.011417 | 0.011437 |  | 0.3 | -0.0028964 | 0.0048697 | 0.0068312 | 0.0085759 | 0.0098314 | 0.010601 | 0.011033 | 0.011295 | 0.011421 | 0.011417 | 0.011437
| 0.35 | -0.0037646 | 0.0048345 | 0.0070819 | 0.0089914 | 0.0102 | 0.010852 | 0.011197 | 0.011349 | 0.011364 | 0.011374 | 0.011279 |  | 0.35 | -0.0037646 | 0.0048345 | 0.0070819 | 0.0089914 | 0.0102 | 0.010852 | 0.011197 | 0.011349 | 0.011364 | 0.011374 | 0.011279
| 0.4 | -0.0046612 | 0.004833 | 0.007457 | 0.0093637 | 0.010469 | 0.01105 | 0.011231 | 0.011318 | 0.011247 | 0.01114 | 0.01102 |  | 0.4 | -0.0046612 | 0.004833 | 0.007457 | 0.0093637 | 0.010469 | 0.01105 | 0.011231 | 0.011318 | 0.011247 | 0.01114 | 0.01102
| 0.45 | -0.0053407 | 0.0048164 | 0.007779 | 0.0096494 | 0.010689 | 0.011146 | 0.011205 | 0.011209 | 0.011041 | 0.010874 | 0.010768 |  | 0.45 | -0.0053407 | 0.0048164 | 0.007779 | 0.0096494 | 0.010689 | 0.011146 | 0.011205 | 0.011209 | 0.011041 | 0.010874 | 0.010768
| 0.5 | -0.0056984 | 0.0047809 | 0.0081029 | 0.0099151 | 0.010781 | 0.011108 | 0.011075 | 0.011032 | 0.010921 | 0.010602 | 0.010453 |  | 0.5 | -0.0056984 | 0.0047809 | 0.0081029 | 0.0099151 | 0.010781 | 0.011108 | 0.011075 | 0.011032 | 0.010921 | 0.010602 | 0.010453
| 0.55 | -0.0062064 | 0.0048012 | 0.0084172 | 0.010175 | 0.010859 | 0.010962 | 0.010981 | 0.010828 | 0.010625 | 0.010392 | 0.010216 |  | 0.55 | -0.0062064 | 0.0048012 | 0.0084172 | 0.010175 | 0.010859 | 0.010962 | 0.010981 | 0.010828 | 0.010625 | 0.010392 | 0.010216
| 0.6 | -0.0067427 | 0.0049165 | 0.0085995 | 0.010242 | 0.010885 | 0.010945 | 0.010857 | 0.01063 | 0.010407 | 0.010134 | 0.0099468 |  | 0.6 | -0.0067427 | 0.0049165 | 0.0085995 | 0.010242 | 0.010885 | 0.010945 | 0.010857 | 0.01063 | 0.010407 | 0.010134 | 0.0099468
| 0.65 | -0.0071206 | 0.005107 | 0.0088816 | 0.01041 | 0.010813 | 0.010819 | 0.010683 | 0.010475 | 0.010169 | 0.0099134 | 0.0096815 |  | 0.65 | -0.0071206 | 0.005107 | 0.0088816 | 0.01041 | 0.010813 | 0.010819 | 0.010683 | 0.010475 | 0.010169 | 0.0099134 | 0.0096815
| 0.7 | -0.0074494 | 0.0052172 | 0.0090916 | 0.010445 | 0.010717 | 0.010704 | 0.010504 | 0.010232 | 0.0099738 | 0.0097018 | 0.00944 |  | 0.7 | -0.0074494 | 0.0052172 | 0.0090916 | 0.010445 | 0.010717 | 0.010704 | 0.010504 | 0.010232 | 0.0099738 | 0.0097018 | 0.00944
| 0.75 | -0.0075628 | 0.0053608 | 0.009247 | 0.01048 | 0.010692 | 0.010588 | 0.010291 | 0.0099886 | 0.0096587 | 0.0094253 | 0.0092021 |  | 0.75 | -0.0075628 | 0.0053608 | 0.009247 | 0.01048 | 0.010692 | 0.010588 | 0.010291 | 0.0099886 | 0.0096587 | 0.0094253 | 0.0092021
| 0.8 | -0.0079048 | 0.0055481 | 0.0093878 | 0.010383 | 0.010538 | 0.010382 | 0.010149 | 0.0098764 | 0.0095023 | 0.0091654 | 0.0089237 |  | 0.8 | -0.0079048 | 0.0055481 | 0.0093878 | 0.010383 | 0.010538 | 0.010382 | 0.010149 | 0.0098764 | 0.0095023 | 0.0091654 | 0.0089237
| 0.85 | -0.008162 | 0.0057555 | 0.0095186 | 0.010372 | 0.010508 | 0.010253 | 0.0099406 | 0.0096187 | 0.0092749 | 0.0090482 | 0.008791 |  | 0.85 | -0.008162 | 0.0057555 | 0.0095186 | 0.010372 | 0.010508 | 0.010253 | 0.0099406 | 0.0096187 | 0.0092749 | 0.0090482 | 0.008791
| 0.9 | -0.0083437 | 0.0059877 | 0.009547 | 0.010401 | 0.010356 | 0.01007 | 0.0097221 | 0.0093788 | 0.0091145 | 0.0088002 | 0.0085412 |  | 0.9 | -0.0083437 | 0.0059877 | 0.009547 | 0.010401 | 0.010356 | 0.01007 | 0.0097221 | 0.0093788 | 0.0091145 | 0.0088002 | 0.0085412
| 0.95 | -0.0083803 | 0.0061117 | 0.009611 | 0.010322 | 0.010235 | 0.009967 | 0.0096005 | 0.0092562 | 0.0088916 | 0.0086434 | 0.0083843 |  | 0.95 | -0.0083803 | 0.0061117 | 0.009611 | 0.010322 | 0.010235 | 0.009967 | 0.0096005 | 0.0092562 | 0.0088916 | 0.0086434 | 0.0083843
| 1 | -0.0086689 | 0.0063409 | 0.0097141 | 0.010247 | 0.010106 | 0.0097295 | 0.0094422 | 0.0091039 | 0.008748 | 0.0085202 | 0.0082335 |  | 1 | -0.0086689 | 0.0063409 | 0.0097141 | 0.010247 | 0.010106 | 0.0097295 | 0.0094422 | 0.0091039 | 0.008748 | 0.0085202 | 0.0082335
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0010945 | 0.0012237 | 0.0013339 | 0.0014365 | 0.0015241 | 0.0016088 | 0.001704 | 0.0017611 | 0.0018136 | 0.0018514 | 0.0018776 |  | 0.05 | 0.0010945 | 0.0012237 | 0.0013339 | 0.0014365 | 0.0015241 | 0.0016088 | 0.001704 | 0.0017611 | 0.0018136 | 0.0018514 | 0.0018776
| 0.1 | 0.0012976 | 0.0015464 | 0.0016938 | 0.0017913 | 0.0018686 | 0.0019174 | 0.0019778 | 0.0020155 | 0.0020289 | 0.0020444 | 0.0020722 |  | 0.1 | 0.0012976 | 0.0015464 | 0.0016938 | 0.0017913 | 0.0018686 | 0.0019174 | 0.0019778 | 0.0020155 | 0.0020289 | 0.0020444 | 0.0020722
| 0.15 | 0.0012802 | 0.0016449 | 0.0018024 | 0.0018869 | 0.0019276 | 0.0019678 | 0.002004 | 0.0020105 | 0.0020253 | 0.0020317 | 0.0020334 |  | 0.15 | 0.0012802 | 0.0016449 | 0.0018024 | 0.0018869 | 0.0019276 | 0.0019678 | 0.002004 | 0.0020105 | 0.0020253 | 0.0020317 | 0.0020334
| 0.2 | 0.0011562 | 0.0016767 | 0.0018055 | 0.0018785 | 0.0019173 | 0.0019484 | 0.0019837 | 0.0019897 | 0.0019901 | 0.0019865 | 0.0019842 |  | 0.2 | 0.0011562 | 0.0016767 | 0.0018055 | 0.0018785 | 0.0019173 | 0.0019484 | 0.0019837 | 0.0019897 | 0.0019901 | 0.0019865 | 0.0019842
| 0.25 | 0.00099848 | 0.0016692 | 0.001805 | 0.0018517 | 0.0019057 | 0.0019381 | 0.0019664 | 0.0019553 | 0.0019555 | 0.0019426 | 0.0019241 |  | 0.25 | 0.00099848 | 0.0016692 | 0.001805 | 0.0018517 | 0.0019057 | 0.0019381 | 0.0019664 | 0.0019553 | 0.0019555 | 0.0019426 | 0.0019241
| 0.3 | 0.00088154 | 0.001626 | 0.0017652 | 0.0018436 | 0.001902 | 0.0019286 | 0.0019432 | 0.0019237 | 0.0019156 | 0.0018891 | 0.0018684 |  | 0.3 | 0.00088154 | 0.001626 | 0.0017652 | 0.0018436 | 0.001902 | 0.0019286 | 0.0019432 | 0.0019237 | 0.0019156 | 0.0018891 | 0.0018684
| 0.35 | 0.00079208 | 0.0016026 | 0.0017416 | 0.0018489 | 0.0019011 | 0.0019108 | 0.0019118 | 0.0018941 | 0.0018645 | 0.0018341 | 0.0018062 |  | 0.35 | 0.00079208 | 0.0016026 | 0.0017416 | 0.0018489 | 0.0019011 | 0.0019108 | 0.0019118 | 0.0018941 | 0.0018645 | 0.0018341 | 0.0018062
| 0.4 | 0.00070346 | 0.0015721 | 0.0017194 | 0.0018426 | 0.0018789 | 0.0018769 | 0.0018647 | 0.0018449 | 0.0018127 | 0.0017815 | 0.0017536 |  | 0.4 | 0.00070346 | 0.0015721 | 0.0017194 | 0.0018426 | 0.0018789 | 0.0018769 | 0.0018647 | 0.0018449 | 0.0018127 | 0.0017815 | 0.0017536
| 0.45 | 0.00063203 | 0.0015515 | 0.0017145 | 0.0018292 | 0.0018626 | 0.0018505 | 0.0018223 | 0.0018001 | 0.0017592 | 0.0017228 | 0.0016915 |  | 0.45 | 0.00063203 | 0.0015515 | 0.0017145 | 0.0018292 | 0.0018626 | 0.0018505 | 0.0018223 | 0.0018001 | 0.0017592 | 0.0017228 | 0.0016915
| 0.5 | 0.00054664 | 0.0015292 | 0.0017146 | 0.0018268 | 0.0018406 | 0.0018207 | 0.001791 | 0.0017482 | 0.0017023 | 0.0016751 | 0.0016275 |  | 0.5 | 0.00054664 | 0.0015292 | 0.0017146 | 0.0018268 | 0.0018406 | 0.0018207 | 0.001791 | 0.0017482 | 0.0017023 | 0.0016751 | 0.0016275
| 0.55 | 0.00051702 | 0.001508 | 0.0017229 | 0.0018014 | 0.0018174 | 0.0017845 | 0.0017492 | 0.0017112 | 0.0016659 | 0.0016216 | 0.0015872 |  | 0.55 | 0.00051702 | 0.001508 | 0.0017229 | 0.0018014 | 0.0018174 | 0.0017845 | 0.0017492 | 0.0017112 | 0.0016659 | 0.0016216 | 0.0015872
| 0.6 | 0.00046545 | 0.0014843 | 0.0017191 | 0.0017908 | 0.0017928 | 0.001751 | 0.0017135 | 0.0016685 | 0.0016165 | 0.0015816 | 0.0015406 |  | 0.6 | 0.00046545 | 0.0014843 | 0.0017191 | 0.0017908 | 0.0017928 | 0.001751 | 0.0017135 | 0.0016685 | 0.0016165 | 0.0015816 | 0.0015406
| 0.65 | 0.00042737 | 0.0014747 | 0.0017165 | 0.0017698 | 0.0017632 | 0.0017215 | 0.0016745 | 0.0016255 | 0.0015784 | 0.0015312 | 0.0014902 |  | 0.65 | 0.00042737 | 0.0014747 | 0.0017165 | 0.0017698 | 0.0017632 | 0.0017215 | 0.0016745 | 0.0016255 | 0.0015784 | 0.0015312 | 0.0014902
| 0.7 | 0.00039113 | 0.001473 | 0.0017068 | 0.0017488 | 0.0017353 | 0.001686 | 0.001633 | 0.0015779 | 0.0015315 | 0.0014876 | 0.001447 |  | 0.7 | 0.00039113 | 0.001473 | 0.0017068 | 0.0017488 | 0.0017353 | 0.001686 | 0.001633 | 0.0015779 | 0.0015315 | 0.0014876 | 0.001447
| 0.75 | 0.00036346 | 0.0014654 | 0.0017069 | 0.0017391 | 0.0017031 | 0.0016542 | 0.0016023 | 0.0015496 | 0.0015058 | 0.0014557 | 0.0014213 |  | 0.75 | 0.00036346 | 0.0014654 | 0.0017069 | 0.0017391 | 0.0017031 | 0.0016542 | 0.0016023 | 0.0015496 | 0.0015058 | 0.0014557 | 0.0014213
| 0.8 | 0.00033499 | 0.0014633 | 0.0016893 | 0.0017156 | 0.0016773 | 0.0016261 | 0.0015626 | 0.0015102 | 0.0014617 | 0.001421 | 0.0013791 |  | 0.8 | 0.00033499 | 0.0014633 | 0.0016893 | 0.0017156 | 0.0016773 | 0.0016261 | 0.0015626 | 0.0015102 | 0.0014617 | 0.001421 | 0.0013791
| 0.85 | 0.00031105 | 0.0014641 | 0.0016854 | 0.0016961 | 0.0016477 | 0.0015959 | 0.0015294 | 0.0014775 | 0.0014245 | 0.0013886 | 0.001352 |  | 0.85 | 0.00031105 | 0.0014641 | 0.0016854 | 0.0016961 | 0.0016477 | 0.0015959 | 0.0015294 | 0.0014775 | 0.0014245 | 0.0013886 | 0.001352
| 0.9 | 0.00030965 | 0.0014613 | 0.0016763 | 0.0016729 | 0.0016171 | 0.0015602 | 0.0014966 | 0.0014449 | 0.0013962 | 0.0013598 | 0.0013194 |  | 0.9 | 0.00030965 | 0.0014613 | 0.0016763 | 0.0016729 | 0.0016171 | 0.0015602 | 0.0014966 | 0.0014449 | 0.0013962 | 0.0013598 | 0.0013194
| 0.95 | 0.00028898 | 0.0014639 | 0.0016566 | 0.0016471 | 0.0015893 | 0.0015273 | 0.001467 | 0.0014149 | 0.0013719 | 0.0013258 | 0.0012928 |  | 0.95 | 0.00028898 | 0.0014639 | 0.0016566 | 0.0016471 | 0.0015893 | 0.0015273 | 0.001467 | 0.0014149 | 0.0013719 | 0.0013258 | 0.0012928
| 1 | 0.00025023 | 0.0014643 | 0.0016458 | 0.0016295 | 0.0015624 | 0.0014986 | 0.0014482 | 0.0013892 | 0.001341 | 0.0013053 | 0.0012635 |  | 1 | 0.00025023 | 0.0014643 | 0.0016458 | 0.0016295 | 0.0015624 | 0.0014986 | 0.0014482 | 0.0013892 | 0.001341 | 0.0013053 | 0.0012635
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | [12 empty] | 0 | 0.99895 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 0 to 1
| 0.05 | 1.4044 | 1.5599 | 1.6875 | 1.7931 | 1.882 | 1.9572 | 2.0199 | 2.0661 | 2.1127 | 2.1363 | 2.1686 |  | 0.05 | 1.4044 | 1.5599 | 1.6875 | 1.7931 | 1.882 | 1.9572 | 2.0199 | 2.0661 | 2.1127 | 2.1363 | 2.1686
| 0.1 | 1.4522 | 1.8093 | 2.0854 | 2.2996 | 2.4703 | 2.6085 | 2.7135 | 2.8047 | 2.8896 | 2.9369 | 2.987 |  | 0.1 | 1.4522 | 1.8093 | 2.0854 | 2.2996 | 2.4703 | 2.6085 | 2.7135 | 2.8047 | 2.8896 | 2.9369 | 2.987
| 0.15 | 1.4211 | 1.9837 | 2.3978 | 2.7126 | 2.9722 | 3.1645 | 3.2974 | 3.4346 | 3.522 | 3.587 | 3.6343 |  | 0.15 | 1.4211 | 1.9837 | 2.3978 | 2.7126 | 2.9722 | 3.1645 | 3.2974 | 3.4346 | 3.522 | 3.587 | 3.6343
| 0.2 | 1.3767 | 2.1357 | 2.6885 | 3.0776 | 3.3829 | 3.6337 | 3.7939 | 4.0023 | 4.0711 | 4.1574 | 4.2215 |  | 0.2 | 1.3767 | 2.1357 | 2.6885 | 3.0776 | 3.3829 | 3.6337 | 3.7939 | 4.0023 | 4.0711 | 4.1574 | 4.2215
| 0.25 | 1.3425 | 2.276 | 2.9304 | 3.4358 | 3.8111 | 4.0926 | 4.2431 | 4.4409 | 4.5824 | 4.651 | 4.6613 |  | 0.25 | 1.3425 | 2.276 | 2.9304 | 3.4358 | 3.8111 | 4.0926 | 4.2431 | 4.4409 | 4.5824 | 4.651 | 4.6613
| 0.3 | 1.3076 | 2.4173 | 3.1867 | 3.719 | 4.123 | 4.4643 | 4.6946 | 4.8139 | 4.9676 | 5.0458 | 5.1087 |  | 0.3 | 1.3076 | 2.4173 | 3.1867 | 3.719 | 4.123 | 4.4643 | 4.6946 | 4.8139 | 4.9676 | 5.0458 | 5.1087
| 0.35 | 1.2781 | 2.5576 | 3.4067 | 4.0355 | 4.3741 | 4.7572 | 4.9932 | 5.1914 | 5.3577 | 5.467 | 5.5553 |  | 0.35 | 1.2781 | 2.5576 | 3.4067 | 4.0355 | 4.3741 | 4.7572 | 4.9932 | 5.1914 | 5.3577 | 5.467 | 5.5553
| 0.4 | 1.2534 | 2.6694 | 3.6615 | 4.2604 | 4.707 | 5.091 | 5.3458 | 5.5649 | 5.729 | 5.8411 | 5.9292 |  | 0.4 | 1.2534 | 2.6694 | 3.6615 | 4.2604 | 4.707 | 5.091 | 5.3458 | 5.5649 | 5.729 | 5.8411 | 5.9292
| 0.45 | 1.2397 | 2.8062 | 3.8711 | 4.5053 | 4.9982 | 5.3961 | 5.6805 | 5.8928 | 6.0766 | 6.1745 | 6.2962 |  | 0.45 | 1.2397 | 2.8062 | 3.8711 | 4.5053 | 4.9982 | 5.3961 | 5.6805 | 5.8928 | 6.0766 | 6.1745 | 6.2962
| 0.5 | 1.2229 | 2.9375 | 4.0137 | 4.7501 | 5.2758 | 5.6829 | 5.9772 | 6.2126 | 6.3933 | 6.5191 | 6.6343 |  | 0.5 | 1.2229 | 2.9375 | 4.0137 | 4.7501 | 5.2758 | 5.6829 | 5.9772 | 6.2126 | 6.3933 | 6.5191 | 6.6343
| 0.55 | 1.2071 | 3.0336 | 4.1723 | 4.9704 | 5.5434 | 5.9638 | 6.2711 | 6.5212 | 6.7012 | 6.8253 | 6.9447 |  | 0.55 | 1.2071 | 3.0336 | 4.1723 | 4.9704 | 5.5434 | 5.9638 | 6.2711 | 6.5212 | 6.7012 | 6.8253 | 6.9447
| 0.6 | 1.1934 | 3.147 | 4.3472 | 5.1974 | 5.7809 | 6.2212 | 6.5429 | 6.8037 | 6.9898 | 7.1423 | 7.2489 |  | 0.6 | 1.1934 | 3.147 | 4.3472 | 5.1974 | 5.7809 | 6.2212 | 6.5429 | 6.8037 | 6.9898 | 7.1423 | 7.2489
| 0.65 | 1.1883 | 3.2559 | 4.5265 | 5.393 | 5.9976 | 6.4639 | 6.807 | 7.0743 | 7.2791 | 7.4169 | 7.5412 |  | 0.65 | 1.1883 | 3.2559 | 4.5265 | 5.393 | 5.9976 | 6.4639 | 6.807 | 7.0743 | 7.2791 | 7.4169 | 7.5412
| 0.7 | 1.1784 | 3.3648 | 4.7078 | 5.5815 | 6.221 | 6.6847 | 7.0544 | 7.3317 | 7.5517 | 7.7035 | 7.8334 |  | 0.7 | 1.1784 | 3.3648 | 4.7078 | 5.5815 | 6.221 | 6.6847 | 7.0544 | 7.3317 | 7.5517 | 7.7035 | 7.8334
| 0.75 | 1.1686 | 3.4699 | 4.86 | 5.7719 | 6.343 | 6.9328 | 7.3029 | 7.5894 | 7.8072 | 7.9709 | 8.1025 |  | 0.75 | 1.1686 | 3.4699 | 4.86 | 5.7719 | 6.343 | 6.9328 | 7.3029 | 7.5894 | 7.8072 | 7.9709 | 8.1025
| 0.8 | 1.161 | 3.5792 | 5.0091 | 5.955 | 6.6384 | 7.1496 | 7.5301 | 7.832 | 8.0638 | 8.2278 | 8.3602 |  | 0.8 | 1.161 | 3.5792 | 5.0091 | 5.955 | 6.6384 | 7.1496 | 7.5301 | 7.832 | 8.0638 | 8.2278 | 8.3602
| 0.85 | 1.1594 | 3.6775 | 5.1533 | 6.1309 | 6.8322 | 7.3598 | 7.7626 | 8.0621 | 8.311 | 8.4844 | 8.6135 |  | 0.85 | 1.1594 | 3.6775 | 5.1533 | 6.1309 | 6.8322 | 7.3598 | 7.7626 | 8.0621 | 8.311 | 8.4844 | 8.6135
| 0.9 | 1.1517 | 3.7757 | 5.2818 | 6.2896 | 7.0303 | 7.5659 | 7.9786 | 8.2959 | 8.5436 | 8.7276 | 8.8636 |  | 0.9 | 1.1517 | 3.7757 | 5.2818 | 6.2896 | 7.0303 | 7.5659 | 7.9786 | 8.2959 | 8.5436 | 8.7276 | 8.8636
| 0.95 | 1.1438 | 3.8694 | 5.4234 | 6.4642 | 7.2084 | 7.7743 | 8.1942 | 8.5232 | 8.7682 | 8.965 | 9.1065 |  | 0.95 | 1.1438 | 3.8694 | 5.4234 | 6.4642 | 7.2084 | 7.7743 | 8.1942 | 8.5232 | 8.7682 | 8.965 | 9.1065
| 1 | 1.1382 | 3.8653 | 5.5639 | 6.6249 | 7.3961 | 7.9701 | 8.401 | 8.7396 | 8.9994 | 9.1939 | 9.3411 |  | 1 | 1.1382 | 3.8653 | 5.5639 | 6.6249 | 7.3961 | 7.9701 | 8.401 | 8.7396 | 8.9994 | 9.1939 | 9.3411
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0012522 | -0.00012407 | 0.0012379 | 0.0029483 | 0.0047839 | 0.0065812 | 0.010021 | 0.011678 | 0.011523 | 0.012747 | 0.014075 |  | 0.05 | -0.0012522 | -0.00012407 | 0.0012379 | 0.0029483 | 0.0047839 | 0.0065812 | 0.010021 | 0.011678 | 0.011523 | 0.012747 | 0.014075
| 0.1 | 0.0046071 | 0.0071665 | 0.010329 | 0.01364 | 0.01622 | 0.019458 | 0.023411 | 0.024681 | 0.026876 | 0.030948 | 0.030647 |  | 0.1 | 0.0046071 | 0.0071665 | 0.010329 | 0.01364 | 0.01622 | 0.019458 | 0.023411 | 0.024681 | 0.026876 | 0.030948 | 0.030647
| 0.15 | 0.0051005 | 0.011617 | 0.016392 | 0.02297 | 0.025292 | 0.03169 | 0.034776 | 0.034789 | 0.039553 | 0.041746 | 0.042323 |  | 0.15 | 0.0051005 | 0.011617 | 0.016392 | 0.02297 | 0.025292 | 0.03169 | 0.034776 | 0.034789 | 0.039553 | 0.041746 | 0.042323
| 0.2 | 0.0045028 | 0.013931 | 0.023033 | 0.031684 | 0.033421 | 0.041108 | 0.04402 | 0.045747 | 0.051247 | 0.053267 | 0.05306 |  | 0.2 | 0.0045028 | 0.013931 | 0.023033 | 0.031684 | 0.033421 | 0.041108 | 0.04402 | 0.045747 | 0.051247 | 0.053267 | 0.05306
| 0.25 | -4.2346e-05 | 0.017103 | 0.029356 | 0.037545 | 0.041551 | 0.050526 | 0.055065 | 0.056704 | 0.062941 | 0.064787 | 0.065673 |  | 0.25 | -4.2346e-05 | 0.017103 | 0.029356 | 0.037545 | 0.041551 | 0.050526 | 0.055065 | 0.056704 | 0.062941 | 0.064787 | 0.065673
| 0.3 | -0.0022571 | 0.016269 | 0.03373 | 0.043405 | 0.04968 | 0.059944 | 0.066386 | 0.067662 | 0.074635 | 0.076307 | 0.0775 |  | 0.3 | -0.0022571 | 0.016269 | 0.03373 | 0.043405 | 0.04968 | 0.059944 | 0.066386 | 0.067662 | 0.074635 | 0.076307 | 0.0775
| 0.35 | -0.0044227 | 0.017206 | 0.038105 | 0.049266 | 0.05781 | 0.069362 | 0.077706 | 0.078619 | 0.086329 | 0.087828 | 0.089326 |  | 0.35 | -0.0044227 | 0.017206 | 0.038105 | 0.049266 | 0.05781 | 0.069362 | 0.077706 | 0.078619 | 0.086329 | 0.087828 | 0.089326
| 0.4 | -0.0046357 | 0.023513 | 0.04248 | 0.055126 | 0.065939 | 0.07878 | 0.088246 | 0.089577 | 0.098024 | 0.099348 | 0.10115 |  | 0.4 | -0.0046357 | 0.023513 | 0.04248 | 0.055126 | 0.065939 | 0.07878 | 0.088246 | 0.089577 | 0.098024 | 0.099348 | 0.10115
| 0.45 | -0.006776 | 0.024454 | 0.046855 | 0.060987 | 0.074069 | 0.088198 | 0.098785 | 0.10053 | 0.10859 | 0.11087 | 0.11298 |  | 0.45 | -0.006776 | 0.024454 | 0.046855 | 0.060987 | 0.074069 | 0.088198 | 0.098785 | 0.10053 | 0.10859 | 0.11087 | 0.11298
| 0.5 | -0.0093046 | 0.025395 | 0.051229 | 0.066848 | 0.082198 | 0.099413 | 0.10703 | 0.11149 | 0.11291 | 0.11429 | 0.11772 |  | 0.5 | -0.0093046 | 0.025395 | 0.051229 | 0.066848 | 0.082198 | 0.099413 | 0.10703 | 0.11149 | 0.11291 | 0.11429 | 0.11772
| 0.55 | -0.011233 | 0.026336 | 0.055604 | 0.072708 | 0.090327 | 0.10723 | 0.11473 | 0.12203 | 0.12337 | 0.12409 | 0.12649 |  | 0.55 | -0.011233 | 0.026336 | 0.055604 | 0.072708 | 0.090327 | 0.10723 | 0.11473 | 0.12203 | 0.12337 | 0.12409 | 0.12649
| 0.6 | -0.010424 | 0.027278 | 0.059979 | 0.080453 | 0.10048 | 0.11368 | 0.12374 | 0.12787 | 0.12965 | 0.13388 | 0.13644 |  | 0.6 | -0.010424 | 0.027278 | 0.059979 | 0.080453 | 0.10048 | 0.11368 | 0.12374 | 0.12787 | 0.12965 | 0.13388 | 0.13644
| 0.65 | -0.01072 | 0.028219 | 0.063346 | 0.089848 | 0.1093 | 0.12045 | 0.12762 | 0.13406 | 0.13696 | 0.13848 | 0.14169 |  | 0.65 | -0.01072 | 0.028219 | 0.063346 | 0.089848 | 0.1093 | 0.12045 | 0.12762 | 0.13406 | 0.13696 | 0.13848 | 0.14169
| 0.7 | -0.011788 | 0.02916 | 0.069244 | 0.095835 | 0.11738 | 0.12524 | 0.1339 | 0.13922 | 0.14376 | 0.14469 | 0.148 |  | 0.7 | -0.011788 | 0.02916 | 0.069244 | 0.095835 | 0.11738 | 0.12524 | 0.1339 | 0.13922 | 0.14376 | 0.14469 | 0.148
| 0.75 | -0.0143 | 0.02639 | 0.072009 | 0.10227 | 0.12275 | 0.13589 | 0.14032 | 0.14558 | 0.1486 | 0.15049 | 0.15165 |  | 0.75 | -0.0143 | 0.02639 | 0.072009 | 0.10227 | 0.12275 | 0.13589 | 0.14032 | 0.14558 | 0.1486 | 0.15049 | 0.15165
| 0.8 | -0.013344 | 0.03025 | 0.077895 | 0.1087 | 0.12903 | 0.13812 | 0.14656 | 0.14988 | 0.15404 | 0.15629 | 0.15698 |  | 0.8 | -0.013344 | 0.03025 | 0.077895 | 0.1087 | 0.12903 | 0.13812 | 0.14656 | 0.14988 | 0.15404 | 0.15629 | 0.15698
| 0.85 | -0.014577 | 0.028235 | 0.083139 | 0.11391 | 0.13351 | 0.14281 | 0.15102 | 0.15604 | 0.15947 | 0.16342 | 0.16359 |  | 0.85 | -0.014577 | 0.028235 | 0.083139 | 0.11391 | 0.13351 | 0.14281 | 0.15102 | 0.15604 | 0.15947 | 0.16342 | 0.16359
| 0.9 | -0.014382 | 0.029444 | 0.090483 | 0.11939 | 0.13475 | 0.1472 | 0.15548 | 0.16016 | 0.16339 | 0.16775 | 0.17033 |  | 0.9 | -0.014382 | 0.029444 | 0.090483 | 0.11939 | 0.13475 | 0.1472 | 0.15548 | 0.16016 | 0.16339 | 0.16775 | 0.17033
| 0.95 | -0.01706 | 0.030654 | 0.094966 | 0.1241 | 0.13921 | 0.15218 | 0.16124 | 0.16744 | 0.16754 | 0.17234 | 0.17572 |  | 0.95 | -0.01706 | 0.030654 | 0.094966 | 0.1241 | 0.13921 | 0.15218 | 0.16124 | 0.16744 | 0.16754 | 0.17234 | 0.17572
| 1 | -0.015472 | 0.03406 | 0.10624 | 0.12962 | 0.14434 | 0.15587 | 0.16564 | 0.17116 | 0.17276 | 0.17795 | 0.17907 |  | 1 | -0.015472 | 0.03406 | 0.10624 | 0.12962 | 0.14434 | 0.15587 | 0.16564 | 0.17116 | 0.17276 | 0.17795 | 0.17907
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0007853 | -0.0021679 | -0.0032469 | -0.0041511 | -0.0048194 | -0.0053784 | -0.0059595 | -0.0063258 | -0.0066344 | -0.0067292 | -0.0066908 |  | 0.05 | -0.0007853 | -0.0021679 | -0.0032469 | -0.0041511 | -0.0048194 | -0.0053784 | -0.0059595 | -0.0063258 | -0.0066344 | -0.0067292 | -0.0066908
| 0.1 | 0.00020754 | -0.0027432 | -0.004737 | -0.0061672 | -0.0072531 | -0.0080794 | -0.0089495 | -0.0093583 | -0.0095464 | -0.010058 | -0.010218 |  | 0.1 | 0.00020754 | -0.0027432 | -0.004737 | -0.0061672 | -0.0072531 | -0.0080794 | -0.0089495 | -0.0093583 | -0.0095464 | -0.010058 | -0.010218
| 0.15 | 0.00068884 | -0.0032223 | -0.0058908 | -0.0079322 | -0.0095895 | -0.0099835 | -0.010955 | -0.011307 | -0.012364 | -0.013229 | -0.012479 |  | 0.15 | 0.00068884 | -0.0032223 | -0.0058908 | -0.0079322 | -0.0095895 | -0.0099835 | -0.010955 | -0.011307 | -0.012364 | -0.013229 | -0.012479
| 0.2 | 0.0011796 | -0.0040299 | -0.0072425 | -0.01047 | -0.011443 | -0.012145 | -0.012534 | -0.012797 | -0.013841 | -0.015272 | -0.014741 |  | 0.2 | 0.0011796 | -0.0040299 | -0.0072425 | -0.01047 | -0.011443 | -0.012145 | -0.012534 | -0.012797 | -0.013841 | -0.015272 | -0.014741
| 0.25 | 0.0014929 | -0.0046847 | -0.0088264 | -0.010956 | -0.012466 | -0.013111 | -0.014009 | -0.014288 | -0.015319 | -0.01629 | -0.017002 |  | 0.25 | 0.0014929 | -0.0046847 | -0.0088264 | -0.010956 | -0.012466 | -0.013111 | -0.014009 | -0.014288 | -0.015319 | -0.01629 | -0.017002
| 0.3 | 0.0016873 | -0.0052103 | -0.0095245 | -0.011771 | -0.013488 | -0.014077 | -0.015515 | -0.015778 | -0.016796 | -0.017308 | -0.01796 |  | 0.3 | 0.0016873 | -0.0052103 | -0.0095245 | -0.011771 | -0.013488 | -0.014077 | -0.015515 | -0.015778 | -0.016796 | -0.017308 | -0.01796
| 0.35 | 0.0014274 | -0.0059047 | -0.010311 | -0.012367 | -0.01393 | -0.015044 | -0.016869 | -0.017269 | -0.017785 | -0.018325 | -0.018918 |  | 0.35 | 0.0014274 | -0.0059047 | -0.010311 | -0.012367 | -0.01393 | -0.015044 | -0.016869 | -0.017269 | -0.017785 | -0.018325 | -0.018918
| 0.4 | 0.0015382 | -0.0065079 | -0.011097 | -0.012963 | -0.014371 | -0.016091 | -0.01767 | -0.018236 | -0.018748 | -0.019074 | -0.019159 |  | 0.4 | 0.0015382 | -0.0065079 | -0.011097 | -0.012963 | -0.014371 | -0.016091 | -0.01767 | -0.018236 | -0.018748 | -0.019074 | -0.019159
| 0.45 | 0.0015196 | -0.007437 | -0.01184 | -0.013559 | -0.015337 | -0.016966 | -0.018471 | -0.019217 | -0.019592 | -0.019964 | -0.020327 |  | 0.45 | 0.0015196 | -0.007437 | -0.01184 | -0.013559 | -0.015337 | -0.016966 | -0.018471 | -0.019217 | -0.019592 | -0.019964 | -0.020327
| 0.5 | 0.0017675 | -0.008075 | -0.012443 | -0.014155 | -0.016302 | -0.017771 | -0.019221 | -0.020134 | -0.02043 | -0.021026 | -0.021078 |  | 0.5 | 0.0017675 | -0.008075 | -0.012443 | -0.014155 | -0.016302 | -0.017771 | -0.019221 | -0.020134 | -0.02043 | -0.021026 | -0.021078
| 0.55 | 0.0015853 | -0.0080839 | -0.013052 | -0.014751 | -0.017595 | -0.018484 | -0.019608 | -0.020707 | -0.021509 | -0.021814 | -0.022042 |  | 0.55 | 0.0015853 | -0.0080839 | -0.013052 | -0.014751 | -0.017595 | -0.018484 | -0.019608 | -0.020707 | -0.021509 | -0.021814 | -0.022042
| 0.6 | 0.0015852 | -0.0084095 | -0.013661 | -0.01632 | -0.017818 | -0.019196 | -0.020342 | -0.021526 | -0.022075 | -0.022725 | -0.023126 |  | 0.6 | 0.0015852 | -0.0084095 | -0.013661 | -0.01632 | -0.017818 | -0.019196 | -0.020342 | -0.021526 | -0.022075 | -0.022725 | -0.023126
| 0.65 | 0.0016244 | -0.009106 | -0.014118 | -0.016513 | -0.018642 | -0.019817 | -0.02128 | -0.022164 | -0.023305 | -0.023333 | -0.024262 |  | 0.65 | 0.0016244 | -0.009106 | -0.014118 | -0.016513 | -0.018642 | -0.019817 | -0.02128 | -0.022164 | -0.023305 | -0.023333 | -0.024262
| 0.7 | 0.0016206 | -0.0098024 | -0.014501 | -0.016602 | -0.019075 | -0.020559 | -0.021856 | -0.023009 | -0.023901 | -0.024323 | -0.025162 |  | 0.7 | 0.0016206 | -0.0098024 | -0.014501 | -0.016602 | -0.019075 | -0.020559 | -0.021856 | -0.023009 | -0.023901 | -0.024323 | -0.025162
| 0.75 | 0.0016187 | -0.010224 | -0.014774 | -0.017915 | -0.019703 | -0.021154 | -0.022723 | -0.023741 | -0.024597 | -0.025404 | -0.025358 |  | 0.75 | 0.0016187 | -0.010224 | -0.014774 | -0.017915 | -0.019703 | -0.021154 | -0.022723 | -0.023741 | -0.024597 | -0.025404 | -0.025358
| 0.8 | 0.0016431 | -0.010277 | -0.015048 | -0.018118 | -0.020232 | -0.021764 | -0.02345 | -0.024548 | -0.025523 | -0.026145 | -0.02633 |  | 0.8 | 0.0016431 | -0.010277 | -0.015048 | -0.018118 | -0.020232 | -0.021764 | -0.02345 | -0.024548 | -0.025523 | -0.026145 | -0.02633
| 0.85 | 0.0015997 | -0.010329 | -0.01549 | -0.018901 | -0.020997 | -0.022372 | -0.024263 | -0.025157 | -0.026299 | -0.026995 | -0.027054 |  | 0.85 | 0.0015997 | -0.010329 | -0.01549 | -0.018901 | -0.020997 | -0.022372 | -0.024263 | -0.025157 | -0.026299 | -0.026995 | -0.027054
| 0.9 | 0.0014346 | -0.010588 | -0.015932 | -0.018944 | -0.021246 | -0.023142 | -0.024951 | -0.025992 | -0.027022 | -0.027609 | -0.028074 |  | 0.9 | 0.0014346 | -0.010588 | -0.015932 | -0.018944 | -0.021246 | -0.023142 | -0.024951 | -0.025992 | -0.027022 | -0.027609 | -0.028074
| 0.95 | 0.0014732 | -0.010847 | -0.016105 | -0.019455 | -0.021685 | -0.023788 | -0.025266 | -0.026721 | -0.027402 | -0.028213 | -0.02862 |  | 0.95 | 0.0014732 | -0.010847 | -0.016105 | -0.019455 | -0.021685 | -0.023788 | -0.025266 | -0.026721 | -0.027402 | -0.028213 | -0.02862
| 1 | 0.0016686 | -0.011106 | -0.016852 | -0.019879 | -0.022271 | -0.024387 | -0.026035 | -0.027425 | -0.028145 | -0.028741 | -0.029425 |  | 1 | 0.0016686 | -0.011106 | -0.016852 | -0.019879 | -0.022271 | -0.024387 | -0.026035 | -0.027425 | -0.028145 | -0.028741 | -0.029425
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## Intermediate calculations_LS< (hidden)
Class | 51-100 MVA
Rated voltage (kV) | 20
Symmetrical component of the rated system-source short-circuit breaking current (kA) | 50
Rated load breaking current (kA) | 5
Capacitance value per phase installed phase to earth at the generator-side of the generator circuit-breaker (µF) | 0.1
Capacitance value per phase installed phase to earth at the transformer-side of the generator circuit-breaker (µF) | 0.1
Load current breaking
Peak value of the standard TRV modified by the capacitors of the generator circuit-breaker (kV) | 22.4844
Rate of rise of the standard TRV modified by the capacitors of the generator circuit-breaker (kV/µs) | 0.57177
Time delay of the standard TRV modified by the capacitors of the generator circuit-breaker (µs) | 4.5154
Cs | 0.1
Cst | 0.05
Csb | 0.1
Cg/Cs | 1
Cg/Csl | 0.9
Cg/Csr | 1
U_ref | 15.79
Isc_ref | 51.89
KE2 | 1.1242
RRRV0 | 0.52707
𝐾_(𝑅𝑅𝑅𝑉−𝑈) | 0.012362
𝐾_(𝑅𝑅𝑅𝑉−I) | 0.0038881
td0 | 4.1103
𝐾_(𝑡𝑑−𝑈) | 0.077295
𝐾_(𝑡𝑑−𝐼) | -0.042148
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
U_ref | 14.51 | 15.79 | 18.05 | 21.52 | 23.83 | 25.25 | 26.1 | 26.54
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
Isc_ref | 44.72 | 51.89 | 65.87 | 92.41 | 117.04 | 139.76 | 160.6 | 179.47
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
KE2avrg | 1.1261 | 1.1242 | 1.1174 | 1.0934 | 1.0961 | 1.0654 | 1.0784 | 1.0528
KE2tl | 1.1161 | 1.11 | 1.1006 | 1.0559 | 1.0567 | 1.0184 | 1.0411 | 1.0002
KE2tr | 1.1055 | 1.1002 | 1.0915 | 1.0509 | 1.052 | 1.0146 | 1.0378 | 0.99688
KE2bl | 1.1392 | 1.1369 | 1.1279 | 1.1038 | 1.1049 | 1.0724 | 1.0852 | 1.0594
KE2br | 1.1261 | 1.1242 | 1.1174 | 1.0934 | 1.0961 | 1.0654 | 1.0784 | 1.0528
KE2lm | 1.1392 | 1.1369 | 1.1279 | 1.1038 | 1.1049 | 1.0724 | 1.0852 | 1.0594
KE2rm | 1.1261 | 1.1242 | 1.1174 | 1.0934 | 1.0961 | 1.0654 | 1.0784 | 1.0528
KE2tm | 1.1055 | 1.1002 | 1.0915 | 1.0509 | 1.052 | 1.0146 | 1.0378 | 0.99688
KE2bm | 1.1261 | 1.1242 | 1.1174 | 1.0934 | 1.0961 | 1.0654 | 1.0784 | 1.0528
KE2 | 1.1261 | 1.1242 | 1.1174 | 1.0934 | 1.0961 | 1.0654 | 1.0784 | 1.0528
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
RRRV0avrg | 0.47032 | 0.52707 | 0.64322 | 0.76259 | 0.90196 | 0.94953 | 1.0683 | 1.0872
RRRV0tl | 0.61035 | 0.6822 | 0.83896 | 0.95022 | 1.1255 | 1.1565 | 1.3119 | 1.3141
RRRV0tr | 0.59727 | 0.66756 | 0.81983 | 0.93436 | 1.1063 | 1.1408 | 1.2915 | 1.2965
RRRV0bl | 0.48332 | 0.54168 | 0.66201 | 0.7803 | 0.923 | 0.96841 | 1.0914 | 1.1083
RRRV0br | 0.47032 | 0.52707 | 0.64322 | 0.76259 | 0.90196 | 0.94953 | 1.0683 | 1.0872
RRRV0lm | 0.48332 | 0.54168 | 0.66201 | 0.7803 | 0.923 | 0.96841 | 1.0914 | 1.1083
RRRV0rm | 0.47032 | 0.52707 | 0.64322 | 0.76259 | 0.90196 | 0.94953 | 1.0683 | 1.0872
RRRV0tm | 0.59727 | 0.66756 | 0.81983 | 0.93436 | 1.1063 | 1.1408 | 1.2915 | 1.2965
RRRV0bm | 0.47032 | 0.52707 | 0.64322 | 0.76259 | 0.90196 | 0.94953 | 1.0683 | 1.0872
RRRV0 | 0.47032 | 0.52707 | 0.64322 | 0.76259 | 0.90196 | 0.94953 | 1.0683 | 1.0872
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑅𝑅𝑅𝑉−𝑈)avrg | 0.012787 | 0.012362 | 0.013831 | 0.01104 | 0.012221 | 0.0085427 | 0.011144 | 0.01219
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tl | 0.013035 | 0.013162 | 0.015013 | 0.0098101 | 0.011607 | 0.0055883 | 0.008047 | 0.010346
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tr | 0.013209 | 0.013152 | 0.014994 | 0.010136 | 0.011825 | 0.0061953 | 0.0086098 | 0.010672
𝐾_(𝑅𝑅𝑅𝑉−𝑈)bl | 0.012781 | 0.012426 | 0.013993 | 0.010834 | 0.012137 | 0.0081363 | 0.010823 | 0.011983
𝐾_(𝑅𝑅𝑅𝑉−𝑈)br | 0.012787 | 0.012362 | 0.013831 | 0.01104 | 0.012221 | 0.0085427 | 0.011144 | 0.01219
𝐾_(𝑅𝑅𝑅𝑉−𝑈)lm | 0.012781 | 0.012426 | 0.013993 | 0.010834 | 0.012137 | 0.0081363 | 0.010823 | 0.011983
𝐾_(𝑅𝑅𝑅𝑉−𝑈)rm | 0.012787 | 0.012362 | 0.013831 | 0.01104 | 0.012221 | 0.0085427 | 0.011144 | 0.01219
𝐾_(𝑅𝑅𝑅𝑉−𝑈)tm | 0.013209 | 0.013152 | 0.014994 | 0.010136 | 0.011825 | 0.0061953 | 0.0086098 | 0.010672
𝐾_(𝑅𝑅𝑅𝑉−𝑈)bm | 0.012787 | 0.012362 | 0.013831 | 0.01104 | 0.012221 | 0.0085427 | 0.011144 | 0.01219
𝐾_(𝑅𝑅𝑅𝑉−𝑈) | 0.012787 | 0.012362 | 0.013831 | 0.01104 | 0.012221 | 0.0085427 | 0.011144 | 0.01219
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑅𝑅𝑅𝑉−I)avrg | 0.0041135 | 0.0038881 | 0.0038227 | 0.0027105 | 0.0025096 | 0.0021335 | 0.0020722 | 0.0017091
𝐾_(𝑅𝑅𝑅𝑉−I)tl | 0.0044755 | 0.0041724 | 0.004103 | 0.0025778 | 0.0024085 | 0.0019705 | 0.0018514 | 0.0014991
𝐾_(𝑅𝑅𝑅𝑉−I)tr | 0.0044826 | 0.0041868 | 0.0041138 | 0.0026242 | 0.0024517 | 0.0020054 | 0.0018776 | 0.0015219
𝐾_(𝑅𝑅𝑅𝑉−I)bl | 0.0041447 | 0.0039142 | 0.0038587 | 0.0027066 | 0.0025139 | 0.0021233 | 0.0020444 | 0.0016691
𝐾_(𝑅𝑅𝑅𝑉−I)br | 0.0041135 | 0.0038881 | 0.0038227 | 0.0027105 | 0.0025096 | 0.0021335 | 0.0020722 | 0.0017091
𝐾_(𝑅𝑅𝑅𝑉−I)lm | 0.0041447 | 0.0039142 | 0.0038587 | 0.0027066 | 0.0025139 | 0.0021233 | 0.0020444 | 0.0016691
𝐾_(𝑅𝑅𝑅𝑉−I)rm | 0.0041135 | 0.0038881 | 0.0038227 | 0.0027105 | 0.0025096 | 0.0021335 | 0.0020722 | 0.0017091
𝐾_(𝑅𝑅𝑅𝑉−I)tm | 0.0044826 | 0.0041868 | 0.0041138 | 0.0026242 | 0.0024517 | 0.0020054 | 0.0018776 | 0.0015219
𝐾_(𝑅𝑅𝑅𝑉−I)bm | 0.0041135 | 0.0038881 | 0.0038227 | 0.0027105 | 0.0025096 | 0.0021335 | 0.0020722 | 0.0017091
𝐾_(𝑅𝑅𝑅𝑉−I) | 0.0041135 | 0.0038881 | 0.0038227 | 0.0027105 | 0.0025096 | 0.0021335 | 0.0020722 | 0.0017091
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
td0avrg | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0tl | 3.0499 | 2.8845 | 2.836 | 2.5465 | 2.3448 | 2.1528 | 2.1363 | 1.9994
td0tr | 3.1037 | 2.9363 | 2.8853 | 2.5945 | 2.3831 | 2.1847 | 2.1686 | 2.0279
td0bl | 4.2742 | 4.0733 | 3.9446 | 3.5554 | 3.265 | 2.9922 | 2.9369 | 2.7457
td0br | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0lm | 4.2742 | 4.0733 | 3.9446 | 3.5554 | 3.265 | 2.9922 | 2.9369 | 2.7457
td0rm | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0tm | 3.1037 | 2.9363 | 2.8853 | 2.5945 | 2.3831 | 2.1847 | 2.1686 | 2.0279
td0bm | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
td0 | 4.3458 | 4.1103 | 4.0091 | 3.6386 | 3.3082 | 3.0506 | 2.987 | 2.7876
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑡𝑑−𝑈)avrg | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)tl | 0.053875 | 0.042893 | 0.03495 | 0.015041 | 0.019194 | 0.003071 | 0.012747 | 0.010194
𝐾_(𝑡𝑑−𝑈)tr | 0.059239 | 0.046612 | 0.037059 | 0.016065 | 0.021049 | 0.0050557 | 0.014075 | 0.010983
𝐾_(𝑡𝑑−𝑈)bl | 0.094002 | 0.076052 | 0.068783 | 0.036052 | 0.042832 | 0.016956 | 0.030948 | 0.022369
𝐾_(𝑡𝑑−𝑈)br | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)lm | 0.094002 | 0.076052 | 0.068783 | 0.036052 | 0.042832 | 0.016956 | 0.030948 | 0.022369
𝐾_(𝑡𝑑−𝑈)rm | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈)tm | 0.059239 | 0.046612 | 0.037059 | 0.016065 | 0.021049 | 0.0050557 | 0.014075 | 0.010983
𝐾_(𝑡𝑑−𝑈)bm | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
𝐾_(𝑡𝑑−𝑈) | 0.10012 | 0.077295 | 0.071744 | 0.036331 | 0.044057 | 0.021502 | 0.030647 | 0.026239
| 10-50 MVA | 51-100 MVA | 101-200 MVA | 201-400 MVA | 401-600 MVA | 601-800 MVA | 801-1000 MVA | ≥1001 MVA
𝐾_(𝑡𝑑−𝐼)avrg | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)tl | -0.037012 | -0.029125 | -0.020052 | -0.012582 | -0.0092115 | -0.0071505 | -0.0067292 | -0.0048972
𝐾_(𝑡𝑑−𝐼)tr | -0.037654 | -0.02932 | -0.020373 | -0.012842 | -0.0094223 | -0.0073457 | -0.0066908 | -0.0047844
𝐾_(𝑡𝑑−𝐼)bl | -0.053741 | -0.042351 | -0.029098 | -0.018636 | -0.014454 | -0.011197 | -0.010058 | -0.007383
𝐾_(𝑡𝑑−𝐼)br | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)lm | -0.053741 | -0.042351 | -0.029098 | -0.018636 | -0.014454 | -0.011197 | -0.010058 | -0.007383
𝐾_(𝑡𝑑−𝐼)rm | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼)tm | -0.037654 | -0.02932 | -0.020373 | -0.012842 | -0.0094223 | -0.0073457 | -0.0066908 | -0.0047844
𝐾_(𝑡𝑑−𝐼)bm | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713
𝐾_(𝑡𝑑−𝐼) | -0.054739 | -0.042148 | -0.029807 | -0.019036 | -0.014458 | -0.01109 | -0.010218 | -0.007713

## CLASS1_LS>= (hidden)
If Iload/Isc x 5.6569 ≥1 | [12 empty] | If Iload/Isc x 5.6569 <1
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 |  | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0329 | 1.0738 | 1.1063 | 1.1269 | 1.1374 | 1.1407 | 1.1389 | 1.1335 | 1.1257 | 1.1161 | 1.1055 |  | 0.05 | 1.0329 | 1.0738 | 1.1063 | 1.1269 | 1.1374 | 1.1407 | 1.1389 | 1.1335 | 1.1257 | 1.1161 | 1.1055
| 0.1 | 1.0354 | 1.0812 | 1.1265 | 1.1567 | 1.1699 | 1.1728 | 1.1692 | 1.1616 | 1.1512 | 1.1392 | 1.1261 |  | 0.1 | 1.0354 | 1.0812 | 1.1265 | 1.1567 | 1.1699 | 1.1728 | 1.1692 | 1.1616 | 1.1512 | 1.1392 | 1.1261
| 0.15 | 1.0183 | 1.0813 | 1.1314 | 1.1608 | 1.1767 | 1.1809 | 1.1781 | 1.1707 | 1.1604 | 1.1482 | 1.1347 |  | 0.15 | 1.0183 | 1.0813 | 1.1314 | 1.1608 | 1.1767 | 1.1809 | 1.1781 | 1.1707 | 1.1604 | 1.1482 | 1.1347
| 0.2 | 0.9968 | 1.0729 | 1.1334 | 1.164 | 1.1795 | 1.1859 | 1.1842 | 1.1773 | 1.167 | 1.1545 | 1.1407 |  | 0.2 | 0.9968 | 1.0729 | 1.1334 | 1.164 | 1.1795 | 1.1859 | 1.1842 | 1.1773 | 1.167 | 1.1545 | 1.1407
| 0.25 | 0.97215 | 1.0635 | 1.1315 | 1.1654 | 1.1825 | 1.1903 | 1.189 | 1.182 | 1.1714 | 1.1586 | 1.1444 |  | 0.25 | 0.97215 | 1.0635 | 1.1315 | 1.1654 | 1.1825 | 1.1903 | 1.189 | 1.182 | 1.1714 | 1.1586 | 1.1444
| 0.3 | 0.94782 | 1.0571 | 1.1286 | 1.1652 | 1.1854 | 1.1936 | 1.1923 | 1.185 | 1.1742 | 1.1612 | 1.1468 |  | 0.3 | 0.94782 | 1.0571 | 1.1286 | 1.1652 | 1.1854 | 1.1936 | 1.1923 | 1.185 | 1.1742 | 1.1612 | 1.1468
| 0.35 | 0.92522 | 1.0509 | 1.1254 | 1.1645 | 1.1876 | 1.1959 | 1.1944 | 1.1871 | 1.1763 | 1.1632 | 1.1487 |  | 0.35 | 0.92522 | 1.0509 | 1.1254 | 1.1645 | 1.1876 | 1.1959 | 1.1944 | 1.1871 | 1.1763 | 1.1632 | 1.1487
| 0.4 | 0.90479 | 1.0451 | 1.1224 | 1.1637 | 1.189 | 1.1974 | 1.196 | 1.1888 | 1.1779 | 1.1648 | 1.1503 |  | 0.4 | 0.90479 | 1.0451 | 1.1224 | 1.1637 | 1.189 | 1.1974 | 1.196 | 1.1888 | 1.1779 | 1.1648 | 1.1503
| 0.45 | 0.88654 | 1.0399 | 1.1196 | 1.1645 | 1.19 | 1.1986 | 1.1973 | 1.1902 | 1.1794 | 1.1663 | 1.1517 |  | 0.45 | 0.88654 | 1.0399 | 1.1196 | 1.1645 | 1.19 | 1.1986 | 1.1973 | 1.1902 | 1.1794 | 1.1663 | 1.1517
| 0.5 | 0.87032 | 1.0353 | 1.117 | 1.1649 | 1.1907 | 1.1996 | 1.1985 | 1.1915 | 1.1806 | 1.1674 | 1.1528 |  | 0.5 | 0.87032 | 1.0353 | 1.117 | 1.1649 | 1.1907 | 1.1996 | 1.1985 | 1.1915 | 1.1806 | 1.1674 | 1.1528
| 0.55 | 0.8559 | 1.0311 | 1.1152 | 1.1652 | 1.1913 | 1.2005 | 1.1996 | 1.1926 | 1.1817 | 1.1684 | 1.1537 |  | 0.55 | 0.8559 | 1.0311 | 1.1152 | 1.1652 | 1.1913 | 1.2005 | 1.1996 | 1.1926 | 1.1817 | 1.1684 | 1.1537
| 0.6 | 0.84306 | 1.0273 | 1.1135 | 1.1653 | 1.1919 | 1.2014 | 1.2006 | 1.1935 | 1.1826 | 1.1692 | 1.1545 |  | 0.6 | 0.84306 | 1.0273 | 1.1135 | 1.1653 | 1.1919 | 1.2014 | 1.2006 | 1.1935 | 1.1826 | 1.1692 | 1.1545
| 0.65 | 0.83158 | 1.0239 | 1.1121 | 1.1658 | 1.1925 | 1.2021 | 1.2014 | 1.1943 | 1.1833 | 1.17 | 1.1552 |  | 0.65 | 0.83158 | 1.0239 | 1.1121 | 1.1658 | 1.1925 | 1.2021 | 1.2014 | 1.1943 | 1.1833 | 1.17 | 1.1552
| 0.7 | 0.8213 | 1.0208 | 1.1113 | 1.1665 | 1.193 | 1.2028 | 1.202 | 1.1949 | 1.184 | 1.1706 | 1.156 |  | 0.7 | 0.8213 | 1.0208 | 1.1113 | 1.1665 | 1.193 | 1.2028 | 1.202 | 1.1949 | 1.184 | 1.1706 | 1.156
| 0.75 | 0.81204 | 1.018 | 1.1109 | 1.167 | 1.1936 | 1.2034 | 1.2026 | 1.1955 | 1.1846 | 1.1712 | 1.1568 |  | 0.75 | 0.81204 | 1.018 | 1.1109 | 1.167 | 1.1936 | 1.2034 | 1.2026 | 1.1955 | 1.1846 | 1.1712 | 1.1568
| 0.8 | 0.80367 | 1.0154 | 1.1108 | 1.1674 | 1.194 | 1.2039 | 1.2032 | 1.1961 | 1.1851 | 1.1717 | 1.1575 |  | 0.8 | 0.80367 | 1.0154 | 1.1108 | 1.1674 | 1.194 | 1.2039 | 1.2032 | 1.1961 | 1.1851 | 1.1717 | 1.1575
| 0.85 | 0.79609 | 1.013 | 1.1107 | 1.1677 | 1.1935 | 1.2043 | 1.2036 | 1.1966 | 1.1856 | 1.1722 | 1.1581 |  | 0.85 | 0.79609 | 1.013 | 1.1107 | 1.1677 | 1.1935 | 1.2043 | 1.2036 | 1.1966 | 1.1856 | 1.1722 | 1.1581
| 0.9 | 0.78918 | 1.0107 | 1.1108 | 1.1679 | 1.1934 | 1.2047 | 1.2041 | 1.1971 | 1.1861 | 1.1726 | 1.1586 |  | 0.9 | 0.78918 | 1.0107 | 1.1108 | 1.1679 | 1.1934 | 1.2047 | 1.2041 | 1.1971 | 1.1861 | 1.1726 | 1.1586
| 0.95 | 0.78287 | 1.0086 | 1.1108 | 1.168 | 1.1936 | 1.2051 | 1.2045 | 1.1975 | 1.1865 | 1.1731 | 1.1591 |  | 0.95 | 0.78287 | 1.0086 | 1.1108 | 1.168 | 1.1936 | 1.2051 | 1.2045 | 1.1975 | 1.1865 | 1.1731 | 1.1591
| 1 | 0.77709 | 1.0067 | 1.1108 | 1.168 | 1.1938 | 1.2055 | 1.2049 | 1.1979 | 1.1869 | 1.1737 | 1.1596 |  | 1 | 0.77709 | 1.0067 | 1.1108 | 1.168 | 1.1938 | 1.2055 | 1.2049 | 1.1979 | 1.1869 | 1.1737 | 1.1596
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 |  | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| 0.05 | 0.76334 | 0.74428 | 0.7251 | 0.70613 | 0.68805 | 0.67061 | 0.65447 | 0.63899 | 0.62421 | 0.61035 | 0.59727 |  | 0.05 | 0.76334 | 0.74428 | 0.7251 | 0.70613 | 0.68805 | 0.67061 | 0.65447 | 0.63899 | 0.62421 | 0.61035 | 0.59727
| 0.1 | 0.66964 | 0.63864 | 0.61161 | 0.58792 | 0.56659 | 0.54704 | 0.52919 | 0.51272 | 0.49743 | 0.48332 | 0.47032 |  | 0.1 | 0.66964 | 0.63864 | 0.61161 | 0.58792 | 0.56659 | 0.54704 | 0.52919 | 0.51272 | 0.49743 | 0.48332 | 0.47032
| 0.15 | 0.62175 | 0.57697 | 0.54565 | 0.52035 | 0.49793 | 0.47789 | 0.45987 | 0.44335 | 0.42836 | 0.41472 | 0.40243 |  | 0.15 | 0.62175 | 0.57697 | 0.54565 | 0.52035 | 0.49793 | 0.47789 | 0.45987 | 0.44335 | 0.42836 | 0.41472 | 0.40243
| 0.2 | 0.59384 | 0.53504 | 0.50092 | 0.47467 | 0.45151 | 0.43075 | 0.41266 | 0.39645 | 0.38181 | 0.36902 | 0.35722 |  | 0.2 | 0.59384 | 0.53504 | 0.50092 | 0.47467 | 0.45151 | 0.43075 | 0.41266 | 0.39645 | 0.38181 | 0.36902 | 0.35722
| 0.25 | 0.57525 | 0.50369 | 0.468 | 0.44005 | 0.41595 | 0.39511 | 0.37727 | 0.36145 | 0.34768 | 0.33534 | 0.32427 |  | 0.25 | 0.57525 | 0.50369 | 0.468 | 0.44005 | 0.41595 | 0.39511 | 0.37727 | 0.36145 | 0.34768 | 0.33534 | 0.32427
| 0.3 | 0.56257 | 0.47893 | 0.44174 | 0.41196 | 0.38744 | 0.36681 | 0.34935 | 0.33416 | 0.32103 | 0.30942 | 0.29891 |  | 0.3 | 0.56257 | 0.47893 | 0.44174 | 0.41196 | 0.38744 | 0.36681 | 0.34935 | 0.33416 | 0.32103 | 0.30942 | 0.29891
| 0.35 | 0.55284 | 0.45893 | 0.41935 | 0.3885 | 0.36376 | 0.34348 | 0.32677 | 0.31215 | 0.29968 | 0.28863 | 0.27875 |  | 0.35 | 0.55284 | 0.45893 | 0.41935 | 0.3885 | 0.36376 | 0.34348 | 0.32677 | 0.31215 | 0.29968 | 0.28863 | 0.27875
| 0.4 | 0.54576 | 0.44183 | 0.40017 | 0.36856 | 0.34382 | 0.32432 | 0.30797 | 0.29414 | 0.28199 | 0.27142 | 0.26211 |  | 0.4 | 0.54576 | 0.44183 | 0.40017 | 0.36856 | 0.34382 | 0.32432 | 0.30797 | 0.29414 | 0.28199 | 0.27142 | 0.26211
| 0.45 | 0.53982 | 0.42724 | 0.38327 | 0.35115 | 0.32685 | 0.30774 | 0.29199 | 0.27869 | 0.26711 | 0.257 | 0.24815 |  | 0.45 | 0.53982 | 0.42724 | 0.38327 | 0.35115 | 0.32685 | 0.30774 | 0.29199 | 0.27869 | 0.26711 | 0.257 | 0.24815
| 0.5 | 0.53528 | 0.41437 | 0.36838 | 0.33597 | 0.31206 | 0.29351 | 0.27836 | 0.26552 | 0.25457 | 0.24479 | 0.23631 |  | 0.5 | 0.53528 | 0.41437 | 0.36838 | 0.33597 | 0.31206 | 0.29351 | 0.27836 | 0.26552 | 0.25457 | 0.24479 | 0.23631
| 0.55 | 0.53122 | 0.40266 | 0.35468 | 0.32242 | 0.29917 | 0.28101 | 0.26641 | 0.2541 | 0.24355 | 0.23412 | 0.22589 |  | 0.55 | 0.53122 | 0.40266 | 0.35468 | 0.32242 | 0.29917 | 0.28101 | 0.26641 | 0.2541 | 0.24355 | 0.23412 | 0.22589
| 0.6 | 0.5282 | 0.39201 | 0.34255 | 0.31055 | 0.28767 | 0.27014 | 0.25603 | 0.24402 | 0.23373 | 0.22489 | 0.21701 |  | 0.6 | 0.5282 | 0.39201 | 0.34255 | 0.31055 | 0.28767 | 0.27014 | 0.25603 | 0.24402 | 0.23373 | 0.22489 | 0.21701
| 0.65 | 0.52525 | 0.38221 | 0.33157 | 0.2997 | 0.27741 | 0.26053 | 0.2466 | 0.23506 | 0.22511 | 0.21659 | 0.20893 |  | 0.65 | 0.52525 | 0.38221 | 0.33157 | 0.2997 | 0.27741 | 0.26053 | 0.2466 | 0.23506 | 0.22511 | 0.21659 | 0.20893
| 0.7 | 0.52304 | 0.37308 | 0.32144 | 0.29002 | 0.26822 | 0.25161 | 0.23827 | 0.22704 | 0.21755 | 0.20906 | 0.20174 |  | 0.7 | 0.52304 | 0.37308 | 0.32144 | 0.29002 | 0.26822 | 0.25161 | 0.23827 | 0.22704 | 0.21755 | 0.20906 | 0.20174
| 0.75 | 0.52082 | 0.36457 | 0.3122 | 0.28122 | 0.2599 | 0.24376 | 0.23081 | 0.21984 | 0.21053 | 0.20243 | 0.19526 |  | 0.75 | 0.52082 | 0.36457 | 0.3122 | 0.28122 | 0.2599 | 0.24376 | 0.23081 | 0.21984 | 0.21053 | 0.20243 | 0.19526
| 0.8 | 0.51916 | 0.35649 | 0.30365 | 0.27309 | 0.25227 | 0.23656 | 0.22399 | 0.21332 | 0.20423 | 0.19631 | 0.18934 |  | 0.8 | 0.51916 | 0.35649 | 0.30365 | 0.27309 | 0.25227 | 0.23656 | 0.22399 | 0.21332 | 0.20423 | 0.19631 | 0.18934
| 0.85 | 0.51773 | 0.34903 | 0.29579 | 0.26557 | 0.24523 | 0.23 | 0.21755 | 0.20731 | 0.19837 | 0.19067 | 0.18385 |  | 0.85 | 0.51773 | 0.34903 | 0.29579 | 0.26557 | 0.24523 | 0.23 | 0.21755 | 0.20731 | 0.19837 | 0.19067 | 0.18385
| 0.9 | 0.5161 | 0.34196 | 0.28843 | 0.25881 | 0.23892 | 0.22395 | 0.21188 | 0.20174 | 0.19312 | 0.18558 | 0.17893 |  | 0.9 | 0.5161 | 0.34196 | 0.28843 | 0.25881 | 0.23892 | 0.22395 | 0.21188 | 0.20174 | 0.19312 | 0.18558 | 0.17893
| 0.95 | 0.51497 | 0.33527 | 0.28174 | 0.25244 | 0.23303 | 0.21833 | 0.20648 | 0.19669 | 0.18827 | 0.18073 | 0.17438 |  | 0.95 | 0.51497 | 0.33527 | 0.28174 | 0.25244 | 0.23303 | 0.21833 | 0.20648 | 0.19669 | 0.18827 | 0.18073 | 0.17438
| 1 | 0.51367 | 0.32894 | 0.27549 | 0.24647 | 0.22759 | 0.21304 | 0.20143 | 0.19183 | 0.1836 | 0.17639 | 0.17009 |  | 1 | 0.51367 | 0.32894 | 0.27549 | 0.24647 | 0.22759 | 0.21304 | 0.20143 | 0.19183 | 0.1836 | 0.17639 | 0.17009
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0069224 | 0.0085033 | 0.0096294 | 0.010568 | 0.011228 | 0.011762 | 0.01222 | 0.012553 | 0.012834 | 0.013035 | 0.013209 |  | 0.05 | 0.0069224 | 0.0085033 | 0.0096294 | 0.010568 | 0.011228 | 0.011762 | 0.01222 | 0.012553 | 0.012834 | 0.013035 | 0.013209
| 0.1 | 0.0051644 | 0.0086385 | 0.010128 | 0.011097 | 0.011731 | 0.012235 | 0.012485 | 0.012677 | 0.012767 | 0.012781 | 0.012787 |  | 0.1 | 0.0051644 | 0.0086385 | 0.010128 | 0.011097 | 0.011731 | 0.012235 | 0.012485 | 0.012677 | 0.012767 | 0.012781 | 0.012787
| 0.15 | 0.0036516 | 0.0083819 | 0.010139 | 0.011287 | 0.011935 | 0.012241 | 0.0124 | 0.01236 | 0.012277 | 0.012195 | 0.012026 |  | 0.15 | 0.0036516 | 0.0083819 | 0.010139 | 0.011287 | 0.011935 | 0.012241 | 0.0124 | 0.01236 | 0.012277 | 0.012195 | 0.012026
| 0.2 | 0.0024349 | 0.0082894 | 0.010364 | 0.011465 | 0.011945 | 0.012048 | 0.012014 | 0.011875 | 0.011696 | 0.011495 | 0.011269 |  | 0.2 | 0.0024349 | 0.0082894 | 0.010364 | 0.011465 | 0.011945 | 0.012048 | 0.012014 | 0.011875 | 0.011696 | 0.011495 | 0.011269
| 0.25 | 0.0016624 | 0.0082036 | 0.010537 | 0.011451 | 0.011763 | 0.011743 | 0.011551 | 0.011312 | 0.01109 | 0.010806 | 0.01055 |  | 0.25 | 0.0016624 | 0.0082036 | 0.010537 | 0.011451 | 0.011763 | 0.011743 | 0.011551 | 0.011312 | 0.01109 | 0.010806 | 0.01055
| 0.3 | 0.0011181 | 0.0082927 | 0.010645 | 0.0114 | 0.011521 | 0.011311 | 0.011051 | 0.010785 | 0.010479 | 0.010166 | 0.0099376 |  | 0.3 | 0.0011181 | 0.0082927 | 0.010645 | 0.0114 | 0.011521 | 0.011311 | 0.011051 | 0.010785 | 0.010479 | 0.010166 | 0.0099376
| 0.35 | 0.00068611 | 0.0083923 | 0.010686 | 0.011255 | 0.011149 | 0.010937 | 0.010591 | 0.010247 | 0.0099393 | 0.0096599 | 0.0093893 |  | 0.35 | 0.00068611 | 0.0083923 | 0.010686 | 0.011255 | 0.011149 | 0.010937 | 0.010591 | 0.010247 | 0.0099393 | 0.0096599 | 0.0093893
| 0.4 | 0.00039338 | 0.008525 | 0.010688 | 0.011015 | 0.010805 | 0.010512 | 0.010128 | 0.0097689 | 0.0094773 | 0.0091609 | 0.0089065 |  | 0.4 | 0.00039338 | 0.008525 | 0.010688 | 0.011015 | 0.010805 | 0.010512 | 0.010128 | 0.0097689 | 0.0094773 | 0.0091609 | 0.0089065
| 0.45 | 0.00012233 | 0.0086479 | 0.010606 | 0.010777 | 0.010479 | 0.010095 | 0.0096985 | 0.0093539 | 0.0090641 | 0.0087786 | 0.0085107 |  | 0.45 | 0.00012233 | 0.0086479 | 0.010606 | 0.010777 | 0.010479 | 0.010095 | 0.0096985 | 0.0093539 | 0.0090641 | 0.0087786 | 0.0085107
| 0.5 | -0.00016091 | 0.0088021 | 0.01051 | 0.01055 | 0.010173 | 0.0097242 | 0.0093589 | 0.0089644 | 0.0086608 | 0.0083903 | 0.0081428 |  | 0.5 | -0.00016091 | 0.0088021 | 0.01051 | 0.01055 | 0.010173 | 0.0097242 | 0.0093589 | 0.0089644 | 0.0086608 | 0.0083903 | 0.0081428
| 0.55 | -0.00031908 | 0.0089061 | 0.010404 | 0.01027 | 0.0098535 | 0.0094124 | 0.009018 | 0.0086535 | 0.0083415 | 0.0080801 | 0.0078305 |  | 0.55 | -0.00031908 | 0.0089061 | 0.010404 | 0.01027 | 0.0098535 | 0.0094124 | 0.009018 | 0.0086535 | 0.0083415 | 0.0080801 | 0.0078305
| 0.6 | -0.00046553 | 0.0089835 | 0.010245 | 0.010029 | 0.0095448 | 0.0091066 | 0.0086888 | 0.0083763 | 0.0080544 | 0.007771 | 0.0075409 |  | 0.6 | -0.00046553 | 0.0089835 | 0.010245 | 0.010029 | 0.0095448 | 0.0091066 | 0.0086888 | 0.0083763 | 0.0080544 | 0.007771 | 0.0075409
| 0.65 | -0.00056326 | 0.0090553 | 0.010121 | 0.0097505 | 0.0092719 | 0.0088572 | 0.0084593 | 0.0080947 | 0.007794 | 0.0075092 | 0.0072835 |  | 0.65 | -0.00056326 | 0.0090553 | 0.010121 | 0.0097505 | 0.0092719 | 0.0088572 | 0.0084593 | 0.0080947 | 0.007794 | 0.0075092 | 0.0072835
| 0.7 | -0.00067764 | 0.0091 | 0.0099796 | 0.0095103 | 0.0090292 | 0.008556 | 0.0081781 | 0.0078457 | 0.0075865 | 0.0073136 | 0.0070479 |  | 0.7 | -0.00067764 | 0.0091 | 0.0099796 | 0.0095103 | 0.0090292 | 0.008556 | 0.0081781 | 0.0078457 | 0.0075865 | 0.0073136 | 0.0070479
| 0.75 | -0.00084461 | 0.0091301 | 0.0097784 | 0.0093102 | 0.0087954 | 0.0083611 | 0.0079713 | 0.007635 | 0.0073614 | 0.0070512 | 0.0068446 |  | 0.75 | -0.00084461 | 0.0091301 | 0.0097784 | 0.0093102 | 0.0087954 | 0.0083611 | 0.0079713 | 0.007635 | 0.0073614 | 0.0070512 | 0.0068446
| 0.8 | -0.00082804 | 0.0091587 | 0.0096287 | 0.0090984 | 0.008565 | 0.0081357 | 0.0077423 | 0.0074514 | 0.0071534 | 0.0068941 | 0.0066582 |  | 0.8 | -0.00082804 | 0.0091587 | 0.0096287 | 0.0090984 | 0.008565 | 0.0081357 | 0.0077423 | 0.0074514 | 0.0071534 | 0.0068941 | 0.0066582
| 0.85 | -0.00096933 | 0.009166 | 0.00946 | 0.0089147 | 0.0083587 | 0.0079452 | 0.007534 | 0.007237 | 0.0069334 | 0.0067083 | 0.0064658 |  | 0.85 | -0.00096933 | 0.009166 | 0.00946 | 0.0089147 | 0.0083587 | 0.0079452 | 0.007534 | 0.007237 | 0.0069334 | 0.0067083 | 0.0064658
| 0.9 | -0.00091761 | 0.0091322 | 0.0093135 | 0.0087096 | 0.0081833 | 0.0077641 | 0.0073842 | 0.0070617 | 0.0068073 | 0.0065399 | 0.0063043 |  | 0.9 | -0.00091761 | 0.0091322 | 0.0093135 | 0.0087096 | 0.0081833 | 0.0077641 | 0.0073842 | 0.0070617 | 0.0068073 | 0.0065399 | 0.0063043
| 0.95 | -0.0010692 | 0.009139 | 0.0091666 | 0.0085296 | 0.0080257 | 0.007588 | 0.0072332 | 0.006922 | 0.0066065 | 0.0063858 | 0.0061393 |  | 0.95 | -0.0010692 | 0.009139 | 0.0091666 | 0.0085296 | 0.0080257 | 0.007588 | 0.0072332 | 0.006922 | 0.0066065 | 0.0063858 | 0.0061393
| 1 | -0.0011146 | 0.0091075 | 0.0090096 | 0.0083585 | 0.0078746 | 0.0074312 | 0.0070819 | 0.006764 | 0.0064892 | 0.0062161 | 0.0059993 |  | 1 | -0.0011146 | 0.0091075 | 0.0090096 | 0.0083585 | 0.0078746 | 0.0074312 | 0.0070819 | 0.006764 | 0.0064892 | 0.0062161 | 0.0059993
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.003473 | 0.0037612 | 0.003969 | 0.0041179 | 0.004228 | 0.0043111 | 0.0043812 | 0.0044226 | 0.0044578 | 0.0044755 | 0.0044826 |  | 0.05 | 0.003473 | 0.0037612 | 0.003969 | 0.0041179 | 0.004228 | 0.0043111 | 0.0043812 | 0.0044226 | 0.0044578 | 0.0044755 | 0.0044826
| 0.1 | 0.0031136 | 0.0037934 | 0.0040139 | 0.004109 | 0.0041657 | 0.0041959 | 0.0042121 | 0.0042008 | 0.0041836 | 0.0041447 | 0.0041135 |  | 0.1 | 0.0031136 | 0.0037934 | 0.0040139 | 0.004109 | 0.0041657 | 0.0041959 | 0.0042121 | 0.0042008 | 0.0041836 | 0.0041447 | 0.0041135
| 0.15 | 0.0026153 | 0.0036397 | 0.0038419 | 0.0039461 | 0.0039971 | 0.0040141 | 0.0039981 | 0.0039596 | 0.0039041 | 0.0038523 | 0.0037885 |  | 0.15 | 0.0026153 | 0.0036397 | 0.0038419 | 0.0039461 | 0.0039971 | 0.0040141 | 0.0039981 | 0.0039596 | 0.0039041 | 0.0038523 | 0.0037885
| 0.2 | 0.0022211 | 0.0034787 | 0.0037108 | 0.0038345 | 0.003873 | 0.003854 | 0.003809 | 0.0037441 | 0.0036722 | 0.0035941 | 0.0035248 |  | 0.2 | 0.0022211 | 0.0034787 | 0.0037108 | 0.0038345 | 0.003873 | 0.003854 | 0.003809 | 0.0037441 | 0.0036722 | 0.0035941 | 0.0035248
| 0.25 | 0.0019355 | 0.0033575 | 0.003622 | 0.0037479 | 0.0037539 | 0.0037089 | 0.0036334 | 0.0035456 | 0.00346 | 0.0033752 | 0.0032928 |  | 0.25 | 0.0019355 | 0.0033575 | 0.003622 | 0.0037479 | 0.0037539 | 0.0037089 | 0.0036334 | 0.0035456 | 0.00346 | 0.0033752 | 0.0032928
| 0.3 | 0.0017241 | 0.0032611 | 0.0035653 | 0.0036635 | 0.0036365 | 0.0035573 | 0.0034633 | 0.0033655 | 0.0032704 | 0.0031795 | 0.0030932 |  | 0.3 | 0.0017241 | 0.0032611 | 0.0035653 | 0.0036635 | 0.0036365 | 0.0035573 | 0.0034633 | 0.0033655 | 0.0032704 | 0.0031795 | 0.0030932
| 0.35 | 0.0015384 | 0.0032003 | 0.0035163 | 0.0035754 | 0.0035114 | 0.0034136 | 0.0033073 | 0.0032016 | 0.0031031 | 0.0030108 | 0.0029238 |  | 0.35 | 0.0015384 | 0.0032003 | 0.0035163 | 0.0035754 | 0.0035114 | 0.0034136 | 0.0033073 | 0.0032016 | 0.0031031 | 0.0030108 | 0.0029238
| 0.4 | 0.0014095 | 0.0031474 | 0.0034702 | 0.0034875 | 0.003396 | 0.0032766 | 0.0031639 | 0.003055 | 0.0029541 | 0.0028612 | 0.0027764 |  | 0.4 | 0.0014095 | 0.0031474 | 0.0034702 | 0.0034875 | 0.003396 | 0.0032766 | 0.0031639 | 0.003055 | 0.0029541 | 0.0028612 | 0.0027764
| 0.45 | 0.0013046 | 0.0031186 | 0.0034167 | 0.0033915 | 0.0032831 | 0.0031554 | 0.0030336 | 0.0029211 | 0.0028229 | 0.0027325 | 0.0026465 |  | 0.45 | 0.0013046 | 0.0031186 | 0.0034167 | 0.0033915 | 0.0032831 | 0.0031554 | 0.0030336 | 0.0029211 | 0.0028229 | 0.0027325 | 0.0026465
| 0.5 | 0.0012107 | 0.0030979 | 0.0033637 | 0.0033019 | 0.0031758 | 0.0030382 | 0.0029194 | 0.0028014 | 0.0027083 | 0.0026169 | 0.0025335 |  | 0.5 | 0.0012107 | 0.0030979 | 0.0033637 | 0.0033019 | 0.0031758 | 0.0030382 | 0.0029194 | 0.0028014 | 0.0027083 | 0.0026169 | 0.0025335
| 0.55 | 0.0011399 | 0.0030811 | 0.0033067 | 0.0032183 | 0.0030729 | 0.0029347 | 0.0028111 | 0.0026986 | 0.0026014 | 0.002513 | 0.0024369 |  | 0.55 | 0.0011399 | 0.0030811 | 0.0033067 | 0.0032183 | 0.0030729 | 0.0029347 | 0.0028111 | 0.0026986 | 0.0026014 | 0.002513 | 0.0024369
| 0.6 | 0.0010819 | 0.0030673 | 0.0032519 | 0.0031337 | 0.0029814 | 0.002839 | 0.002717 | 0.0026083 | 0.0025086 | 0.0024235 | 0.002348 |  | 0.6 | 0.0010819 | 0.0030673 | 0.0032519 | 0.0031337 | 0.0029814 | 0.002839 | 0.002717 | 0.0026083 | 0.0025086 | 0.0024235 | 0.002348
| 0.65 | 0.0010125 | 0.0030559 | 0.0031933 | 0.0030536 | 0.0028955 | 0.002753 | 0.0026318 | 0.0025241 | 0.0024281 | 0.0023469 | 0.0022692 |  | 0.65 | 0.0010125 | 0.0030559 | 0.0031933 | 0.0030536 | 0.0028955 | 0.002753 | 0.0026318 | 0.0025241 | 0.0024281 | 0.0023469 | 0.0022692
| 0.7 | 0.00096843 | 0.0030442 | 0.0031356 | 0.0029794 | 0.0028149 | 0.0026717 | 0.0025518 | 0.0024459 | 0.0023565 | 0.0022721 | 0.0021979 |  | 0.7 | 0.00096843 | 0.0030442 | 0.0031356 | 0.0029794 | 0.0028149 | 0.0026717 | 0.0025518 | 0.0024459 | 0.0023565 | 0.0022721 | 0.0021979
| 0.75 | 0.00093297 | 0.0030278 | 0.0030746 | 0.0029068 | 0.0027404 | 0.0026022 | 0.0024781 | 0.0023752 | 0.0022847 | 0.0022056 | 0.0021334 |  | 0.75 | 0.00093297 | 0.0030278 | 0.0030746 | 0.0029068 | 0.0027404 | 0.0026022 | 0.0024781 | 0.0023752 | 0.0022847 | 0.0022056 | 0.0021334
| 0.8 | 0.00088981 | 0.003016 | 0.0030227 | 0.0028449 | 0.002672 | 0.0025316 | 0.0024134 | 0.0023121 | 0.0022227 | 0.0021459 | 0.0020744 |  | 0.8 | 0.00088981 | 0.003016 | 0.0030227 | 0.0028449 | 0.002672 | 0.0025316 | 0.0024134 | 0.0023121 | 0.0022227 | 0.0021459 | 0.0020744
| 0.85 | 0.00086379 | 0.0029977 | 0.0029688 | 0.0027759 | 0.002606 | 0.0024714 | 0.0023524 | 0.0022537 | 0.0021671 | 0.0020851 | 0.0020186 |  | 0.85 | 0.00086379 | 0.0029977 | 0.0029688 | 0.0027759 | 0.002606 | 0.0024714 | 0.0023524 | 0.0022537 | 0.0021671 | 0.0020851 | 0.0020186
| 0.9 | 0.00083808 | 0.0029823 | 0.0029186 | 0.0027161 | 0.002546 | 0.0024137 | 0.0022935 | 0.0021983 | 0.002109 | 0.0020354 | 0.0019669 |  | 0.9 | 0.00083808 | 0.0029823 | 0.0029186 | 0.0027161 | 0.002546 | 0.0024137 | 0.0022935 | 0.0021983 | 0.002109 | 0.0020354 | 0.0019669
| 0.95 | 0.00080702 | 0.0029585 | 0.0028677 | 0.0026607 | 0.002495 | 0.0023587 | 0.0022446 | 0.0021499 | 0.0020634 | 0.0019878 | 0.0019197 |  | 0.95 | 0.00080702 | 0.0029585 | 0.0028677 | 0.0026607 | 0.002495 | 0.0023587 | 0.0022446 | 0.0021499 | 0.0020634 | 0.0019878 | 0.0019197
| 1 | 0.00077872 | 0.0029404 | 0.0028145 | 0.0026065 | 0.0024403 | 0.0023108 | 0.0021935 | 0.0020998 | 0.0020139 | 0.0019421 | 0.0018803 |  | 1 | 0.00077872 | 0.0029404 | 0.0028145 | 0.0026065 | 0.0024403 | 0.0023108 | 0.0021935 | 0.0020998 | 0.0020139 | 0.0019421 | 0.0018803
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | [12 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 0 to 1
| 0.05 | 1.3486 | 1.7582 | 2.0798 | 2.3281 | 2.5262 | 2.6797 | 2.8051 | 2.9109 | 2.9806 | 3.0499 | 3.1037 |  | 0.05 | 1.3486 | 1.7582 | 2.0798 | 2.3281 | 2.5262 | 2.6797 | 2.8051 | 2.9109 | 2.9806 | 3.0499 | 3.1037
| 0.1 | 1.2327 | 2.109 | 2.7084 | 3.1577 | 3.495 | 3.738 | 3.9091 | 4.0851 | 4.2268 | 4.2742 | 4.3458 |  | 0.1 | 1.2327 | 2.109 | 2.7084 | 3.1577 | 3.495 | 3.738 | 3.9091 | 4.0851 | 4.2268 | 4.2742 | 4.3458
| 0.15 | 1.1207 | 2.4089 | 3.2492 | 3.7122 | 4.4173 | 4.5317 | 4.7553 | 4.9508 | 5.0726 | 5.0754 | 5.2976 |  | 0.15 | 1.1207 | 2.4089 | 3.2492 | 3.7122 | 4.4173 | 4.5317 | 4.7553 | 4.9508 | 5.0726 | 5.0754 | 5.2976
| 0.2 | 1.0371 | 2.6864 | 3.6607 | 4.391 | 4.8916 | 5.2267 | 5.5418 | 5.7515 | 5.903 | 6.0266 | 6.1206 |  | 0.2 | 1.0371 | 2.6864 | 3.6607 | 4.391 | 4.8916 | 5.2267 | 5.5418 | 5.7515 | 5.903 | 6.0266 | 6.1206
| 0.25 | 0.98632 | 2.979 | 4.096 | 4.8996 | 5.4722 | 5.872 | 6.1739 | 6.403 | 6.576 | 6.7191 | 6.8153 |  | 0.25 | 0.98632 | 2.979 | 4.096 | 4.8996 | 5.4722 | 5.872 | 6.1739 | 6.403 | 6.576 | 6.7191 | 6.8153
| 0.3 | 0.89171 | 3.1924 | 4.4682 | 5.3652 | 5.9726 | 6.415 | 6.7468 | 7.0045 | 7.1905 | 7.3422 | 7.4416 |  | 0.3 | 0.89171 | 3.1924 | 4.4682 | 5.3652 | 5.9726 | 6.415 | 6.7468 | 7.0045 | 7.1905 | 7.3422 | 7.4416
| 0.35 | 0.93618 | 3.4057 | 4.8565 | 5.7777 | 6.4235 | 6.9086 | 7.268 | 7.5343 | 7.7471 | 7.8953 | 8.0179 |  | 0.35 | 0.93618 | 3.4057 | 4.8565 | 5.7777 | 6.4235 | 6.9086 | 7.268 | 7.5343 | 7.7471 | 7.8953 | 8.0179
| 0.4 | 0.89506 | 3.6327 | 5.1788 | 6.1606 | 6.8556 | 7.3679 | 7.7457 | 8.0366 | 8.2556 | 8.4195 | 8.5446 |  | 0.4 | 0.89506 | 3.6327 | 5.1788 | 6.1606 | 6.8556 | 7.3679 | 7.7457 | 8.0366 | 8.2556 | 8.4195 | 8.5446
| 0.45 | 0.88473 | 3.8457 | 5.477 | 6.511 | 7.25 | 7.7885 | 8.1912 | 8.5013 | 8.7409 | 8.9131 | 9.0483 |  | 0.45 | 0.88473 | 3.8457 | 5.477 | 6.511 | 7.25 | 7.7885 | 8.1912 | 8.5013 | 8.7409 | 8.9131 | 9.0483
| 0.5 | 0.86821 | 4.0487 | 5.7585 | 6.8538 | 7.6189 | 8.1866 | 8.6162 | 8.9428 | 9.1916 | 9.3744 | 9.5285 |  | 0.5 | 0.86821 | 4.0487 | 5.7585 | 6.8538 | 7.6189 | 8.1866 | 8.6162 | 8.9428 | 9.1916 | 9.3744 | 9.5285
| 0.55 | 0.863 | 4.2322 | 6.0239 | 7.1582 | 7.9677 | 8.5612 | 9.0174 | 9.3652 | 9.628 | 9.82 | 9.969 |  | 0.55 | 0.863 | 4.2322 | 6.0239 | 7.1582 | 7.9677 | 8.5612 | 9.0174 | 9.3652 | 9.628 | 9.82 | 9.969
| 0.6 | 0.85095 | 4.435 | 6.2708 | 7.4538 | 8.293 | 8.9233 | 9.4052 | 9.7644 | 10.0403 | 10.2544 | 10.4138 |  | 0.6 | 0.85095 | 4.435 | 6.2708 | 7.4538 | 8.293 | 8.9233 | 9.4052 | 9.7644 | 10.0403 | 10.2544 | 10.4138
| 0.65 | 0.85074 | 4.6037 | 6.507 | 7.7319 | 8.6091 | 9.2794 | 9.7695 | 10.149 | 10.4373 | 10.6641 | 10.82 |  | 0.65 | 0.85074 | 4.6037 | 6.507 | 7.7319 | 8.6091 | 9.2794 | 9.7695 | 10.149 | 10.4373 | 10.6641 | 10.82
| 0.7 | 0.84087 | 4.7783 | 6.7379 | 8.0002 | 8.9161 | 9.6038 | 10.1292 | 10.5244 | 10.8203 | 11.0448 | 11.225 |  | 0.7 | 0.84087 | 4.7783 | 6.7379 | 8.0002 | 8.9161 | 9.6038 | 10.1292 | 10.5244 | 10.8203 | 11.0448 | 11.225
| 0.75 | 0.83918 | 4.9388 | 6.9515 | 8.2707 | 9.2132 | 9.9286 | 10.4742 | 10.8839 | 11.1893 | 11.4329 | 11.6154 |  | 0.75 | 0.83918 | 4.9388 | 6.9515 | 8.2707 | 9.2132 | 9.9286 | 10.4742 | 10.8839 | 11.1893 | 11.4329 | 11.6154
| 0.8 | 0.82983 | 5.1071 | 7.1525 | 8.5136 | 9.5086 | 10.2406 | 10.8091 | 11.2249 | 11.5518 | 11.7995 | 11.9792 |  | 0.8 | 0.82983 | 5.1071 | 7.1525 | 8.5136 | 9.5086 | 10.2406 | 10.8091 | 11.2249 | 11.5518 | 11.7995 | 11.9792
| 0.85 | 0.82459 | 5.2633 | 7.361 | 8.7562 | 9.7822 | 10.5446 | 11.1224 | 11.5618 | 11.8951 | 12.1454 | 12.3391 |  | 0.85 | 0.82459 | 5.2633 | 7.361 | 8.7562 | 9.7822 | 10.5446 | 11.1224 | 11.5618 | 11.8951 | 12.1454 | 12.3391
| 0.9 | 0.82416 | 5.4006 | 7.5518 | 8.9929 | 10.0524 | 10.8397 | 11.4417 | 11.8858 | 12.2368 | 12.4937 | 12.6932 |  | 0.9 | 0.82416 | 5.4006 | 7.5518 | 8.9929 | 10.0524 | 10.8397 | 11.4417 | 11.8858 | 12.2368 | 12.4937 | 12.6932
| 0.95 | 0.81627 | 5.5543 | 7.7412 | 9.2269 | 10.3147 | 11.1227 | 11.7424 | 12.2097 | 12.562 | 12.8224 | 13.0307 |  | 0.95 | 0.81627 | 5.5543 | 7.7412 | 9.2269 | 10.3147 | 11.1227 | 11.7424 | 12.2097 | 12.562 | 12.8224 | 13.0307
| 1 | 0.8193 | 5.6889 | 7.9276 | 9.4463 | 10.5747 | 11.3969 | 12.0304 | 12.5105 | 12.8715 | 13.1444 | 13.3616 |  | 1 | 0.8193 | 5.6889 | 7.9276 | 9.4463 | 10.5747 | 11.3969 | 12.0304 | 12.5105 | 12.8715 | 13.1444 | 13.3616
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.016634 | 0.020505 | 0.025156 | 0.030727 | 0.035003 | 0.039266 | 0.043413 | 0.047056 | 0.050536 | 0.053875 | 0.059239 |  | 0.05 | 0.016634 | 0.020505 | 0.025156 | 0.030727 | 0.035003 | 0.039266 | 0.043413 | 0.047056 | 0.050536 | 0.053875 | 0.059239
| 0.1 | 0.015004 | 0.030043 | 0.047296 | 0.060312 | 0.070347 | 0.074086 | 0.079918 | 0.084217 | 0.090582 | 0.094002 | 0.10012 |  | 0.1 | 0.015004 | 0.030043 | 0.047296 | 0.060312 | 0.070347 | 0.074086 | 0.079918 | 0.084217 | 0.090582 | 0.094002 | 0.10012
| 0.15 | 0.0065987 | 0.038138 | 0.063182 | 0.080852 | 0.094706 | 0.10891 | 0.10999 | 0.12138 | 0.13063 | 0.13413 | 0.141 |  | 0.15 | 0.0065987 | 0.038138 | 0.063182 | 0.080852 | 0.094706 | 0.10891 | 0.10999 | 0.12138 | 0.13063 | 0.13413 | 0.141
| 0.2 | 0.002924 | 0.048816 | 0.079067 | 0.10139 | 0.11907 | 0.13587 | 0.14855 | 0.15854 | 0.16604 | 0.17038 | 0.18187 |  | 0.2 | 0.002924 | 0.048816 | 0.079067 | 0.10139 | 0.11907 | 0.13587 | 0.14855 | 0.15854 | 0.16604 | 0.17038 | 0.18187
| 0.25 | -0.00041602 | 0.055884 | 0.094953 | 0.12193 | 0.14342 | 0.16283 | 0.1808 | 0.18681 | 0.19221 | 0.20075 | 0.20221 |  | 0.25 | -0.00041602 | 0.055884 | 0.094953 | 0.12193 | 0.14342 | 0.16283 | 0.1808 | 0.18681 | 0.19221 | 0.20075 | 0.20221
| 0.3 | -0.0032475 | 0.062951 | 0.11084 | 0.14247 | 0.16778 | 0.18979 | 0.20126 | 0.20983 | 0.22073 | 0.22152 | 0.22628 |  | 0.3 | -0.0032475 | 0.062951 | 0.11084 | 0.14247 | 0.16778 | 0.18979 | 0.20126 | 0.20983 | 0.22073 | 0.22152 | 0.22628
| 0.35 | -0.0047683 | 0.070019 | 0.12615 | 0.15733 | 0.19214 | 0.21333 | 0.22296 | 0.23026 | 0.23988 | 0.24303 | 0.24692 |  | 0.35 | -0.0047683 | 0.070019 | 0.12615 | 0.15733 | 0.19214 | 0.21333 | 0.22296 | 0.23026 | 0.23988 | 0.24303 | 0.24692
| 0.4 | -0.0064421 | 0.077086 | 0.13886 | 0.186 | 0.20847 | 0.22883 | 0.23966 | 0.24754 | 0.25678 | 0.2622 | 0.26805 |  | 0.4 | -0.0064421 | 0.077086 | 0.13886 | 0.186 | 0.20847 | 0.22883 | 0.23966 | 0.24754 | 0.25678 | 0.2622 | 0.26805
| 0.45 | -0.0085543 | 0.084153 | 0.16313 | 0.19764 | 0.22584 | 0.24305 | 0.25706 | 0.26686 | 0.27576 | 0.28121 | 0.28567 |  | 0.45 | -0.0085543 | 0.084153 | 0.16313 | 0.19764 | 0.22584 | 0.24305 | 0.25706 | 0.26686 | 0.27576 | 0.28121 | 0.28567
| 0.5 | -0.0073515 | 0.091221 | 0.17273 | 0.21157 | 0.2381 | 0.25811 | 0.27423 | 0.28492 | 0.29116 | 0.29789 | 0.30437 |  | 0.5 | -0.0073515 | 0.091221 | 0.17273 | 0.21157 | 0.2381 | 0.25811 | 0.27423 | 0.28492 | 0.29116 | 0.29789 | 0.30437
| 0.55 | -0.0090714 | 0.098288 | 0.17882 | 0.22655 | 0.25166 | 0.27339 | 0.28964 | 0.30027 | 0.30673 | 0.31515 | 0.32108 |  | 0.55 | -0.0090714 | 0.098288 | 0.17882 | 0.22655 | 0.25166 | 0.27339 | 0.28964 | 0.30027 | 0.30673 | 0.31515 | 0.32108
| 0.6 | -0.010071 | 0.10536 | 0.18958 | 0.23582 | 0.2639 | 0.28686 | 0.3024 | 0.31684 | 0.32291 | 0.3276 | 0.33526 |  | 0.6 | -0.010071 | 0.10536 | 0.18958 | 0.23582 | 0.2639 | 0.28686 | 0.3024 | 0.31684 | 0.32291 | 0.3276 | 0.33526
| 0.65 | -0.010687 | 0.11242 | 0.19739 | 0.24948 | 0.27584 | 0.30128 | 0.31894 | 0.33051 | 0.3381 | 0.3444 | 0.35217 |  | 0.65 | -0.010687 | 0.11242 | 0.19739 | 0.24948 | 0.27584 | 0.30128 | 0.31894 | 0.33051 | 0.3381 | 0.3444 | 0.35217
| 0.7 | -0.011484 | 0.11949 | 0.21227 | 0.25926 | 0.28978 | 0.31128 | 0.32962 | 0.34144 | 0.35384 | 0.36163 | 0.36474 |  | 0.7 | -0.011484 | 0.11949 | 0.21227 | 0.25926 | 0.28978 | 0.31128 | 0.32962 | 0.34144 | 0.35384 | 0.36163 | 0.36474
| 0.75 | -0.010223 | 0.12656 | 0.21897 | 0.2688 | 0.30121 | 0.32496 | 0.34334 | 0.35544 | 0.36746 | 0.3707 | 0.37794 |  | 0.75 | -0.010223 | 0.12656 | 0.21897 | 0.2688 | 0.30121 | 0.32496 | 0.34334 | 0.35544 | 0.36746 | 0.3707 | 0.37794
| 0.8 | -0.012855 | 0.13363 | 0.22831 | 0.27727 | 0.31167 | 0.33655 | 0.35468 | 0.37008 | 0.37816 | 0.38678 | 0.39317 |  | 0.8 | -0.012855 | 0.13363 | 0.22831 | 0.27727 | 0.31167 | 0.33655 | 0.35468 | 0.37008 | 0.37816 | 0.38678 | 0.39317
| 0.85 | -0.01144 | 0.1421 | 0.23414 | 0.28764 | 0.32154 | 0.34819 | 0.36588 | 0.38069 | 0.39096 | 0.40004 | 0.40549 |  | 0.85 | -0.01144 | 0.1421 | 0.23414 | 0.28764 | 0.32154 | 0.34819 | 0.36588 | 0.38069 | 0.39096 | 0.40004 | 0.40549
| 0.9 | -0.014066 | 0.14439 | 0.2441 | 0.29565 | 0.33239 | 0.35905 | 0.37922 | 0.39277 | 0.40561 | 0.41294 | 0.41605 |  | 0.9 | -0.014066 | 0.14439 | 0.2441 | 0.29565 | 0.33239 | 0.35905 | 0.37922 | 0.39277 | 0.40561 | 0.41294 | 0.41605
| 0.95 | -0.012752 | 0.15313 | 0.25127 | 0.30365 | 0.34186 | 0.3695 | 0.38999 | 0.40778 | 0.41486 | 0.42469 | 0.42973 |  | 0.95 | -0.012752 | 0.15313 | 0.25127 | 0.30365 | 0.34186 | 0.3695 | 0.38999 | 0.40778 | 0.41486 | 0.42469 | 0.42973
| 1 | -0.013227 | 0.15839 | 0.25838 | 0.31251 | 0.35145 | 0.38006 | 0.40093 | 0.41646 | 0.42744 | 0.43268 | 0.43994 |  | 1 | -0.013227 | 0.15839 | 0.25838 | 0.31251 | 0.35145 | 0.38006 | 0.40093 | 0.41646 | 0.42744 | 0.43268 | 0.43994
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0021579 | -0.010444 | -0.018906 | -0.024147 | -0.028715 | -0.031507 | -0.033327 | -0.034946 | -0.037251 | -0.037012 | -0.037654 |  | 0.05 | 0.0021579 | -0.010444 | -0.018906 | -0.024147 | -0.028715 | -0.031507 | -0.033327 | -0.034946 | -0.037251 | -0.037012 | -0.037654
| 0.1 | 0.0052353 | -0.01602 | -0.029631 | -0.038613 | -0.041966 | -0.04476 | -0.049242 | -0.051672 | -0.052768 | -0.053741 | -0.054739 |  | 0.1 | 0.0052353 | -0.01602 | -0.029631 | -0.038613 | -0.041966 | -0.04476 | -0.049242 | -0.051672 | -0.052768 | -0.053741 | -0.054739
| 0.15 | 0.0053041 | -0.021873 | -0.036731 | -0.046836 | -0.053279 | -0.056669 | -0.060208 | -0.061157 | -0.064164 | -0.065061 | -0.066244 |  | 0.15 | 0.0053041 | -0.021873 | -0.036731 | -0.046836 | -0.053279 | -0.056669 | -0.060208 | -0.061157 | -0.064164 | -0.065061 | -0.066244
| 0.2 | 0.0050167 | -0.026913 | -0.044117 | -0.053311 | -0.060768 | -0.065742 | -0.069155 | -0.070641 | -0.074102 | -0.076382 | -0.077095 |  | 0.2 | 0.0050167 | -0.026913 | -0.044117 | -0.053311 | -0.060768 | -0.065742 | -0.069155 | -0.070641 | -0.074102 | -0.076382 | -0.077095
| 0.25 | 0.0044098 | -0.030737 | -0.049151 | -0.060112 | -0.069342 | -0.072318 | -0.076169 | -0.080126 | -0.082729 | -0.083526 | -0.085097 |  | 0.25 | 0.0044098 | -0.030737 | -0.049151 | -0.060112 | -0.069342 | -0.072318 | -0.076169 | -0.080126 | -0.082729 | -0.083526 | -0.085097
| 0.3 | 0.0038897 | -0.03648 | -0.054662 | -0.065412 | -0.072874 | -0.078587 | -0.083182 | -0.086462 | -0.089264 | -0.090983 | -0.0927 |  | 0.3 | 0.0038897 | -0.03648 | -0.054662 | -0.065412 | -0.072874 | -0.078587 | -0.083182 | -0.086462 | -0.089264 | -0.090983 | -0.0927
| 0.35 | 0.0038238 | -0.040223 | -0.058432 | -0.069506 | -0.078068 | -0.084346 | -0.089502 | -0.093411 | -0.096101 | -0.098168 | -0.099966 |  | 0.35 | 0.0038238 | -0.040223 | -0.058432 | -0.069506 | -0.078068 | -0.084346 | -0.089502 | -0.093411 | -0.096101 | -0.098168 | -0.099966
| 0.4 | 0.003435 | -0.046421 | -0.062135 | -0.07389 | -0.082948 | -0.089912 | -0.095906 | -0.099583 | -0.10268 | -0.10481 | -0.10695 |  | 0.4 | 0.003435 | -0.046421 | -0.062135 | -0.07389 | -0.082948 | -0.089912 | -0.095906 | -0.099583 | -0.10268 | -0.10481 | -0.10695
| 0.45 | 0.0031154 | -0.047776 | -0.065328 | -0.07788 | -0.087845 | -0.095327 | -0.1013 | -0.10596 | -0.10872 | -0.11126 | -0.11324 |  | 0.45 | 0.0031154 | -0.047776 | -0.065328 | -0.07788 | -0.087845 | -0.095327 | -0.1013 | -0.10596 | -0.10872 | -0.11126 | -0.11324
| 0.5 | 0.0029879 | -0.049131 | -0.068372 | -0.081744 | -0.092323 | -0.10018 | -0.10653 | -0.11121 | -0.11463 | -0.11745 | -0.11916 |  | 0.5 | 0.0029879 | -0.049131 | -0.068372 | -0.081744 | -0.092323 | -0.10018 | -0.10653 | -0.11121 | -0.11463 | -0.11745 | -0.11916
| 0.55 | 0.0027116 | -0.053257 | -0.071085 | -0.085554 | -0.096959 | -0.10509 | -0.11189 | -0.11643 | -0.12024 | -0.1231 | -0.12496 |  | 0.55 | 0.0027116 | -0.053257 | -0.071085 | -0.085554 | -0.096959 | -0.10509 | -0.11189 | -0.11643 | -0.12024 | -0.1231 | -0.12496
| 0.6 | 0.0024662 | -0.054885 | -0.074213 | -0.08915 | -0.1006 | -0.10976 | -0.11643 | -0.12184 | -0.12559 | -0.1285 | -0.13064 |  | 0.6 | 0.0024662 | -0.054885 | -0.074213 | -0.08915 | -0.1006 | -0.10976 | -0.11643 | -0.12184 | -0.12559 | -0.1285 | -0.13064
| 0.65 | 0.0026991 | -0.056264 | -0.077163 | -0.092576 | -0.10475 | -0.11399 | -0.12105 | -0.12651 | -0.13046 | -0.13328 | -0.13577 |  | 0.65 | 0.0026991 | -0.056264 | -0.077163 | -0.092576 | -0.10475 | -0.11399 | -0.12105 | -0.12651 | -0.13046 | -0.13328 | -0.13577
| 0.7 | 0.0024329 | -0.057695 | -0.079527 | -0.09598 | -0.10894 | -0.11842 | -0.12568 | -0.13135 | -0.13528 | -0.13838 | -0.14077 |  | 0.7 | 0.0024329 | -0.057695 | -0.079527 | -0.09598 | -0.10894 | -0.11842 | -0.12568 | -0.13135 | -0.13528 | -0.13838 | -0.14077
| 0.75 | 0.0022449 | -0.059669 | -0.081201 | -0.099164 | -0.11261 | -0.12259 | -0.13025 | -0.13602 | -0.1405 | -0.14324 | -0.14587 |  | 0.75 | 0.0022449 | -0.059669 | -0.081201 | -0.099164 | -0.11261 | -0.12259 | -0.13025 | -0.13602 | -0.1405 | -0.14324 | -0.14587
| 0.8 | 0.0022472 | -0.06121 | -0.084278 | -0.10235 | -0.11636 | -0.12667 | -0.13438 | -0.14024 | -0.14459 | -0.14791 | -0.15054 |  | 0.8 | 0.0022472 | -0.06121 | -0.084278 | -0.10235 | -0.11636 | -0.12667 | -0.13438 | -0.14024 | -0.14459 | -0.14791 | -0.15054
| 0.85 | 0.0021159 | -0.062752 | -0.087024 | -0.10571 | -0.1199 | -0.13038 | -0.13841 | -0.14428 | -0.14888 | -0.1526 | -0.15549 |  | 0.85 | 0.0021159 | -0.062752 | -0.087024 | -0.10571 | -0.1199 | -0.13038 | -0.13841 | -0.14428 | -0.14888 | -0.1526 | -0.15549
| 0.9 | 0.0019008 | -0.0645 | -0.089217 | -0.10877 | -0.12346 | -0.13402 | -0.14262 | -0.14851 | -0.1534 | -0.15697 | -0.15972 |  | 0.9 | 0.0019008 | -0.0645 | -0.089217 | -0.10877 | -0.12346 | -0.13402 | -0.14262 | -0.14851 | -0.1534 | -0.15697 | -0.15972
| 0.95 | 0.0019398 | -0.065951 | -0.091721 | -0.11181 | -0.12664 | -0.1377 | -0.14613 | -0.15228 | -0.15729 | -0.16102 | -0.16418 |  | 0.95 | 0.0019398 | -0.065951 | -0.091721 | -0.11181 | -0.12664 | -0.1377 | -0.14613 | -0.15228 | -0.15729 | -0.16102 | -0.16418
| 1 | 0.0020556 | -0.067112 | -0.093938 | -0.1148 | -0.13 | -0.14096 | -0.15002 | -0.15584 | -0.16166 | -0.16577 | -0.16788 |  | 1 | 0.0020556 | -0.067112 | -0.093938 | -0.1148 | -0.13 | -0.14096 | -0.15002 | -0.15584 | -0.16166 | -0.16577 | -0.16788
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
𝐸2=𝐾_𝐸2∙𝑈
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))

## CLASS1_LS< (hidden)
If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0329 | 1.0738 | 1.1063 | 1.1269 | 1.1374 | 1.1407 | 1.1389 | 1.1335 | 1.1257 | 1.1161 | 1.1055
| 0.1 | 1.0354 | 1.0812 | 1.1265 | 1.1567 | 1.1699 | 1.1728 | 1.1692 | 1.1616 | 1.1512 | 1.1392 | 1.1261
| 0.15 | 1.0183 | 1.0813 | 1.1314 | 1.1608 | 1.1767 | 1.1809 | 1.1781 | 1.1707 | 1.1604 | 1.1482 | 1.1347
| 0.2 | 0.9968 | 1.0729 | 1.1334 | 1.164 | 1.1795 | 1.1859 | 1.1842 | 1.1773 | 1.167 | 1.1545 | 1.1407
| 0.25 | 0.97215 | 1.0635 | 1.1315 | 1.1654 | 1.1825 | 1.1903 | 1.189 | 1.182 | 1.1714 | 1.1586 | 1.1444
| 0.3 | 0.94782 | 1.0571 | 1.1286 | 1.1652 | 1.1854 | 1.1936 | 1.1923 | 1.185 | 1.1742 | 1.1612 | 1.1468
| 0.35 | 0.92522 | 1.0509 | 1.1254 | 1.1645 | 1.1876 | 1.1959 | 1.1944 | 1.1871 | 1.1763 | 1.1632 | 1.1487
| 0.4 | 0.90479 | 1.0451 | 1.1224 | 1.1637 | 1.189 | 1.1974 | 1.196 | 1.1888 | 1.1779 | 1.1648 | 1.1503
| 0.45 | 0.88654 | 1.0399 | 1.1196 | 1.1645 | 1.19 | 1.1986 | 1.1973 | 1.1902 | 1.1794 | 1.1663 | 1.1517
| 0.5 | 0.87032 | 1.0353 | 1.117 | 1.1649 | 1.1907 | 1.1996 | 1.1985 | 1.1915 | 1.1806 | 1.1674 | 1.1528
| 0.55 | 0.8559 | 1.0311 | 1.1152 | 1.1652 | 1.1913 | 1.2005 | 1.1996 | 1.1926 | 1.1817 | 1.1684 | 1.1537
| 0.6 | 0.84306 | 1.0273 | 1.1135 | 1.1653 | 1.1919 | 1.2014 | 1.2006 | 1.1935 | 1.1826 | 1.1692 | 1.1545
| 0.65 | 0.83158 | 1.0239 | 1.1121 | 1.1658 | 1.1925 | 1.2021 | 1.2014 | 1.1943 | 1.1833 | 1.17 | 1.1552
| 0.7 | 0.8213 | 1.0208 | 1.1113 | 1.1665 | 1.193 | 1.2028 | 1.202 | 1.1949 | 1.184 | 1.1706 | 1.156
| 0.75 | 0.81204 | 1.018 | 1.1109 | 1.167 | 1.1936 | 1.2034 | 1.2026 | 1.1955 | 1.1846 | 1.1712 | 1.1568
| 0.8 | 0.80367 | 1.0154 | 1.1108 | 1.1674 | 1.194 | 1.2039 | 1.2032 | 1.1961 | 1.1851 | 1.1717 | 1.1575
| 0.85 | 0.79609 | 1.013 | 1.1107 | 1.1677 | 1.1935 | 1.2043 | 1.2036 | 1.1966 | 1.1856 | 1.1722 | 1.1581
| 0.9 | 0.78918 | 1.0107 | 1.1108 | 1.1679 | 1.1934 | 1.2047 | 1.2041 | 1.1971 | 1.1861 | 1.1726 | 1.1586
| 0.95 | 0.78287 | 1.0086 | 1.1108 | 1.168 | 1.1936 | 1.2051 | 1.2045 | 1.1975 | 1.1865 | 1.1731 | 1.1591
| 1 | 0.77709 | 1.0067 | 1.1108 | 1.168 | 1.1938 | 1.2055 | 1.2049 | 1.1979 | 1.1869 | 1.1737 | 1.1596
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| 0.05 | 0.76334 | 0.74428 | 0.7251 | 0.70613 | 0.68805 | 0.67061 | 0.65447 | 0.63899 | 0.62421 | 0.61035 | 0.59727
| 0.1 | 0.66964 | 0.63864 | 0.61161 | 0.58792 | 0.56659 | 0.54704 | 0.52919 | 0.51272 | 0.49743 | 0.48332 | 0.47032
| 0.15 | 0.62175 | 0.57697 | 0.54565 | 0.52035 | 0.49793 | 0.47789 | 0.45987 | 0.44335 | 0.42836 | 0.41472 | 0.40243
| 0.2 | 0.59384 | 0.53504 | 0.50092 | 0.47467 | 0.45151 | 0.43075 | 0.41266 | 0.39645 | 0.38181 | 0.36902 | 0.35722
| 0.25 | 0.57525 | 0.50369 | 0.468 | 0.44005 | 0.41595 | 0.39511 | 0.37727 | 0.36145 | 0.34768 | 0.33534 | 0.32427
| 0.3 | 0.56257 | 0.47893 | 0.44174 | 0.41196 | 0.38744 | 0.36681 | 0.34935 | 0.33416 | 0.32103 | 0.30942 | 0.29891
| 0.35 | 0.55284 | 0.45893 | 0.41935 | 0.3885 | 0.36376 | 0.34348 | 0.32677 | 0.31215 | 0.29968 | 0.28863 | 0.27875
| 0.4 | 0.54576 | 0.44183 | 0.40017 | 0.36856 | 0.34382 | 0.32432 | 0.30797 | 0.29414 | 0.28199 | 0.27142 | 0.26211
| 0.45 | 0.53982 | 0.42724 | 0.38327 | 0.35115 | 0.32685 | 0.30774 | 0.29199 | 0.27869 | 0.26711 | 0.257 | 0.24815
| 0.5 | 0.53528 | 0.41437 | 0.36838 | 0.33597 | 0.31206 | 0.29351 | 0.27836 | 0.26552 | 0.25457 | 0.24479 | 0.23631
| 0.55 | 0.53122 | 0.40266 | 0.35468 | 0.32242 | 0.29917 | 0.28101 | 0.26641 | 0.2541 | 0.24355 | 0.23412 | 0.22589
| 0.6 | 0.5282 | 0.39201 | 0.34255 | 0.31055 | 0.28767 | 0.27014 | 0.25603 | 0.24402 | 0.23373 | 0.22489 | 0.21701
| 0.65 | 0.52525 | 0.38221 | 0.33157 | 0.2997 | 0.27741 | 0.26053 | 0.2466 | 0.23506 | 0.22511 | 0.21659 | 0.20893
| 0.7 | 0.52304 | 0.37308 | 0.32144 | 0.29002 | 0.26822 | 0.25161 | 0.23827 | 0.22704 | 0.21755 | 0.20906 | 0.20174
| 0.75 | 0.52082 | 0.36457 | 0.3122 | 0.28122 | 0.2599 | 0.24376 | 0.23081 | 0.21984 | 0.21053 | 0.20243 | 0.19526
| 0.8 | 0.51916 | 0.35649 | 0.30365 | 0.27309 | 0.25227 | 0.23656 | 0.22399 | 0.21332 | 0.20423 | 0.19631 | 0.18934
| 0.85 | 0.51773 | 0.34903 | 0.29579 | 0.26557 | 0.24523 | 0.23 | 0.21755 | 0.20731 | 0.19837 | 0.19067 | 0.18385
| 0.9 | 0.5161 | 0.34196 | 0.28843 | 0.25881 | 0.23892 | 0.22395 | 0.21188 | 0.20174 | 0.19312 | 0.18558 | 0.17893
| 0.95 | 0.51497 | 0.33527 | 0.28174 | 0.25244 | 0.23303 | 0.21833 | 0.20648 | 0.19669 | 0.18827 | 0.18073 | 0.17438
| 1 | 0.51367 | 0.32894 | 0.27549 | 0.24647 | 0.22759 | 0.21304 | 0.20143 | 0.19183 | 0.1836 | 0.17639 | 0.17009
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0069224 | 0.0085033 | 0.0096294 | 0.010568 | 0.011228 | 0.011762 | 0.01222 | 0.012553 | 0.012834 | 0.013035 | 0.013209
| 0.1 | 0.0051644 | 0.0086385 | 0.010128 | 0.011097 | 0.011731 | 0.012235 | 0.012485 | 0.012677 | 0.012767 | 0.012781 | 0.012787
| 0.15 | 0.0036516 | 0.0083819 | 0.010139 | 0.011287 | 0.011935 | 0.012241 | 0.0124 | 0.01236 | 0.012277 | 0.012195 | 0.012026
| 0.2 | 0.0024349 | 0.0082894 | 0.010364 | 0.011465 | 0.011945 | 0.012048 | 0.012014 | 0.011875 | 0.011696 | 0.011495 | 0.011269
| 0.25 | 0.0016624 | 0.0082036 | 0.010537 | 0.011451 | 0.011763 | 0.011743 | 0.011551 | 0.011312 | 0.01109 | 0.010806 | 0.01055
| 0.3 | 0.0011181 | 0.0082927 | 0.010645 | 0.0114 | 0.011521 | 0.011311 | 0.011051 | 0.010785 | 0.010479 | 0.010166 | 0.0099376
| 0.35 | 0.00068611 | 0.0083923 | 0.010686 | 0.011255 | 0.011149 | 0.010937 | 0.010591 | 0.010247 | 0.0099393 | 0.0096599 | 0.0093893
| 0.4 | 0.00039338 | 0.008525 | 0.010688 | 0.011015 | 0.010805 | 0.010512 | 0.010128 | 0.0097689 | 0.0094773 | 0.0091609 | 0.0089065
| 0.45 | 0.00012233 | 0.0086479 | 0.010606 | 0.010777 | 0.010479 | 0.010095 | 0.0096985 | 0.0093539 | 0.0090641 | 0.0087786 | 0.0085107
| 0.5 | -0.00016091 | 0.0088021 | 0.01051 | 0.01055 | 0.010173 | 0.0097242 | 0.0093589 | 0.0089644 | 0.0086608 | 0.0083903 | 0.0081428
| 0.55 | -0.00031908 | 0.0089061 | 0.010404 | 0.01027 | 0.0098535 | 0.0094124 | 0.009018 | 0.0086535 | 0.0083415 | 0.0080801 | 0.0078305
| 0.6 | -0.00046553 | 0.0089835 | 0.010245 | 0.010029 | 0.0095448 | 0.0091066 | 0.0086888 | 0.0083763 | 0.0080544 | 0.007771 | 0.0075409
| 0.65 | -0.00056326 | 0.0090553 | 0.010121 | 0.0097505 | 0.0092719 | 0.0088572 | 0.0084593 | 0.0080947 | 0.007794 | 0.0075092 | 0.0072835
| 0.7 | -0.00067764 | 0.0091 | 0.0099796 | 0.0095103 | 0.0090292 | 0.008556 | 0.0081781 | 0.0078457 | 0.0075865 | 0.0073136 | 0.0070479
| 0.75 | -0.00084461 | 0.0091301 | 0.0097784 | 0.0093102 | 0.0087954 | 0.0083611 | 0.0079713 | 0.007635 | 0.0073614 | 0.0070512 | 0.0068446
| 0.8 | -0.00082804 | 0.0091587 | 0.0096287 | 0.0090984 | 0.008565 | 0.0081357 | 0.0077423 | 0.0074514 | 0.0071534 | 0.0068941 | 0.0066582
| 0.85 | -0.00096933 | 0.009166 | 0.00946 | 0.0089147 | 0.0083587 | 0.0079452 | 0.007534 | 0.007237 | 0.0069334 | 0.0067083 | 0.0064658
| 0.9 | -0.00091761 | 0.0091322 | 0.0093135 | 0.0087096 | 0.0081833 | 0.0077641 | 0.0073842 | 0.0070617 | 0.0068073 | 0.0065399 | 0.0063043
| 0.95 | -0.0010692 | 0.009139 | 0.0091666 | 0.0085296 | 0.0080257 | 0.007588 | 0.0072332 | 0.006922 | 0.0066065 | 0.0063858 | 0.0061393
| 1 | -0.0011146 | 0.0091075 | 0.0090096 | 0.0083585 | 0.0078746 | 0.0074312 | 0.0070819 | 0.006764 | 0.0064892 | 0.0062161 | 0.0059993
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.003473 | 0.0037612 | 0.003969 | 0.0041179 | 0.004228 | 0.0043111 | 0.0043812 | 0.0044226 | 0.0044578 | 0.0044755 | 0.0044826
| 0.1 | 0.0031136 | 0.0037934 | 0.0040139 | 0.004109 | 0.0041657 | 0.0041959 | 0.0042121 | 0.0042008 | 0.0041836 | 0.0041447 | 0.0041135
| 0.15 | 0.0026153 | 0.0036397 | 0.0038419 | 0.0039461 | 0.0039971 | 0.0040141 | 0.0039981 | 0.0039596 | 0.0039041 | 0.0038523 | 0.0037885
| 0.2 | 0.0022211 | 0.0034787 | 0.0037108 | 0.0038345 | 0.003873 | 0.003854 | 0.003809 | 0.0037441 | 0.0036722 | 0.0035941 | 0.0035248
| 0.25 | 0.0019355 | 0.0033575 | 0.003622 | 0.0037479 | 0.0037539 | 0.0037089 | 0.0036334 | 0.0035456 | 0.00346 | 0.0033752 | 0.0032928
| 0.3 | 0.0017241 | 0.0032611 | 0.0035653 | 0.0036635 | 0.0036365 | 0.0035573 | 0.0034633 | 0.0033655 | 0.0032704 | 0.0031795 | 0.0030932
| 0.35 | 0.0015384 | 0.0032003 | 0.0035163 | 0.0035754 | 0.0035114 | 0.0034136 | 0.0033073 | 0.0032016 | 0.0031031 | 0.0030108 | 0.0029238
| 0.4 | 0.0014095 | 0.0031474 | 0.0034702 | 0.0034875 | 0.003396 | 0.0032766 | 0.0031639 | 0.003055 | 0.0029541 | 0.0028612 | 0.0027764
| 0.45 | 0.0013046 | 0.0031186 | 0.0034167 | 0.0033915 | 0.0032831 | 0.0031554 | 0.0030336 | 0.0029211 | 0.0028229 | 0.0027325 | 0.0026465
| 0.5 | 0.0012107 | 0.0030979 | 0.0033637 | 0.0033019 | 0.0031758 | 0.0030382 | 0.0029194 | 0.0028014 | 0.0027083 | 0.0026169 | 0.0025335
| 0.55 | 0.0011399 | 0.0030811 | 0.0033067 | 0.0032183 | 0.0030729 | 0.0029347 | 0.0028111 | 0.0026986 | 0.0026014 | 0.002513 | 0.0024369
| 0.6 | 0.0010819 | 0.0030673 | 0.0032519 | 0.0031337 | 0.0029814 | 0.002839 | 0.002717 | 0.0026083 | 0.0025086 | 0.0024235 | 0.002348
| 0.65 | 0.0010125 | 0.0030559 | 0.0031933 | 0.0030536 | 0.0028955 | 0.002753 | 0.0026318 | 0.0025241 | 0.0024281 | 0.0023469 | 0.0022692
| 0.7 | 0.00096843 | 0.0030442 | 0.0031356 | 0.0029794 | 0.0028149 | 0.0026717 | 0.0025518 | 0.0024459 | 0.0023565 | 0.0022721 | 0.0021979
| 0.75 | 0.00093297 | 0.0030278 | 0.0030746 | 0.0029068 | 0.0027404 | 0.0026022 | 0.0024781 | 0.0023752 | 0.0022847 | 0.0022056 | 0.0021334
| 0.8 | 0.00088981 | 0.003016 | 0.0030227 | 0.0028449 | 0.002672 | 0.0025316 | 0.0024134 | 0.0023121 | 0.0022227 | 0.0021459 | 0.0020744
| 0.85 | 0.00086379 | 0.0029977 | 0.0029688 | 0.0027759 | 0.002606 | 0.0024714 | 0.0023524 | 0.0022537 | 0.0021671 | 0.0020851 | 0.0020186
| 0.9 | 0.00083808 | 0.0029823 | 0.0029186 | 0.0027161 | 0.002546 | 0.0024137 | 0.0022935 | 0.0021983 | 0.002109 | 0.0020354 | 0.0019669
| 0.95 | 0.00080702 | 0.0029585 | 0.0028677 | 0.0026607 | 0.002495 | 0.0023587 | 0.0022446 | 0.0021499 | 0.0020634 | 0.0019878 | 0.0019197
| 1 | 0.00077872 | 0.0029404 | 0.0028145 | 0.0026065 | 0.0024403 | 0.0023108 | 0.0021935 | 0.0020998 | 0.0020139 | 0.0019421 | 0.0018803
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.3486 | 1.7582 | 2.0798 | 2.3281 | 2.5262 | 2.6797 | 2.8051 | 2.9109 | 2.9806 | 3.0499 | 3.1037
| 0.1 | 1.2327 | 2.109 | 2.7084 | 3.1577 | 3.495 | 3.738 | 3.9091 | 4.0851 | 4.2268 | 4.2742 | 4.3458
| 0.15 | 1.1207 | 2.4089 | 3.2492 | 3.7122 | 4.4173 | 4.5317 | 4.7553 | 4.9508 | 5.0726 | 5.0754 | 5.2976
| 0.2 | 1.0371 | 2.6864 | 3.6607 | 4.391 | 4.8916 | 5.2267 | 5.5418 | 5.7515 | 5.903 | 6.0266 | 6.1206
| 0.25 | 0.98632 | 2.979 | 4.096 | 4.8996 | 5.4722 | 5.872 | 6.1739 | 6.403 | 6.576 | 6.7191 | 6.8153
| 0.3 | 0.89171 | 3.1924 | 4.4682 | 5.3652 | 5.9726 | 6.415 | 6.7468 | 7.0045 | 7.1905 | 7.3422 | 7.4416
| 0.35 | 0.93618 | 3.4057 | 4.8565 | 5.7777 | 6.4235 | 6.9086 | 7.268 | 7.5343 | 7.7471 | 7.8953 | 8.0179
| 0.4 | 0.89506 | 3.6327 | 5.1788 | 6.1606 | 6.8556 | 7.3679 | 7.7457 | 8.0366 | 8.2556 | 8.4195 | 8.5446
| 0.45 | 0.88473 | 3.8457 | 5.477 | 6.511 | 7.25 | 7.7885 | 8.1912 | 8.5013 | 8.7409 | 8.9131 | 9.0483
| 0.5 | 0.86821 | 4.0487 | 5.7585 | 6.8538 | 7.6189 | 8.1866 | 8.6162 | 8.9428 | 9.1916 | 9.3744 | 9.5285
| 0.55 | 0.863 | 4.2322 | 6.0239 | 7.1582 | 7.9677 | 8.5612 | 9.0174 | 9.3652 | 9.628 | 9.82 | 9.969
| 0.6 | 0.85095 | 4.435 | 6.2708 | 7.4538 | 8.293 | 8.9233 | 9.4052 | 9.7644 | 10.0403 | 10.2544 | 10.4138
| 0.65 | 0.85074 | 4.6037 | 6.507 | 7.7319 | 8.6091 | 9.2794 | 9.7695 | 10.149 | 10.4373 | 10.6641 | 10.82
| 0.7 | 0.84087 | 4.7783 | 6.7379 | 8.0002 | 8.9161 | 9.6038 | 10.1292 | 10.5244 | 10.8203 | 11.0448 | 11.225
| 0.75 | 0.83918 | 4.9388 | 6.9515 | 8.2707 | 9.2132 | 9.9286 | 10.4742 | 10.8839 | 11.1893 | 11.4329 | 11.6154
| 0.8 | 0.82983 | 5.1071 | 7.1525 | 8.5136 | 9.5086 | 10.2406 | 10.8091 | 11.2249 | 11.5518 | 11.7995 | 11.9792
| 0.85 | 0.82459 | 5.2633 | 7.361 | 8.7562 | 9.7822 | 10.5446 | 11.1224 | 11.5618 | 11.8951 | 12.1454 | 12.3391
| 0.9 | 0.82416 | 5.4006 | 7.5518 | 8.9929 | 10.0524 | 10.8397 | 11.4417 | 11.8858 | 12.2368 | 12.4937 | 12.6932
| 0.95 | 0.81627 | 5.5543 | 7.7412 | 9.2269 | 10.3147 | 11.1227 | 11.7424 | 12.2097 | 12.562 | 12.8224 | 13.0307
| 1 | 0.8193 | 5.6889 | 7.9276 | 9.4463 | 10.5747 | 11.3969 | 12.0304 | 12.5105 | 12.8715 | 13.1444 | 13.3616
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.016634 | 0.020505 | 0.025156 | 0.030727 | 0.035003 | 0.039266 | 0.043413 | 0.047056 | 0.050536 | 0.053875 | 0.059239
| 0.1 | 0.015004 | 0.030043 | 0.047296 | 0.060312 | 0.070347 | 0.074086 | 0.079918 | 0.084217 | 0.090582 | 0.094002 | 0.10012
| 0.15 | 0.0065987 | 0.038138 | 0.063182 | 0.080852 | 0.094706 | 0.10891 | 0.10999 | 0.12138 | 0.13063 | 0.13413 | 0.141
| 0.2 | 0.002924 | 0.048816 | 0.079067 | 0.10139 | 0.11907 | 0.13587 | 0.14855 | 0.15854 | 0.16604 | 0.17038 | 0.18187
| 0.25 | -0.00041602 | 0.055884 | 0.094953 | 0.12193 | 0.14342 | 0.16283 | 0.1808 | 0.18681 | 0.19221 | 0.20075 | 0.20221
| 0.3 | -0.0032475 | 0.062951 | 0.11084 | 0.14247 | 0.16778 | 0.18979 | 0.20126 | 0.20983 | 0.22073 | 0.22152 | 0.22628
| 0.35 | -0.0047683 | 0.070019 | 0.12615 | 0.15733 | 0.19214 | 0.21333 | 0.22296 | 0.23026 | 0.23988 | 0.24303 | 0.24692
| 0.4 | -0.0064421 | 0.077086 | 0.13886 | 0.186 | 0.20847 | 0.22883 | 0.23966 | 0.24754 | 0.25678 | 0.2622 | 0.26805
| 0.45 | -0.0085543 | 0.084153 | 0.16313 | 0.19764 | 0.22584 | 0.24305 | 0.25706 | 0.26686 | 0.27576 | 0.28121 | 0.28567
| 0.5 | -0.0073515 | 0.091221 | 0.17273 | 0.21157 | 0.2381 | 0.25811 | 0.27423 | 0.28492 | 0.29116 | 0.29789 | 0.30437
| 0.55 | -0.0090714 | 0.098288 | 0.17882 | 0.22655 | 0.25166 | 0.27339 | 0.28964 | 0.30027 | 0.30673 | 0.31515 | 0.32108
| 0.6 | -0.010071 | 0.10536 | 0.18958 | 0.23582 | 0.2639 | 0.28686 | 0.3024 | 0.31684 | 0.32291 | 0.3276 | 0.33526
| 0.65 | -0.010687 | 0.11242 | 0.19739 | 0.24948 | 0.27584 | 0.30128 | 0.31894 | 0.33051 | 0.3381 | 0.3444 | 0.35217
| 0.7 | -0.011484 | 0.11949 | 0.21227 | 0.25926 | 0.28978 | 0.31128 | 0.32962 | 0.34144 | 0.35384 | 0.36163 | 0.36474
| 0.75 | -0.010223 | 0.12656 | 0.21897 | 0.2688 | 0.30121 | 0.32496 | 0.34334 | 0.35544 | 0.36746 | 0.3707 | 0.37794
| 0.8 | -0.012855 | 0.13363 | 0.22831 | 0.27727 | 0.31167 | 0.33655 | 0.35468 | 0.37008 | 0.37816 | 0.38678 | 0.39317
| 0.85 | -0.01144 | 0.1421 | 0.23414 | 0.28764 | 0.32154 | 0.34819 | 0.36588 | 0.38069 | 0.39096 | 0.40004 | 0.40549
| 0.9 | -0.014066 | 0.14439 | 0.2441 | 0.29565 | 0.33239 | 0.35905 | 0.37922 | 0.39277 | 0.40561 | 0.41294 | 0.41605
| 0.95 | -0.012752 | 0.15313 | 0.25127 | 0.30365 | 0.34186 | 0.3695 | 0.38999 | 0.40778 | 0.41486 | 0.42469 | 0.42973
| 1 | -0.013227 | 0.15839 | 0.25838 | 0.31251 | 0.35145 | 0.38006 | 0.40093 | 0.41646 | 0.42744 | 0.43268 | 0.43994
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0021579 | -0.010444 | -0.018906 | -0.024147 | -0.028715 | -0.031507 | -0.033327 | -0.034946 | -0.037251 | -0.037012 | -0.037654
| 0.1 | 0.0052353 | -0.01602 | -0.029631 | -0.038613 | -0.041966 | -0.04476 | -0.049242 | -0.051672 | -0.052768 | -0.053741 | -0.054739
| 0.15 | 0.0053041 | -0.021873 | -0.036731 | -0.046836 | -0.053279 | -0.056669 | -0.060208 | -0.061157 | -0.064164 | -0.065061 | -0.066244
| 0.2 | 0.0050167 | -0.026913 | -0.044117 | -0.053311 | -0.060768 | -0.065742 | -0.069155 | -0.070641 | -0.074102 | -0.076382 | -0.077095
| 0.25 | 0.0044098 | -0.030737 | -0.049151 | -0.060112 | -0.069342 | -0.072318 | -0.076169 | -0.080126 | -0.082729 | -0.083526 | -0.085097
| 0.3 | 0.0038897 | -0.03648 | -0.054662 | -0.065412 | -0.072874 | -0.078587 | -0.083182 | -0.086462 | -0.089264 | -0.090983 | -0.0927
| 0.35 | 0.0038238 | -0.040223 | -0.058432 | -0.069506 | -0.078068 | -0.084346 | -0.089502 | -0.093411 | -0.096101 | -0.098168 | -0.099966
| 0.4 | 0.003435 | -0.046421 | -0.062135 | -0.07389 | -0.082948 | -0.089912 | -0.095906 | -0.099583 | -0.10268 | -0.10481 | -0.10695
| 0.45 | 0.0031154 | -0.047776 | -0.065328 | -0.07788 | -0.087845 | -0.095327 | -0.1013 | -0.10596 | -0.10872 | -0.11126 | -0.11324
| 0.5 | 0.0029879 | -0.049131 | -0.068372 | -0.081744 | -0.092323 | -0.10018 | -0.10653 | -0.11121 | -0.11463 | -0.11745 | -0.11916
| 0.55 | 0.0027116 | -0.053257 | -0.071085 | -0.085554 | -0.096959 | -0.10509 | -0.11189 | -0.11643 | -0.12024 | -0.1231 | -0.12496
| 0.6 | 0.0024662 | -0.054885 | -0.074213 | -0.08915 | -0.1006 | -0.10976 | -0.11643 | -0.12184 | -0.12559 | -0.1285 | -0.13064
| 0.65 | 0.0026991 | -0.056264 | -0.077163 | -0.092576 | -0.10475 | -0.11399 | -0.12105 | -0.12651 | -0.13046 | -0.13328 | -0.13577
| 0.7 | 0.0024329 | -0.057695 | -0.079527 | -0.09598 | -0.10894 | -0.11842 | -0.12568 | -0.13135 | -0.13528 | -0.13838 | -0.14077
| 0.75 | 0.0022449 | -0.059669 | -0.081201 | -0.099164 | -0.11261 | -0.12259 | -0.13025 | -0.13602 | -0.1405 | -0.14324 | -0.14587
| 0.8 | 0.0022472 | -0.06121 | -0.084278 | -0.10235 | -0.11636 | -0.12667 | -0.13438 | -0.14024 | -0.14459 | -0.14791 | -0.15054
| 0.85 | 0.0021159 | -0.062752 | -0.087024 | -0.10571 | -0.1199 | -0.13038 | -0.13841 | -0.14428 | -0.14888 | -0.1526 | -0.15549
| 0.9 | 0.0019008 | -0.0645 | -0.089217 | -0.10877 | -0.12346 | -0.13402 | -0.14262 | -0.14851 | -0.1534 | -0.15697 | -0.15972
| 0.95 | 0.0019398 | -0.065951 | -0.091721 | -0.11181 | -0.12664 | -0.1377 | -0.14613 | -0.15228 | -0.15729 | -0.16102 | -0.16418
| 1 | 0.0020556 | -0.067112 | -0.093938 | -0.1148 | -0.13 | -0.14096 | -0.15002 | -0.15584 | -0.16166 | -0.16577 | -0.16788
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
𝐸2=𝐾_𝐸2∙𝑈
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-14.51) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-44.72))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-14.51) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-44.72))

## CLASS2_LS>= (hidden)
If Iload/Isc x 5.6569 ≥1 | [12 empty] | If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 |  | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0358 | 1.0722 | 1.1008 | 1.1191 | 1.1288 | 1.132 | 1.1306 | 1.1258 | 1.1188 | 1.11 | 1.1002 |  | 0.05 | 1.0358 | 1.0722 | 1.1008 | 1.1191 | 1.1288 | 1.132 | 1.1306 | 1.1258 | 1.1188 | 1.11 | 1.1002
| 0.1 | 1.0388 | 1.0768 | 1.1241 | 1.1528 | 1.1657 | 1.1688 | 1.1656 | 1.1583 | 1.1484 | 1.1369 | 1.1242 |  | 0.1 | 1.0388 | 1.0768 | 1.1241 | 1.1528 | 1.1657 | 1.1688 | 1.1656 | 1.1583 | 1.1484 | 1.1369 | 1.1242
| 0.15 | 1.0287 | 1.0793 | 1.1249 | 1.1598 | 1.1752 | 1.1792 | 1.1763 | 1.169 | 1.1589 | 1.1469 | 1.1337 |  | 0.15 | 1.0287 | 1.0793 | 1.1249 | 1.1598 | 1.1752 | 1.1792 | 1.1763 | 1.169 | 1.1589 | 1.1469 | 1.1337
| 0.2 | 1.0072 | 1.0775 | 1.1268 | 1.1609 | 1.179 | 1.1848 | 1.183 | 1.1761 | 1.166 | 1.1538 | 1.1403 |  | 0.2 | 1.0072 | 1.0775 | 1.1268 | 1.1609 | 1.179 | 1.1848 | 1.183 | 1.1761 | 1.166 | 1.1538 | 1.1403
| 0.25 | 0.98246 | 1.0718 | 1.1293 | 1.1611 | 1.1822 | 1.1896 | 1.1883 | 1.1814 | 1.1711 | 1.1586 | 1.1447 |  | 0.25 | 0.98246 | 1.0718 | 1.1293 | 1.1611 | 1.1822 | 1.1896 | 1.1883 | 1.1814 | 1.1711 | 1.1586 | 1.1447
| 0.3 | 0.95806 | 1.0652 | 1.1297 | 1.1623 | 1.1853 | 1.1934 | 1.1921 | 1.1851 | 1.1746 | 1.1618 | 1.1476 |  | 0.3 | 0.95806 | 1.0652 | 1.1297 | 1.1623 | 1.1853 | 1.1934 | 1.1921 | 1.1851 | 1.1746 | 1.1618 | 1.1476
| 0.35 | 0.93543 | 1.0587 | 1.1289 | 1.1636 | 1.1878 | 1.1961 | 1.1949 | 1.1877 | 1.177 | 1.1641 | 1.1498 |  | 0.35 | 0.93543 | 1.0587 | 1.1289 | 1.1636 | 1.1878 | 1.1961 | 1.1949 | 1.1877 | 1.177 | 1.1641 | 1.1498
| 0.4 | 0.91499 | 1.0527 | 1.1274 | 1.1646 | 1.1897 | 1.1981 | 1.1969 | 1.1897 | 1.179 | 1.166 | 1.1516 |  | 0.4 | 0.91499 | 1.0527 | 1.1274 | 1.1646 | 1.1897 | 1.1981 | 1.1969 | 1.1897 | 1.179 | 1.166 | 1.1516
| 0.45 | 0.89675 | 1.0474 | 1.1257 | 1.1656 | 1.1911 | 1.1996 | 1.1984 | 1.1914 | 1.1806 | 1.1676 | 1.1532 |  | 0.45 | 0.89675 | 1.0474 | 1.1257 | 1.1656 | 1.1911 | 1.1996 | 1.1984 | 1.1914 | 1.1806 | 1.1676 | 1.1532
| 0.5 | 0.88053 | 1.0426 | 1.1238 | 1.1664 | 1.1921 | 1.2009 | 1.1998 | 1.1928 | 1.1821 | 1.169 | 1.1545 |  | 0.5 | 0.88053 | 1.0426 | 1.1238 | 1.1664 | 1.1921 | 1.2009 | 1.1998 | 1.1928 | 1.1821 | 1.169 | 1.1545
| 0.55 | 0.86611 | 1.0383 | 1.1219 | 1.1669 | 1.1929 | 1.2019 | 1.201 | 1.1941 | 1.1833 | 1.1702 | 1.1556 |  | 0.55 | 0.86611 | 1.0383 | 1.1219 | 1.1669 | 1.1929 | 1.2019 | 1.201 | 1.1941 | 1.1833 | 1.1702 | 1.1556
| 0.6 | 0.85327 | 1.0345 | 1.1201 | 1.1673 | 1.1936 | 1.2029 | 1.2021 | 1.1952 | 1.1844 | 1.1712 | 1.1565 |  | 0.6 | 0.85327 | 1.0345 | 1.1201 | 1.1673 | 1.1936 | 1.2029 | 1.2021 | 1.1952 | 1.1844 | 1.1712 | 1.1565
| 0.65 | 0.84179 | 1.031 | 1.1185 | 1.1675 | 1.1943 | 1.2038 | 1.2031 | 1.1961 | 1.1853 | 1.172 | 1.1573 |  | 0.65 | 0.84179 | 1.031 | 1.1185 | 1.1675 | 1.1943 | 1.2038 | 1.2031 | 1.1961 | 1.1853 | 1.172 | 1.1573
| 0.7 | 0.8315 | 1.0278 | 1.117 | 1.1677 | 1.1949 | 1.2046 | 1.204 | 1.197 | 1.1861 | 1.1728 | 1.1581 |  | 0.7 | 0.8315 | 1.0278 | 1.117 | 1.1677 | 1.1949 | 1.2046 | 1.204 | 1.197 | 1.1861 | 1.1728 | 1.1581
| 0.75 | 0.82224 | 1.0249 | 1.1158 | 1.168 | 1.1955 | 1.2054 | 1.2047 | 1.1977 | 1.1868 | 1.1735 | 1.1587 |  | 0.75 | 0.82224 | 1.0249 | 1.1158 | 1.168 | 1.1955 | 1.2054 | 1.2047 | 1.1977 | 1.1868 | 1.1735 | 1.1587
| 0.8 | 0.81386 | 1.0223 | 1.1148 | 1.1682 | 1.1961 | 1.206 | 1.2053 | 1.1983 | 1.1874 | 1.1741 | 1.1593 |  | 0.8 | 0.81386 | 1.0223 | 1.1148 | 1.1682 | 1.1961 | 1.206 | 1.2053 | 1.1983 | 1.1874 | 1.1741 | 1.1593
| 0.85 | 0.80626 | 1.0198 | 1.114 | 1.1684 | 1.1966 | 1.2066 | 1.2059 | 1.1989 | 1.188 | 1.1747 | 1.1599 |  | 0.85 | 0.80626 | 1.0198 | 1.114 | 1.1684 | 1.1966 | 1.2066 | 1.2059 | 1.1989 | 1.188 | 1.1747 | 1.1599
| 0.9 | 0.79934 | 1.0175 | 1.1134 | 1.1687 | 1.1971 | 1.2071 | 1.2065 | 1.1995 | 1.1886 | 1.1752 | 1.1603 |  | 0.9 | 0.79934 | 1.0175 | 1.1134 | 1.1687 | 1.1971 | 1.2071 | 1.2065 | 1.1995 | 1.1886 | 1.1752 | 1.1603
| 0.95 | 0.79302 | 1.0153 | 1.1129 | 1.169 | 1.1975 | 1.2075 | 1.207 | 1.2 | 1.1891 | 1.1757 | 1.1608 |  | 0.95 | 0.79302 | 1.0153 | 1.1129 | 1.169 | 1.1975 | 1.2075 | 1.207 | 1.2 | 1.1891 | 1.1757 | 1.1608
| 1 | 0.78722 | 1.0133 | 1.1127 | 1.1692 | 1.1978 | 1.208 | 1.2074 | 1.2005 | 1.1895 | 1.1761 | 1.1612 |  | 1 | 0.78722 | 1.0133 | 1.1127 | 1.1692 | 1.1978 | 1.208 | 1.2074 | 1.2005 | 1.1895 | 1.1761 | 1.1612
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | [12 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 0 to 1
| 0.05 | 0.85541 | 0.83294 | 0.81054 | 0.78911 | 0.76857 | 0.74909 | 0.73127 | 0.7138 | 0.69751 | 0.6822 | 0.66756 |  | 0.05 | 0.85541 | 0.83294 | 0.81054 | 0.78911 | 0.76857 | 0.74909 | 0.73127 | 0.7138 | 0.69751 | 0.6822 | 0.66756
| 0.1 | 0.75149 | 0.71499 | 0.6847 | 0.6582 | 0.63437 | 0.61269 | 0.59281 | 0.57444 | 0.55731 | 0.54168 | 0.52707 |  | 0.1 | 0.75149 | 0.71499 | 0.6847 | 0.6582 | 0.63437 | 0.61269 | 0.59281 | 0.57444 | 0.55731 | 0.54168 | 0.52707
| 0.15 | 0.69805 | 0.64629 | 0.61181 | 0.58343 | 0.55836 | 0.53564 | 0.51554 | 0.49703 | 0.48015 | 0.465 | 0.45125 |  | 0.15 | 0.69805 | 0.64629 | 0.61181 | 0.58343 | 0.55836 | 0.53564 | 0.51554 | 0.49703 | 0.48015 | 0.465 | 0.45125
| 0.2 | 0.66683 | 0.59988 | 0.56211 | 0.5323 | 0.50589 | 0.48282 | 0.46242 | 0.44436 | 0.42827 | 0.41391 | 0.40071 |  | 0.2 | 0.66683 | 0.59988 | 0.56211 | 0.5323 | 0.50589 | 0.48282 | 0.46242 | 0.44436 | 0.42827 | 0.41391 | 0.40071
| 0.25 | 0.64602 | 0.5651 | 0.52509 | 0.49317 | 0.46612 | 0.44288 | 0.4229 | 0.4053 | 0.38996 | 0.37632 | 0.36392 |  | 0.25 | 0.64602 | 0.5651 | 0.52509 | 0.49317 | 0.46612 | 0.44288 | 0.4229 | 0.4053 | 0.38996 | 0.37632 | 0.36392
| 0.3 | 0.63182 | 0.53759 | 0.49521 | 0.46154 | 0.43404 | 0.41118 | 0.39187 | 0.37493 | 0.36032 | 0.34738 | 0.33571 |  | 0.3 | 0.63182 | 0.53759 | 0.49521 | 0.46154 | 0.43404 | 0.41118 | 0.39187 | 0.37493 | 0.36032 | 0.34738 | 0.33571
| 0.35 | 0.62086 | 0.51518 | 0.47011 | 0.43532 | 0.40777 | 0.38533 | 0.36669 | 0.3505 | 0.33649 | 0.32404 | 0.31322 |  | 0.35 | 0.62086 | 0.51518 | 0.47011 | 0.43532 | 0.40777 | 0.38533 | 0.36669 | 0.3505 | 0.33649 | 0.32404 | 0.31322
| 0.4 | 0.61291 | 0.49634 | 0.44818 | 0.41286 | 0.38576 | 0.36378 | 0.34568 | 0.33021 | 0.31678 | 0.30505 | 0.29452 |  | 0.4 | 0.61291 | 0.49634 | 0.44818 | 0.41286 | 0.38576 | 0.36378 | 0.34568 | 0.33021 | 0.31678 | 0.30505 | 0.29452
| 0.45 | 0.60653 | 0.47969 | 0.42918 | 0.39356 | 0.36662 | 0.34551 | 0.328 | 0.31308 | 0.30035 | 0.28896 | 0.27902 |  | 0.45 | 0.60653 | 0.47969 | 0.42918 | 0.39356 | 0.36662 | 0.34551 | 0.328 | 0.31308 | 0.30035 | 0.28896 | 0.27902
| 0.5 | 0.6011 | 0.46503 | 0.4125 | 0.37665 | 0.35018 | 0.32954 | 0.31269 | 0.29844 | 0.28601 | 0.2753 | 0.26575 |  | 0.5 | 0.6011 | 0.46503 | 0.4125 | 0.37665 | 0.35018 | 0.32954 | 0.31269 | 0.29844 | 0.28601 | 0.2753 | 0.26575
| 0.55 | 0.59691 | 0.45179 | 0.39727 | 0.36161 | 0.33577 | 0.31572 | 0.29946 | 0.28563 | 0.27374 | 0.26344 | 0.2541 |  | 0.55 | 0.59691 | 0.45179 | 0.39727 | 0.36161 | 0.33577 | 0.31572 | 0.29946 | 0.28563 | 0.27374 | 0.26344 | 0.2541
| 0.6 | 0.59305 | 0.43956 | 0.38383 | 0.3483 | 0.32296 | 0.30343 | 0.28765 | 0.27437 | 0.26292 | 0.25289 | 0.24401 |  | 0.6 | 0.59305 | 0.43956 | 0.38383 | 0.3483 | 0.32296 | 0.30343 | 0.28765 | 0.27437 | 0.26292 | 0.25289 | 0.24401
| 0.65 | 0.5901 | 0.4285 | 0.37151 | 0.33626 | 0.31166 | 0.29257 | 0.27732 | 0.26433 | 0.2532 | 0.24357 | 0.23501 |  | 0.65 | 0.5901 | 0.4285 | 0.37151 | 0.33626 | 0.31166 | 0.29257 | 0.27732 | 0.26433 | 0.2532 | 0.24357 | 0.23501
| 0.7 | 0.58721 | 0.41788 | 0.36024 | 0.32541 | 0.30126 | 0.28287 | 0.268 | 0.25539 | 0.24464 | 0.23531 | 0.22703 |  | 0.7 | 0.58721 | 0.41788 | 0.36024 | 0.32541 | 0.30126 | 0.28287 | 0.268 | 0.25539 | 0.24464 | 0.23531 | 0.22703
| 0.75 | 0.58504 | 0.40829 | 0.35003 | 0.31547 | 0.29192 | 0.274 | 0.25944 | 0.24739 | 0.23686 | 0.22773 | 0.21965 |  | 0.75 | 0.58504 | 0.40829 | 0.35003 | 0.31547 | 0.29192 | 0.274 | 0.25944 | 0.24739 | 0.23686 | 0.22773 | 0.21965
| 0.8 | 0.58274 | 0.39928 | 0.34047 | 0.30652 | 0.2835 | 0.26588 | 0.25172 | 0.23994 | 0.22965 | 0.22084 | 0.21298 |  | 0.8 | 0.58274 | 0.39928 | 0.34047 | 0.30652 | 0.2835 | 0.26588 | 0.25172 | 0.23994 | 0.22965 | 0.22084 | 0.21298
| 0.85 | 0.58116 | 0.39082 | 0.33184 | 0.29836 | 0.27572 | 0.2586 | 0.24477 | 0.23315 | 0.22335 | 0.21456 | 0.20699 |  | 0.85 | 0.58116 | 0.39082 | 0.33184 | 0.29836 | 0.27572 | 0.2586 | 0.24477 | 0.23315 | 0.22335 | 0.21456 | 0.20699
| 0.9 | 0.57978 | 0.38293 | 0.32354 | 0.29063 | 0.26852 | 0.25185 | 0.23837 | 0.22695 | 0.21722 | 0.20891 | 0.20135 |  | 0.9 | 0.57978 | 0.38293 | 0.32354 | 0.29063 | 0.26852 | 0.25185 | 0.23837 | 0.22695 | 0.21722 | 0.20891 | 0.20135
| 0.95 | 0.57808 | 0.37541 | 0.31608 | 0.28367 | 0.26189 | 0.24548 | 0.23224 | 0.22127 | 0.21187 | 0.20353 | 0.19624 |  | 0.95 | 0.57808 | 0.37541 | 0.31608 | 0.28367 | 0.26189 | 0.24548 | 0.23224 | 0.22127 | 0.21187 | 0.20353 | 0.19624
| 1 | 0.57694 | 0.36819 | 0.30903 | 0.277 | 0.25577 | 0.23975 | 0.2267 | 0.21597 | 0.20669 | 0.19858 | 0.19138 |  | 1 | 0.57694 | 0.36819 | 0.30903 | 0.277 | 0.25577 | 0.23975 | 0.2267 | 0.21597 | 0.20669 | 0.19858 | 0.19138
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.010371 | 0.011048 | 0.011623 | 0.012155 | 0.012449 | 0.012692 | 0.01291 | 0.013011 | 0.013148 | 0.013162 | 0.013152 |  | 0.05 | 0.010371 | 0.011048 | 0.011623 | 0.012155 | 0.012449 | 0.012692 | 0.01291 | 0.013011 | 0.013148 | 0.013162 | 0.013152
| 0.1 | 0.0097078 | 0.011363 | 0.011944 | 0.012255 | 0.012504 | 0.012622 | 0.012642 | 0.012602 | 0.01252 | 0.012426 | 0.012362 |  | 0.1 | 0.0097078 | 0.011363 | 0.011944 | 0.012255 | 0.012504 | 0.012622 | 0.012642 | 0.012602 | 0.01252 | 0.012426 | 0.012362
| 0.15 | 0.0080403 | 0.010985 | 0.011535 | 0.011925 | 0.012137 | 0.012239 | 0.012224 | 0.012097 | 0.01193 | 0.01177 | 0.011578 |  | 0.15 | 0.0080403 | 0.010985 | 0.011535 | 0.011925 | 0.012137 | 0.012239 | 0.012224 | 0.012097 | 0.01193 | 0.01177 | 0.011578
| 0.2 | 0.0067654 | 0.010449 | 0.011243 | 0.011725 | 0.011923 | 0.01197 | 0.01178 | 0.011558 | 0.011349 | 0.011111 | 0.010809 |  | 0.2 | 0.0067654 | 0.010449 | 0.011243 | 0.011725 | 0.011923 | 0.01197 | 0.01178 | 0.011558 | 0.011349 | 0.011111 | 0.010809
| 0.25 | 0.0058163 | 0.010085 | 0.011116 | 0.011656 | 0.011719 | 0.011536 | 0.011294 | 0.011013 | 0.010726 | 0.010429 | 0.010161 |  | 0.25 | 0.0058163 | 0.010085 | 0.011116 | 0.011656 | 0.011719 | 0.011536 | 0.011294 | 0.011013 | 0.010726 | 0.010429 | 0.010161
| 0.3 | 0.0050793 | 0.0098301 | 0.011085 | 0.011475 | 0.011397 | 0.011151 | 0.010827 | 0.01047 | 0.010183 | 0.0098784 | 0.0095737 |  | 0.3 | 0.0050793 | 0.0098301 | 0.011085 | 0.011475 | 0.011397 | 0.011151 | 0.010827 | 0.01047 | 0.010183 | 0.0098784 | 0.0095737
| 0.35 | 0.0044253 | 0.0096733 | 0.011007 | 0.011275 | 0.01106 | 0.010716 | 0.010383 | 0.010004 | 0.0096359 | 0.0093246 | 0.0090674 |  | 0.35 | 0.0044253 | 0.0096733 | 0.011007 | 0.011275 | 0.01106 | 0.010716 | 0.010383 | 0.010004 | 0.0096359 | 0.0093246 | 0.0090674
| 0.4 | 0.0040727 | 0.009604 | 0.010937 | 0.01101 | 0.010716 | 0.010299 | 0.0099006 | 0.0095187 | 0.0091796 | 0.0089031 | 0.0085952 |  | 0.4 | 0.0040727 | 0.009604 | 0.010937 | 0.01101 | 0.010716 | 0.010299 | 0.0099006 | 0.0095187 | 0.0091796 | 0.0089031 | 0.0085952
| 0.45 | 0.0036295 | 0.0095718 | 0.010801 | 0.010742 | 0.010394 | 0.0099377 | 0.009511 | 0.0091492 | 0.0088102 | 0.0084743 | 0.0082257 |  | 0.45 | 0.0036295 | 0.0095718 | 0.010801 | 0.010742 | 0.010394 | 0.0099377 | 0.009511 | 0.0091492 | 0.0088102 | 0.0084743 | 0.0082257
| 0.5 | 0.0033117 | 0.0095594 | 0.010683 | 0.010463 | 0.010032 | 0.0095734 | 0.0091546 | 0.0087493 | 0.0084311 | 0.0081391 | 0.0078799 |  | 0.5 | 0.0033117 | 0.0095594 | 0.010683 | 0.010463 | 0.010032 | 0.0095734 | 0.0091546 | 0.0087493 | 0.0084311 | 0.0081391 | 0.0078799
| 0.55 | 0.0030649 | 0.0095933 | 0.010504 | 0.010191 | 0.00972 | 0.0092467 | 0.0087875 | 0.0084432 | 0.0080993 | 0.007828 | 0.0075624 |  | 0.55 | 0.0030649 | 0.0095933 | 0.010504 | 0.010191 | 0.00972 | 0.0092467 | 0.0087875 | 0.0084432 | 0.0080993 | 0.007828 | 0.0075624
| 0.6 | 0.0028586 | 0.0095482 | 0.010356 | 0.0099691 | 0.0094471 | 0.0089126 | 0.0084999 | 0.008164 | 0.0078482 | 0.0075418 | 0.007313 |  | 0.6 | 0.0028586 | 0.0095482 | 0.010356 | 0.0099691 | 0.0094471 | 0.0089126 | 0.0084999 | 0.008164 | 0.0078482 | 0.0075418 | 0.007313
| 0.65 | 0.0027017 | 0.0096053 | 0.010179 | 0.0097016 | 0.0091492 | 0.0086786 | 0.0082499 | 0.0078842 | 0.0076068 | 0.0073073 | 0.0070743 |  | 0.65 | 0.0027017 | 0.0096053 | 0.010179 | 0.0097016 | 0.0091492 | 0.0086786 | 0.0082499 | 0.0078842 | 0.0076068 | 0.0073073 | 0.0070743
| 0.7 | 0.0025401 | 0.0095914 | 0.010011 | 0.0094665 | 0.0088809 | 0.0084137 | 0.0080185 | 0.0076497 | 0.0073559 | 0.0070712 | 0.0068448 |  | 0.7 | 0.0025401 | 0.0095914 | 0.010011 | 0.0094665 | 0.0088809 | 0.0084137 | 0.0080185 | 0.0076497 | 0.0073559 | 0.0070712 | 0.0068448
| 0.75 | 0.0023255 | 0.0095729 | 0.0098128 | 0.0092048 | 0.0086626 | 0.0081569 | 0.0077841 | 0.0074418 | 0.0071335 | 0.0068663 | 0.0066387 |  | 0.75 | 0.0023255 | 0.0095729 | 0.0098128 | 0.0092048 | 0.0086626 | 0.0081569 | 0.0077841 | 0.0074418 | 0.0071335 | 0.0068663 | 0.0066387
| 0.8 | 0.0022997 | 0.0095707 | 0.0096924 | 0.0090188 | 0.0084437 | 0.0079463 | 0.0075656 | 0.0072368 | 0.0069426 | 0.0067112 | 0.0064633 |  | 0.8 | 0.0022997 | 0.0095707 | 0.0096924 | 0.0090188 | 0.0084437 | 0.0079463 | 0.0075656 | 0.0072368 | 0.0069426 | 0.0067112 | 0.0064633
| 0.85 | 0.0021095 | 0.0095215 | 0.0094519 | 0.0087945 | 0.0082173 | 0.007777 | 0.0074047 | 0.0070767 | 0.0067752 | 0.006533 | 0.0062966 |  | 0.85 | 0.0021095 | 0.0095215 | 0.0094519 | 0.0087945 | 0.0082173 | 0.007777 | 0.0074047 | 0.0070767 | 0.0067752 | 0.006533 | 0.0062966
| 0.9 | 0.002 | 0.0094951 | 0.0093083 | 0.0086063 | 0.0080459 | 0.0076112 | 0.0072064 | 0.0068973 | 0.0066317 | 0.0063518 | 0.0061675 |  | 0.9 | 0.002 | 0.0094951 | 0.0093083 | 0.0086063 | 0.0080459 | 0.0076112 | 0.0072064 | 0.0068973 | 0.0066317 | 0.0063518 | 0.0061675
| 0.95 | 0.0019554 | 0.009469 | 0.0091854 | 0.0084509 | 0.0078447 | 0.0074305 | 0.0070929 | 0.0067445 | 0.0064458 | 0.0062421 | 0.0060212 |  | 0.95 | 0.0019554 | 0.009469 | 0.0091854 | 0.0084509 | 0.0078447 | 0.0074305 | 0.0070929 | 0.0067445 | 0.0064458 | 0.0062421 | 0.0060212
| 1 | 0.0018596 | 0.009361 | 0.0089822 | 0.0082503 | 0.0077217 | 0.007279 | 0.0069166 | 0.0066014 | 0.0063198 | 0.0060887 | 0.0058683 |  | 1 | 0.0018596 | 0.009361 | 0.0089822 | 0.0082503 | 0.0077217 | 0.007279 | 0.0069166 | 0.0066014 | 0.0063198 | 0.0060887 | 0.0058683
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0030947 | 0.0033905 | 0.0036016 | 0.003756 | 0.0038818 | 0.0039747 | 0.0040512 | 0.0041035 | 0.004142 | 0.0041724 | 0.0041868 |  | 0.05 | 0.0030947 | 0.0033905 | 0.0036016 | 0.003756 | 0.0038818 | 0.0039747 | 0.0040512 | 0.0041035 | 0.004142 | 0.0041724 | 0.0041868
| 0.1 | 0.0028507 | 0.0035011 | 0.0037201 | 0.0038219 | 0.003882 | 0.0039252 | 0.0039467 | 0.0039486 | 0.0039368 | 0.0039142 | 0.0038881 |  | 0.1 | 0.0028507 | 0.0035011 | 0.0037201 | 0.0038219 | 0.003882 | 0.0039252 | 0.0039467 | 0.0039486 | 0.0039368 | 0.0039142 | 0.0038881
| 0.15 | 0.0023995 | 0.003369 | 0.0035717 | 0.0036797 | 0.0037436 | 0.0037744 | 0.0037674 | 0.0037464 | 0.0037071 | 0.0036556 | 0.0036029 |  | 0.15 | 0.0023995 | 0.003369 | 0.0035717 | 0.0036797 | 0.0037436 | 0.0037744 | 0.0037674 | 0.0037464 | 0.0037071 | 0.0036556 | 0.0036029
| 0.2 | 0.0020104 | 0.0032269 | 0.0034529 | 0.0035949 | 0.003647 | 0.0036497 | 0.0036171 | 0.003564 | 0.0035015 | 0.003434 | 0.0033704 |  | 0.2 | 0.0020104 | 0.0032269 | 0.0034529 | 0.0035949 | 0.003647 | 0.0036497 | 0.0036171 | 0.003564 | 0.0035015 | 0.003434 | 0.0033704
| 0.25 | 0.0017339 | 0.0031058 | 0.0033837 | 0.0035341 | 0.0035591 | 0.0035284 | 0.0034645 | 0.0033918 | 0.0033114 | 0.0032346 | 0.0031596 |  | 0.25 | 0.0017339 | 0.0031058 | 0.0033837 | 0.0035341 | 0.0035591 | 0.0035284 | 0.0034645 | 0.0033918 | 0.0033114 | 0.0032346 | 0.0031596
| 0.3 | 0.0015226 | 0.0030245 | 0.0033436 | 0.0034686 | 0.0034634 | 0.0033973 | 0.0033175 | 0.0032233 | 0.0031364 | 0.0030535 | 0.0029754 |  | 0.3 | 0.0015226 | 0.0030245 | 0.0033436 | 0.0034686 | 0.0034634 | 0.0033973 | 0.0033175 | 0.0032233 | 0.0031364 | 0.0030535 | 0.0029754
| 0.35 | 0.0013491 | 0.0029679 | 0.0033148 | 0.0033982 | 0.0033573 | 0.0032736 | 0.0031712 | 0.0030714 | 0.0029812 | 0.0028924 | 0.0028122 |  | 0.35 | 0.0013491 | 0.0029679 | 0.0033148 | 0.0033982 | 0.0033573 | 0.0032736 | 0.0031712 | 0.0030714 | 0.0029812 | 0.0028924 | 0.0028122
| 0.4 | 0.0012118 | 0.0029173 | 0.0032823 | 0.0033239 | 0.0032513 | 0.0031474 | 0.0030426 | 0.0029385 | 0.0028399 | 0.0027511 | 0.002673 |  | 0.4 | 0.0012118 | 0.0029173 | 0.0032823 | 0.0033239 | 0.0032513 | 0.0031474 | 0.0030426 | 0.0029385 | 0.0028399 | 0.0027511 | 0.002673
| 0.45 | 0.0011069 | 0.0028959 | 0.0032462 | 0.0032469 | 0.0031478 | 0.0030309 | 0.0029177 | 0.0028117 | 0.0027199 | 0.0026264 | 0.0025474 |  | 0.45 | 0.0011069 | 0.0028959 | 0.0032462 | 0.0032469 | 0.0031478 | 0.0030309 | 0.0029177 | 0.0028117 | 0.0027199 | 0.0026264 | 0.0025474
| 0.5 | 0.0010131 | 0.0028839 | 0.0031967 | 0.0031671 | 0.0030523 | 0.0029268 | 0.0028049 | 0.0027006 | 0.0026037 | 0.002523 | 0.0024408 |  | 0.5 | 0.0010131 | 0.0028839 | 0.0031967 | 0.0031671 | 0.0030523 | 0.0029268 | 0.0028049 | 0.0027006 | 0.0026037 | 0.002523 | 0.0024408
| 0.55 | 0.00093251 | 0.0028792 | 0.0031552 | 0.0030905 | 0.0029585 | 0.0028245 | 0.0027079 | 0.0025983 | 0.0025095 | 0.0024248 | 0.002345 |  | 0.55 | 0.00093251 | 0.0028792 | 0.0031552 | 0.0030905 | 0.0029585 | 0.0028245 | 0.0027079 | 0.0025983 | 0.0025095 | 0.0024248 | 0.002345
| 0.6 | 0.00087599 | 0.0028718 | 0.0031052 | 0.0030138 | 0.002868 | 0.0027333 | 0.0026187 | 0.0025146 | 0.0024165 | 0.0023351 | 0.0022619 |  | 0.6 | 0.00087599 | 0.0028718 | 0.0031052 | 0.0030138 | 0.002868 | 0.0027333 | 0.0026187 | 0.0025146 | 0.0024165 | 0.0023351 | 0.0022619
| 0.65 | 0.0008154 | 0.0028675 | 0.0030528 | 0.0029417 | 0.0027874 | 0.0026509 | 0.0025314 | 0.0024327 | 0.0023371 | 0.0022589 | 0.0021854 |  | 0.65 | 0.0008154 | 0.0028675 | 0.0030528 | 0.0029417 | 0.0027874 | 0.0026509 | 0.0025314 | 0.0024327 | 0.0023371 | 0.0022589 | 0.0021854
| 0.7 | 0.00077263 | 0.0028664 | 0.0030049 | 0.0028675 | 0.0027126 | 0.0025771 | 0.0024586 | 0.0023577 | 0.0022702 | 0.0021886 | 0.0021159 |  | 0.7 | 0.00077263 | 0.0028664 | 0.0030049 | 0.0028675 | 0.0027126 | 0.0025771 | 0.0024586 | 0.0023577 | 0.0022702 | 0.0021886 | 0.0021159
| 0.75 | 0.00072498 | 0.0028603 | 0.0029504 | 0.0027983 | 0.0026377 | 0.0025011 | 0.0023912 | 0.0022879 | 0.0022022 | 0.0021259 | 0.0020572 |  | 0.75 | 0.00072498 | 0.0028603 | 0.0029504 | 0.0027983 | 0.0026377 | 0.0025011 | 0.0023912 | 0.0022879 | 0.0022022 | 0.0021259 | 0.0020572
| 0.8 | 0.00068626 | 0.0028467 | 0.0029067 | 0.0027327 | 0.0025767 | 0.0024389 | 0.0023259 | 0.00223 | 0.0021423 | 0.0020668 | 0.0019992 |  | 0.8 | 0.00068626 | 0.0028467 | 0.0029067 | 0.0027327 | 0.0025767 | 0.0024389 | 0.0023259 | 0.00223 | 0.0021423 | 0.0020668 | 0.0019992
| 0.85 | 0.00065868 | 0.0028385 | 0.0028549 | 0.0026766 | 0.0025119 | 0.0023825 | 0.002267 | 0.0021716 | 0.0020858 | 0.0020148 | 0.0019451 |  | 0.85 | 0.00065868 | 0.0028385 | 0.0028549 | 0.0026766 | 0.0025119 | 0.0023825 | 0.002267 | 0.0021716 | 0.0020858 | 0.0020148 | 0.0019451
| 0.9 | 0.00062214 | 0.0028272 | 0.0028035 | 0.0026138 | 0.0024547 | 0.0023252 | 0.0022129 | 0.0021198 | 0.002037 | 0.0019631 | 0.0018944 |  | 0.9 | 0.00062214 | 0.0028272 | 0.0028035 | 0.0026138 | 0.0024547 | 0.0023252 | 0.0022129 | 0.0021198 | 0.002037 | 0.0019631 | 0.0018944
| 0.95 | 0.00059313 | 0.0028142 | 0.0027627 | 0.0025641 | 0.002404 | 0.002272 | 0.0021677 | 0.00207 | 0.0019854 | 0.0019166 | 0.0018518 |  | 0.95 | 0.00059313 | 0.0028142 | 0.0027627 | 0.0025641 | 0.002404 | 0.002272 | 0.0021677 | 0.00207 | 0.0019854 | 0.0019166 | 0.0018518
| 1 | 0.00057426 | 0.0027936 | 0.0027146 | 0.0025129 | 0.0023532 | 0.0022254 | 0.0021165 | 0.0020267 | 0.0019446 | 0.0018737 | 0.0018117 |  | 1 | 0.00057426 | 0.0027936 | 0.0027146 | 0.0025129 | 0.0023532 | 0.0022254 | 0.0021165 | 0.0020267 | 0.0019446 | 0.0018737 | 0.0018117
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | [12 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 0 to 1
| 0.05 | 1.3693 | 1.7383 | 2.0169 | 2.2377 | 2.4086 | 2.5474 | 2.6516 | 2.7488 | 2.8227 | 2.8845 | 2.9363 |  | 0.05 | 1.3693 | 1.7383 | 2.0169 | 2.2377 | 2.4086 | 2.5474 | 2.6516 | 2.7488 | 2.8227 | 2.8845 | 2.9363
| 0.1 | 1.2795 | 2.0627 | 2.6018 | 2.9995 | 3.3024 | 3.5354 | 3.7053 | 3.9088 | 3.9562 | 4.0733 | 4.1103 |  | 0.1 | 1.2795 | 2.0627 | 2.6018 | 2.9995 | 3.3024 | 3.5354 | 3.7053 | 3.9088 | 3.9562 | 4.0733 | 4.1103
| 0.15 | 1.203 | 2.3404 | 3.0875 | 3.6296 | 4.0316 | 4.3289 | 4.6368 | 4.7077 | 4.8051 | 4.96 | 4.9824 |  | 0.15 | 1.203 | 2.3404 | 3.0875 | 3.6296 | 4.0316 | 4.3289 | 4.6368 | 4.7077 | 4.8051 | 4.96 | 4.9824
| 0.2 | 1.1472 | 2.588 | 3.5276 | 4.1523 | 4.6524 | 5.0038 | 5.2423 | 5.455 | 5.589 | 5.7071 | 5.7951 |  | 0.2 | 1.1472 | 2.588 | 3.5276 | 4.1523 | 4.6524 | 5.0038 | 5.2423 | 5.455 | 5.589 | 5.7071 | 5.7951
| 0.25 | 1.1128 | 2.8225 | 3.8457 | 4.675 | 5.1976 | 5.5778 | 5.8613 | 6.079 | 6.2549 | 6.3741 | 6.4761 |  | 0.25 | 1.1128 | 2.8225 | 3.8457 | 4.675 | 5.1976 | 5.5778 | 5.8613 | 6.079 | 6.2549 | 6.3741 | 6.4761
| 0.3 | 1.0819 | 3.0789 | 4.2835 | 5.1058 | 5.6778 | 6.1042 | 6.4073 | 6.6523 | 6.8334 | 6.9778 | 7.0648 |  | 0.3 | 1.0819 | 3.0789 | 4.2835 | 5.1058 | 5.6778 | 6.1042 | 6.4073 | 6.6523 | 6.8334 | 6.9778 | 7.0648
| 0.35 | 1.0665 | 3.2706 | 4.6135 | 5.4996 | 6.1159 | 6.5773 | 6.9115 | 7.1699 | 7.3713 | 7.5249 | 7.6426 |  | 0.35 | 1.0665 | 3.2706 | 4.6135 | 5.4996 | 6.1159 | 6.5773 | 6.9115 | 7.1699 | 7.3713 | 7.5249 | 7.6426
| 0.4 | 1.0486 | 3.6173 | 4.9136 | 5.8588 | 6.5151 | 7.0128 | 7.375 | 7.6597 | 7.8667 | 8.0298 | 8.154 |  | 0.4 | 1.0486 | 3.6173 | 4.9136 | 5.8588 | 6.5151 | 7.0128 | 7.375 | 7.6597 | 7.8667 | 8.0298 | 8.154
| 0.45 | 1.0301 | 3.6807 | 5.1645 | 6.1942 | 6.903 | 7.4235 | 7.812 | 8.1009 | 8.3384 | 8.5073 | 8.6367 |  | 0.45 | 1.0301 | 3.6807 | 5.1645 | 6.1942 | 6.903 | 7.4235 | 7.812 | 8.1009 | 8.3384 | 8.5073 | 8.6367
| 0.5 | 1.0262 | 3.7441 | 5.4557 | 6.5137 | 7.2519 | 7.8039 | 8.2192 | 8.5317 | 8.7664 | 8.9611 | 9.0977 |  | 0.5 | 1.0262 | 3.7441 | 5.4557 | 6.5137 | 7.2519 | 7.8039 | 8.2192 | 8.5317 | 8.7664 | 8.9611 | 9.0977
| 0.55 | 1.0131 | 4.0039 | 5.7263 | 6.8136 | 7.5915 | 8.1699 | 8.61 | 8.9381 | 9.1902 | 9.3886 | 9.5342 |  | 0.55 | 1.0131 | 4.0039 | 5.7263 | 6.8136 | 7.5915 | 8.1699 | 8.61 | 8.9381 | 9.1902 | 9.3886 | 9.5342
| 0.6 | 1.0137 | 4.2355 | 5.9558 | 7.0962 | 7.9104 | 8.5169 | 8.9783 | 9.3272 | 9.5943 | 9.799 | 9.9502 |  | 0.6 | 1.0137 | 4.2355 | 5.9558 | 7.0962 | 7.9104 | 8.5169 | 8.9783 | 9.3272 | 9.5943 | 9.799 | 9.9502
| 0.65 | 1.0025 | 4.3739 | 6.1811 | 7.3602 | 8.2175 | 8.8528 | 9.3367 | 9.6984 | 9.9775 | 10.1949 | 10.3554 |  | 0.65 | 1.0025 | 4.3739 | 6.1811 | 7.3602 | 8.2175 | 8.8528 | 9.3367 | 9.6984 | 9.9775 | 10.1949 | 10.3554
| 0.7 | 1.0019 | 4.5631 | 6.3965 | 7.6204 | 8.5125 | 9.1793 | 9.6818 | 10.0624 | 10.3532 | 10.5798 | 10.7376 |  | 0.7 | 1.0019 | 4.5631 | 6.3965 | 7.6204 | 8.5125 | 9.1793 | 9.6818 | 10.0624 | 10.3532 | 10.5798 | 10.7376
| 0.75 | 0.99266 | 4.7145 | 6.6174 | 7.8774 | 8.7962 | 9.4854 | 10.0086 | 10.4125 | 10.7103 | 10.9409 | 11.1086 |  | 0.75 | 0.99266 | 4.7145 | 6.6174 | 7.8774 | 8.7962 | 9.4854 | 10.0086 | 10.4125 | 10.7103 | 10.9409 | 11.1086
| 0.8 | 0.99448 | 4.8611 | 6.8133 | 8.1195 | 9.0699 | 9.7875 | 10.3269 | 10.7457 | 11.0439 | 11.2901 | 11.4691 |  | 0.8 | 0.99448 | 4.8611 | 6.8133 | 8.1195 | 9.0699 | 9.7875 | 10.3269 | 10.7457 | 11.0439 | 11.2901 | 11.4691
| 0.85 | 0.98648 | 4.9966 | 7.0077 | 8.3598 | 9.3491 | 10.0823 | 10.6439 | 11.059 | 11.3943 | 11.6347 | 11.8164 |  | 0.85 | 0.98648 | 4.9966 | 7.0077 | 8.3598 | 9.3491 | 10.0823 | 10.6439 | 11.059 | 11.3943 | 11.6347 | 11.8164
| 0.9 | 0.98056 | 5.1335 | 7.1948 | 8.583 | 9.6057 | 10.3702 | 10.9511 | 11.3755 | 11.7111 | 11.9653 | 12.1526 |  | 0.9 | 0.98056 | 5.1335 | 7.1948 | 8.583 | 9.6057 | 10.3702 | 10.9511 | 11.3755 | 11.7111 | 11.9653 | 12.1526
| 0.95 | 0.98283 | 5.2649 | 7.3806 | 8.8049 | 9.8608 | 10.6409 | 11.2375 | 11.6855 | 12.0378 | 12.2875 | 12.4866 |  | 0.95 | 0.98283 | 5.2649 | 7.3806 | 8.8049 | 9.8608 | 10.6409 | 11.2375 | 11.6855 | 12.0378 | 12.2875 | 12.4866
| 1 | 0.97758 | 5.4087 | 7.5558 | 9.0166 | 10.1066 | 10.9154 | 11.5235 | 11.9871 | 12.3342 | 12.603 | 12.7936 |  | 1 | 0.97758 | 5.4087 | 7.5558 | 9.0166 | 10.1066 | 10.9154 | 11.5235 | 11.9871 | 12.3342 | 12.603 | 12.7936
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.027299 | 0.025175 | 0.026181 | 0.027245 | 0.031641 | 0.033309 | 0.034403 | 0.038584 | 0.041617 | 0.042893 | 0.046612 |  | 0.05 | 0.027299 | 0.025175 | 0.026181 | 0.027245 | 0.031641 | 0.033309 | 0.034403 | 0.038584 | 0.041617 | 0.042893 | 0.046612
| 0.1 | 0.028088 | 0.036426 | 0.047094 | 0.04799 | 0.052027 | 0.054858 | 0.061699 | 0.064867 | 0.069618 | 0.076052 | 0.077295 |  | 0.1 | 0.028088 | 0.036426 | 0.047094 | 0.04799 | 0.052027 | 0.054858 | 0.061699 | 0.064867 | 0.069618 | 0.076052 | 0.077295
| 0.15 | 0.022838 | 0.041492 | 0.058385 | 0.063236 | 0.072413 | 0.076407 | 0.088994 | 0.091149 | 0.09762 | 0.1052 | 0.10564 |  | 0.15 | 0.022838 | 0.041492 | 0.058385 | 0.063236 | 0.072413 | 0.076407 | 0.088994 | 0.091149 | 0.09762 | 0.1052 | 0.10564
| 0.2 | 0.016339 | 0.046559 | 0.068437 | 0.081238 | 0.094783 | 0.10612 | 0.11504 | 0.11743 | 0.12562 | 0.13435 | 0.13398 |  | 0.2 | 0.016339 | 0.046559 | 0.068437 | 0.081238 | 0.094783 | 0.10612 | 0.11504 | 0.11743 | 0.12562 | 0.13435 | 0.13398
| 0.25 | 0.010429 | 0.051625 | 0.078489 | 0.095644 | 0.11723 | 0.12844 | 0.13658 | 0.14371 | 0.15362 | 0.15562 | 0.15718 |  | 0.25 | 0.010429 | 0.051625 | 0.078489 | 0.095644 | 0.11723 | 0.12844 | 0.13658 | 0.14371 | 0.15362 | 0.15562 | 0.15718
| 0.3 | 0.006884 | 0.056691 | 0.088709 | 0.11236 | 0.13561 | 0.14754 | 0.15812 | 0.17 | 0.17266 | 0.17412 | 0.179 |  | 0.3 | 0.006884 | 0.056691 | 0.088709 | 0.11236 | 0.13561 | 0.14754 | 0.15812 | 0.17 | 0.17266 | 0.17412 | 0.179
| 0.35 | 0.0046273 | 0.061758 | 0.10139 | 0.12907 | 0.15366 | 0.16665 | 0.17559 | 0.18287 | 0.18853 | 0.19191 | 0.19386 |  | 0.35 | 0.0046273 | 0.061758 | 0.10139 | 0.12907 | 0.15366 | 0.16665 | 0.17559 | 0.18287 | 0.18853 | 0.19191 | 0.19386
| 0.4 | 0.00023239 | 0.066824 | 0.1193 | 0.14579 | 0.1658 | 0.18094 | 0.19508 | 0.19835 | 0.20387 | 0.21019 | 0.21105 |  | 0.4 | 0.00023239 | 0.066824 | 0.1193 | 0.14579 | 0.1658 | 0.18094 | 0.19508 | 0.19835 | 0.20387 | 0.21019 | 0.21105
| 0.45 | -0.00032594 | 0.069066 | 0.13149 | 0.16148 | 0.17876 | 0.19522 | 0.2077 | 0.21436 | 0.22068 | 0.2221 | 0.22617 |  | 0.45 | -0.00032594 | 0.069066 | 0.13149 | 0.16148 | 0.17876 | 0.19522 | 0.2077 | 0.21436 | 0.22068 | 0.2221 | 0.22617
| 0.5 | -0.0022584 | 0.073401 | 0.14368 | 0.17622 | 0.19418 | 0.20841 | 0.22099 | 0.22649 | 0.23325 | 0.2383 | 0.24063 |  | 0.5 | -0.0022584 | 0.073401 | 0.14368 | 0.17622 | 0.19418 | 0.20841 | 0.22099 | 0.22649 | 0.23325 | 0.2383 | 0.24063
| 0.55 | -0.0040517 | 0.078043 | 0.15002 | 0.18091 | 0.20293 | 0.22096 | 0.2312 | 0.23943 | 0.24633 | 0.25155 | 0.25525 |  | 0.55 | -0.0040517 | 0.078043 | 0.15002 | 0.18091 | 0.20293 | 0.22096 | 0.2312 | 0.23943 | 0.24633 | 0.25155 | 0.25525
| 0.6 | -0.0053788 | 0.083495 | 0.15449 | 0.19091 | 0.21426 | 0.23076 | 0.24273 | 0.25255 | 0.25815 | 0.26299 | 0.26833 |  | 0.6 | -0.0053788 | 0.083495 | 0.15449 | 0.19091 | 0.21426 | 0.23076 | 0.24273 | 0.25255 | 0.25815 | 0.26299 | 0.26833
| 0.65 | -0.0066564 | 0.087553 | 0.16201 | 0.2006 | 0.22417 | 0.24286 | 0.25573 | 0.26393 | 0.27118 | 0.27622 | 0.28125 |  | 0.65 | -0.0066564 | 0.087553 | 0.16201 | 0.2006 | 0.22417 | 0.24286 | 0.25573 | 0.26393 | 0.27118 | 0.27622 | 0.28125
| 0.7 | -0.0079171 | 0.099776 | 0.17283 | 0.20891 | 0.2321 | 0.25127 | 0.26684 | 0.27495 | 0.2843 | 0.28957 | 0.29351 |  | 0.7 | -0.0079171 | 0.099776 | 0.17283 | 0.20891 | 0.2321 | 0.25127 | 0.26684 | 0.27495 | 0.2843 | 0.28957 | 0.29351
| 0.75 | -0.0063821 | 0.10666 | 0.17761 | 0.21637 | 0.24208 | 0.26115 | 0.27554 | 0.28658 | 0.2951 | 0.29922 | 0.30493 |  | 0.75 | -0.0063821 | 0.10666 | 0.17761 | 0.21637 | 0.24208 | 0.26115 | 0.27554 | 0.28658 | 0.2951 | 0.29922 | 0.30493
| 0.8 | -0.0094273 | 0.11419 | 0.18582 | 0.22649 | 0.25058 | 0.26994 | 0.28499 | 0.29694 | 0.30417 | 0.31326 | 0.31533 |  | 0.8 | -0.0094273 | 0.11419 | 0.18582 | 0.22649 | 0.25058 | 0.26994 | 0.28499 | 0.29694 | 0.30417 | 0.31326 | 0.31533
| 0.85 | -0.0084187 | 0.1195 | 0.19022 | 0.23096 | 0.26034 | 0.28109 | 0.29637 | 0.30881 | 0.31559 | 0.32402 | 0.3268 |  | 0.85 | -0.0084187 | 0.1195 | 0.19022 | 0.23096 | 0.26034 | 0.28109 | 0.29637 | 0.30881 | 0.31559 | 0.32402 | 0.3268
| 0.9 | -0.0096091 | 0.12481 | 0.19777 | 0.23858 | 0.26782 | 0.2903 | 0.30454 | 0.31841 | 0.32743 | 0.33339 | 0.34162 |  | 0.9 | -0.0096091 | 0.12481 | 0.19777 | 0.23858 | 0.26782 | 0.2903 | 0.30454 | 0.31841 | 0.32743 | 0.33339 | 0.34162
| 0.95 | -0.010207 | 0.1327 | 0.204 | 0.24687 | 0.27484 | 0.29886 | 0.31663 | 0.3287 | 0.33541 | 0.34607 | 0.35056 |  | 0.95 | -0.010207 | 0.1327 | 0.204 | 0.24687 | 0.27484 | 0.29886 | 0.31663 | 0.3287 | 0.33541 | 0.34607 | 0.35056
| 1 | -0.011241 | 0.13982 | 0.21209 | 0.25311 | 0.28435 | 0.30805 | 0.32476 | 0.33661 | 0.34831 | 0.35553 | 0.35949 |  | 1 | -0.011241 | 0.13982 | 0.21209 | 0.25311 | 0.28435 | 0.30805 | 0.32476 | 0.33661 | 0.34831 | 0.35553 | 0.35949
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.00042404 | -0.0087715 | -0.014896 | -0.019104 | -0.022194 | -0.02443 | -0.026477 | -0.027295 | -0.028174 | -0.029125 | -0.02932 |  | 0.05 | 0.00042404 | -0.0087715 | -0.014896 | -0.019104 | -0.022194 | -0.02443 | -0.026477 | -0.027295 | -0.028174 | -0.029125 | -0.02932
| 0.1 | 0.002932 | -0.012981 | -0.022512 | -0.03037 | -0.031858 | -0.036595 | -0.039092 | -0.040716 | -0.041506 | -0.042351 | -0.042148 |  | 0.1 | 0.002932 | -0.012981 | -0.022512 | -0.03037 | -0.031858 | -0.036595 | -0.039092 | -0.040716 | -0.041506 | -0.042351 | -0.042148
| 0.15 | 0.0028208 | -0.017992 | -0.029248 | -0.036707 | -0.041522 | -0.044968 | -0.047846 | -0.049475 | -0.051041 | -0.050905 | -0.052032 |  | 0.15 | 0.0028208 | -0.017992 | -0.029248 | -0.036707 | -0.041522 | -0.044968 | -0.047846 | -0.049475 | -0.051041 | -0.050905 | -0.052032
| 0.2 | 0.0027568 | -0.022518 | -0.035195 | -0.042013 | -0.047127 | -0.051418 | -0.054313 | -0.055606 | -0.057946 | -0.058351 | -0.060057 |  | 0.2 | 0.0027568 | -0.022518 | -0.035195 | -0.042013 | -0.047127 | -0.051418 | -0.054313 | -0.055606 | -0.057946 | -0.058351 | -0.060057
| 0.25 | 0.0021948 | -0.027586 | -0.039593 | -0.047519 | -0.052012 | -0.057944 | -0.06078 | -0.063247 | -0.064313 | -0.065797 | -0.066791 |  | 0.25 | 0.0021948 | -0.027586 | -0.039593 | -0.047519 | -0.052012 | -0.057944 | -0.06078 | -0.063247 | -0.064313 | -0.065797 | -0.066791
| 0.3 | 0.001755 | -0.028491 | -0.043876 | -0.053587 | -0.058278 | -0.062461 | -0.065661 | -0.068354 | -0.070527 | -0.071853 | -0.072843 |  | 0.3 | 0.001755 | -0.028491 | -0.043876 | -0.053587 | -0.058278 | -0.062461 | -0.065661 | -0.068354 | -0.070527 | -0.071853 | -0.072843
| 0.35 | 0.0014784 | -0.03207 | -0.048159 | -0.055414 | -0.062011 | -0.066733 | -0.070789 | -0.073678 | -0.075798 | -0.07739 | -0.078644 |  | 0.35 | 0.0014784 | -0.03207 | -0.048159 | -0.055414 | -0.062011 | -0.066733 | -0.070789 | -0.073678 | -0.075798 | -0.07739 | -0.078644
| 0.4 | 0.00137 | -0.034553 | -0.050403 | -0.05878 | -0.065735 | -0.071435 | -0.075231 | -0.078473 | -0.081047 | -0.082932 | -0.084413 |  | 0.4 | 0.00137 | -0.034553 | -0.050403 | -0.05878 | -0.065735 | -0.071435 | -0.075231 | -0.078473 | -0.081047 | -0.082932 | -0.084413
| 0.45 | 0.0010723 | -0.037412 | -0.05208 | -0.061593 | -0.069348 | -0.07523 | -0.079837 | -0.083247 | -0.086081 | -0.087814 | -0.089544 |  | 0.45 | 0.0010723 | -0.037412 | -0.05208 | -0.061593 | -0.069348 | -0.07523 | -0.079837 | -0.083247 | -0.086081 | -0.087814 | -0.089544
| 0.5 | 0.0009592 | -0.040272 | -0.053756 | -0.064366 | -0.072726 | -0.079577 | -0.084419 | -0.088119 | -0.090646 | -0.092794 | -0.0945 |  | 0.5 | 0.0009592 | -0.040272 | -0.053756 | -0.064366 | -0.072726 | -0.079577 | -0.084419 | -0.088119 | -0.090646 | -0.092794 | -0.0945
| 0.55 | 0.00086283 | -0.04087 | -0.055846 | -0.067322 | -0.076409 | -0.083005 | -0.088301 | -0.09201 | -0.094904 | -0.097275 | -0.099081 |  | 0.55 | 0.00086283 | -0.04087 | -0.055846 | -0.067322 | -0.076409 | -0.083005 | -0.088301 | -0.09201 | -0.094904 | -0.097275 | -0.099081
| 0.6 | 0.0006228 | -0.042454 | -0.058081 | -0.07015 | -0.079359 | -0.086766 | -0.092263 | -0.096221 | -0.099429 | -0.10181 | -0.10353 |  | 0.6 | 0.0006228 | -0.042454 | -0.058081 | -0.07015 | -0.079359 | -0.086766 | -0.092263 | -0.096221 | -0.099429 | -0.10181 | -0.10353
| 0.65 | 0.00061832 | -0.043643 | -0.060149 | -0.073136 | -0.08263 | -0.090115 | -0.096143 | -0.10013 | -0.10343 | -0.10597 | -0.10795 |  | 0.65 | 0.00061832 | -0.043643 | -0.060149 | -0.073136 | -0.08263 | -0.090115 | -0.096143 | -0.10013 | -0.10343 | -0.10597 | -0.10795
| 0.7 | 0.00040261 | -0.04578 | -0.062276 | -0.075423 | -0.085751 | -0.093589 | -0.099737 | -0.10405 | -0.10738 | -0.10973 | -0.11191 |  | 0.7 | 0.00040261 | -0.04578 | -0.062276 | -0.075423 | -0.085751 | -0.093589 | -0.099737 | -0.10405 | -0.10738 | -0.10973 | -0.11191
| 0.75 | 0.00043963 | -0.047079 | -0.064129 | -0.078116 | -0.089024 | -0.097001 | -0.10287 | -0.10787 | -0.11138 | -0.11399 | -0.1157 |  | 0.75 | 0.00043963 | -0.047079 | -0.064129 | -0.078116 | -0.089024 | -0.097001 | -0.10287 | -0.10787 | -0.11138 | -0.11399 | -0.1157
| 0.8 | 0.0004584 | -0.048826 | -0.066123 | -0.081084 | -0.091947 | -0.10018 | -0.10632 | -0.11091 | -0.11486 | -0.11754 | -0.11954 |  | 0.8 | 0.0004584 | -0.048826 | -0.066123 | -0.081084 | -0.091947 | -0.10018 | -0.10632 | -0.11091 | -0.11486 | -0.11754 | -0.11954
| 0.85 | 0.00022448 | -0.049491 | -0.068035 | -0.083189 | -0.09495 | -0.10325 | -0.10979 | -0.11458 | -0.11848 | -0.12102 | -0.12327 |  | 0.85 | 0.00022448 | -0.049491 | -0.068035 | -0.083189 | -0.09495 | -0.10325 | -0.10979 | -0.11458 | -0.11848 | -0.12102 | -0.12327
| 0.9 | 0.00028245 | -0.052035 | -0.070273 | -0.086012 | -0.09764 | -0.10639 | -0.11283 | -0.11788 | -0.12182 | -0.12451 | -0.127 |  | 0.9 | 0.00028245 | -0.052035 | -0.070273 | -0.086012 | -0.09764 | -0.10639 | -0.11283 | -0.11788 | -0.12182 | -0.12451 | -0.127
| 0.95 | 0.00028203 | -0.052698 | -0.071885 | -0.088295 | -0.10016 | -0.10938 | -0.11564 | -0.12119 | -0.12508 | -0.128 | -0.13025 |  | 0.95 | 0.00028203 | -0.052698 | -0.071885 | -0.088295 | -0.10016 | -0.10938 | -0.11564 | -0.12119 | -0.12508 | -0.128 | -0.13025
| 1 | 0.00013357 | -0.053362 | -0.073954 | -0.090605 | -0.10277 | -0.11204 | -0.11887 | -0.12412 | -0.12818 | -0.13146 | -0.13367 |  | 1 | 0.00013357 | -0.053362 | -0.073954 | -0.090605 | -0.10277 | -0.11204 | -0.11887 | -0.12412 | -0.12818 | -0.13146 | -0.13367
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS2_LS< (hidden)
If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0358 | 1.0722 | 1.1008 | 1.1191 | 1.1288 | 1.132 | 1.1306 | 1.1258 | 1.1188 | 1.11 | 1.1002
| 0.1 | 1.0388 | 1.0768 | 1.1241 | 1.1528 | 1.1657 | 1.1688 | 1.1656 | 1.1583 | 1.1484 | 1.1369 | 1.1242
| 0.15 | 1.0287 | 1.0793 | 1.1249 | 1.1598 | 1.1752 | 1.1792 | 1.1763 | 1.169 | 1.1589 | 1.1469 | 1.1337
| 0.2 | 1.0072 | 1.0775 | 1.1268 | 1.1609 | 1.179 | 1.1848 | 1.183 | 1.1761 | 1.166 | 1.1538 | 1.1403
| 0.25 | 0.98246 | 1.0718 | 1.1293 | 1.1611 | 1.1822 | 1.1896 | 1.1883 | 1.1814 | 1.1711 | 1.1586 | 1.1447
| 0.3 | 0.95806 | 1.0652 | 1.1297 | 1.1623 | 1.1853 | 1.1934 | 1.1921 | 1.1851 | 1.1746 | 1.1618 | 1.1476
| 0.35 | 0.93543 | 1.0587 | 1.1289 | 1.1636 | 1.1878 | 1.1961 | 1.1949 | 1.1877 | 1.177 | 1.1641 | 1.1498
| 0.4 | 0.91499 | 1.0527 | 1.1274 | 1.1646 | 1.1897 | 1.1981 | 1.1969 | 1.1897 | 1.179 | 1.166 | 1.1516
| 0.45 | 0.89675 | 1.0474 | 1.1257 | 1.1656 | 1.1911 | 1.1996 | 1.1984 | 1.1914 | 1.1806 | 1.1676 | 1.1532
| 0.5 | 0.88053 | 1.0426 | 1.1238 | 1.1664 | 1.1921 | 1.2009 | 1.1998 | 1.1928 | 1.1821 | 1.169 | 1.1545
| 0.55 | 0.86611 | 1.0383 | 1.1219 | 1.1669 | 1.1929 | 1.2019 | 1.201 | 1.1941 | 1.1833 | 1.1702 | 1.1556
| 0.6 | 0.85327 | 1.0345 | 1.1201 | 1.1673 | 1.1936 | 1.2029 | 1.2021 | 1.1952 | 1.1844 | 1.1712 | 1.1565
| 0.65 | 0.84179 | 1.031 | 1.1185 | 1.1675 | 1.1943 | 1.2038 | 1.2031 | 1.1961 | 1.1853 | 1.172 | 1.1573
| 0.7 | 0.8315 | 1.0278 | 1.117 | 1.1677 | 1.1949 | 1.2046 | 1.204 | 1.197 | 1.1861 | 1.1728 | 1.1581
| 0.75 | 0.82224 | 1.0249 | 1.1158 | 1.168 | 1.1955 | 1.2054 | 1.2047 | 1.1977 | 1.1868 | 1.1735 | 1.1587
| 0.8 | 0.81386 | 1.0223 | 1.1148 | 1.1682 | 1.1961 | 1.206 | 1.2053 | 1.1983 | 1.1874 | 1.1741 | 1.1593
| 0.85 | 0.80626 | 1.0198 | 1.114 | 1.1684 | 1.1966 | 1.2066 | 1.2059 | 1.1989 | 1.188 | 1.1747 | 1.1599
| 0.9 | 0.79934 | 1.0175 | 1.1134 | 1.1687 | 1.1971 | 1.2071 | 1.2065 | 1.1995 | 1.1886 | 1.1752 | 1.1603
| 0.95 | 0.79302 | 1.0153 | 1.1129 | 1.169 | 1.1975 | 1.2075 | 1.207 | 1.2 | 1.1891 | 1.1757 | 1.1608
| 1 | 0.78722 | 1.0133 | 1.1127 | 1.1692 | 1.1978 | 1.208 | 1.2074 | 1.2005 | 1.1895 | 1.1761 | 1.1612
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 0.85541 | 0.83294 | 0.81054 | 0.78911 | 0.76857 | 0.74909 | 0.73127 | 0.7138 | 0.69751 | 0.6822 | 0.66756
| 0.1 | 0.75149 | 0.71499 | 0.6847 | 0.6582 | 0.63437 | 0.61269 | 0.59281 | 0.57444 | 0.55731 | 0.54168 | 0.52707
| 0.15 | 0.69805 | 0.64629 | 0.61181 | 0.58343 | 0.55836 | 0.53564 | 0.51554 | 0.49703 | 0.48015 | 0.465 | 0.45125
| 0.2 | 0.66683 | 0.59988 | 0.56211 | 0.5323 | 0.50589 | 0.48282 | 0.46242 | 0.44436 | 0.42827 | 0.41391 | 0.40071
| 0.25 | 0.64602 | 0.5651 | 0.52509 | 0.49317 | 0.46612 | 0.44288 | 0.4229 | 0.4053 | 0.38996 | 0.37632 | 0.36392
| 0.3 | 0.63182 | 0.53759 | 0.49521 | 0.46154 | 0.43404 | 0.41118 | 0.39187 | 0.37493 | 0.36032 | 0.34738 | 0.33571
| 0.35 | 0.62086 | 0.51518 | 0.47011 | 0.43532 | 0.40777 | 0.38533 | 0.36669 | 0.3505 | 0.33649 | 0.32404 | 0.31322
| 0.4 | 0.61291 | 0.49634 | 0.44818 | 0.41286 | 0.38576 | 0.36378 | 0.34568 | 0.33021 | 0.31678 | 0.30505 | 0.29452
| 0.45 | 0.60653 | 0.47969 | 0.42918 | 0.39356 | 0.36662 | 0.34551 | 0.328 | 0.31308 | 0.30035 | 0.28896 | 0.27902
| 0.5 | 0.6011 | 0.46503 | 0.4125 | 0.37665 | 0.35018 | 0.32954 | 0.31269 | 0.29844 | 0.28601 | 0.2753 | 0.26575
| 0.55 | 0.59691 | 0.45179 | 0.39727 | 0.36161 | 0.33577 | 0.31572 | 0.29946 | 0.28563 | 0.27374 | 0.26344 | 0.2541
| 0.6 | 0.59305 | 0.43956 | 0.38383 | 0.3483 | 0.32296 | 0.30343 | 0.28765 | 0.27437 | 0.26292 | 0.25289 | 0.24401
| 0.65 | 0.5901 | 0.4285 | 0.37151 | 0.33626 | 0.31166 | 0.29257 | 0.27732 | 0.26433 | 0.2532 | 0.24357 | 0.23501
| 0.7 | 0.58721 | 0.41788 | 0.36024 | 0.32541 | 0.30126 | 0.28287 | 0.268 | 0.25539 | 0.24464 | 0.23531 | 0.22703
| 0.75 | 0.58504 | 0.40829 | 0.35003 | 0.31547 | 0.29192 | 0.274 | 0.25944 | 0.24739 | 0.23686 | 0.22773 | 0.21965
| 0.8 | 0.58274 | 0.39928 | 0.34047 | 0.30652 | 0.2835 | 0.26588 | 0.25172 | 0.23994 | 0.22965 | 0.22084 | 0.21298
| 0.85 | 0.58116 | 0.39082 | 0.33184 | 0.29836 | 0.27572 | 0.2586 | 0.24477 | 0.23315 | 0.22335 | 0.21456 | 0.20699
| 0.9 | 0.57978 | 0.38293 | 0.32354 | 0.29063 | 0.26852 | 0.25185 | 0.23837 | 0.22695 | 0.21722 | 0.20891 | 0.20135
| 0.95 | 0.57808 | 0.37541 | 0.31608 | 0.28367 | 0.26189 | 0.24548 | 0.23224 | 0.22127 | 0.21187 | 0.20353 | 0.19624
| 1 | 0.57694 | 0.36819 | 0.30903 | 0.277 | 0.25577 | 0.23975 | 0.2267 | 0.21597 | 0.20669 | 0.19858 | 0.19138
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.010371 | 0.011048 | 0.011623 | 0.012155 | 0.012449 | 0.012692 | 0.01291 | 0.013011 | 0.013148 | 0.013162 | 0.013152
| 0.1 | 0.0097078 | 0.011363 | 0.011944 | 0.012255 | 0.012504 | 0.012622 | 0.012642 | 0.012602 | 0.01252 | 0.012426 | 0.012362
| 0.15 | 0.0080403 | 0.010985 | 0.011535 | 0.011925 | 0.012137 | 0.012239 | 0.012224 | 0.012097 | 0.01193 | 0.01177 | 0.011578
| 0.2 | 0.0067654 | 0.010449 | 0.011243 | 0.011725 | 0.011923 | 0.01197 | 0.01178 | 0.011558 | 0.011349 | 0.011111 | 0.010809
| 0.25 | 0.0058163 | 0.010085 | 0.011116 | 0.011656 | 0.011719 | 0.011536 | 0.011294 | 0.011013 | 0.010726 | 0.010429 | 0.010161
| 0.3 | 0.0050793 | 0.0098301 | 0.011085 | 0.011475 | 0.011397 | 0.011151 | 0.010827 | 0.01047 | 0.010183 | 0.0098784 | 0.0095737
| 0.35 | 0.0044253 | 0.0096733 | 0.011007 | 0.011275 | 0.01106 | 0.010716 | 0.010383 | 0.010004 | 0.0096359 | 0.0093246 | 0.0090674
| 0.4 | 0.0040727 | 0.009604 | 0.010937 | 0.01101 | 0.010716 | 0.010299 | 0.0099006 | 0.0095187 | 0.0091796 | 0.0089031 | 0.0085952
| 0.45 | 0.0036295 | 0.0095718 | 0.010801 | 0.010742 | 0.010394 | 0.0099377 | 0.009511 | 0.0091492 | 0.0088102 | 0.0084743 | 0.0082257
| 0.5 | 0.0033117 | 0.0095594 | 0.010683 | 0.010463 | 0.010032 | 0.0095734 | 0.0091546 | 0.0087493 | 0.0084311 | 0.0081391 | 0.0078799
| 0.55 | 0.0030649 | 0.0095933 | 0.010504 | 0.010191 | 0.00972 | 0.0092467 | 0.0087875 | 0.0084432 | 0.0080993 | 0.007828 | 0.0075624
| 0.6 | 0.0028586 | 0.0095482 | 0.010356 | 0.0099691 | 0.0094471 | 0.0089126 | 0.0084999 | 0.008164 | 0.0078482 | 0.0075418 | 0.007313
| 0.65 | 0.0027017 | 0.0096053 | 0.010179 | 0.0097016 | 0.0091492 | 0.0086786 | 0.0082499 | 0.0078842 | 0.0076068 | 0.0073073 | 0.0070743
| 0.7 | 0.0025401 | 0.0095914 | 0.010011 | 0.0094665 | 0.0088809 | 0.0084137 | 0.0080185 | 0.0076497 | 0.0073559 | 0.0070712 | 0.0068448
| 0.75 | 0.0023255 | 0.0095729 | 0.0098128 | 0.0092048 | 0.0086626 | 0.0081569 | 0.0077841 | 0.0074418 | 0.0071335 | 0.0068663 | 0.0066387
| 0.8 | 0.0022997 | 0.0095707 | 0.0096924 | 0.0090188 | 0.0084437 | 0.0079463 | 0.0075656 | 0.0072368 | 0.0069426 | 0.0067112 | 0.0064633
| 0.85 | 0.0021095 | 0.0095215 | 0.0094519 | 0.0087945 | 0.0082173 | 0.007777 | 0.0074047 | 0.0070767 | 0.0067752 | 0.006533 | 0.0062966
| 0.9 | 0.002 | 0.0094951 | 0.0093083 | 0.0086063 | 0.0080459 | 0.0076112 | 0.0072064 | 0.0068973 | 0.0066317 | 0.0063518 | 0.0061675
| 0.95 | 0.0019554 | 0.009469 | 0.0091854 | 0.0084509 | 0.0078447 | 0.0074305 | 0.0070929 | 0.0067445 | 0.0064458 | 0.0062421 | 0.0060212
| 1 | 0.0018596 | 0.009361 | 0.0089822 | 0.0082503 | 0.0077217 | 0.007279 | 0.0069166 | 0.0066014 | 0.0063198 | 0.0060887 | 0.0058683
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0030947 | 0.0033905 | 0.0036016 | 0.003756 | 0.0038818 | 0.0039747 | 0.0040512 | 0.0041035 | 0.004142 | 0.0041724 | 0.0041868
| 0.1 | 0.0028507 | 0.0035011 | 0.0037201 | 0.0038219 | 0.003882 | 0.0039252 | 0.0039467 | 0.0039486 | 0.0039368 | 0.0039142 | 0.0038881
| 0.15 | 0.0023995 | 0.003369 | 0.0035717 | 0.0036797 | 0.0037436 | 0.0037744 | 0.0037674 | 0.0037464 | 0.0037071 | 0.0036556 | 0.0036029
| 0.2 | 0.0020104 | 0.0032269 | 0.0034529 | 0.0035949 | 0.003647 | 0.0036497 | 0.0036171 | 0.003564 | 0.0035015 | 0.003434 | 0.0033704
| 0.25 | 0.0017339 | 0.0031058 | 0.0033837 | 0.0035341 | 0.0035591 | 0.0035284 | 0.0034645 | 0.0033918 | 0.0033114 | 0.0032346 | 0.0031596
| 0.3 | 0.0015226 | 0.0030245 | 0.0033436 | 0.0034686 | 0.0034634 | 0.0033973 | 0.0033175 | 0.0032233 | 0.0031364 | 0.0030535 | 0.0029754
| 0.35 | 0.0013491 | 0.0029679 | 0.0033148 | 0.0033982 | 0.0033573 | 0.0032736 | 0.0031712 | 0.0030714 | 0.0029812 | 0.0028924 | 0.0028122
| 0.4 | 0.0012118 | 0.0029173 | 0.0032823 | 0.0033239 | 0.0032513 | 0.0031474 | 0.0030426 | 0.0029385 | 0.0028399 | 0.0027511 | 0.002673
| 0.45 | 0.0011069 | 0.0028959 | 0.0032462 | 0.0032469 | 0.0031478 | 0.0030309 | 0.0029177 | 0.0028117 | 0.0027199 | 0.0026264 | 0.0025474
| 0.5 | 0.0010131 | 0.0028839 | 0.0031967 | 0.0031671 | 0.0030523 | 0.0029268 | 0.0028049 | 0.0027006 | 0.0026037 | 0.002523 | 0.0024408
| 0.55 | 0.00093251 | 0.0028792 | 0.0031552 | 0.0030905 | 0.0029585 | 0.0028245 | 0.0027079 | 0.0025983 | 0.0025095 | 0.0024248 | 0.002345
| 0.6 | 0.00087599 | 0.0028718 | 0.0031052 | 0.0030138 | 0.002868 | 0.0027333 | 0.0026187 | 0.0025146 | 0.0024165 | 0.0023351 | 0.0022619
| 0.65 | 0.0008154 | 0.0028675 | 0.0030528 | 0.0029417 | 0.0027874 | 0.0026509 | 0.0025314 | 0.0024327 | 0.0023371 | 0.0022589 | 0.0021854
| 0.7 | 0.00077263 | 0.0028664 | 0.0030049 | 0.0028675 | 0.0027126 | 0.0025771 | 0.0024586 | 0.0023577 | 0.0022702 | 0.0021886 | 0.0021159
| 0.75 | 0.00072498 | 0.0028603 | 0.0029504 | 0.0027983 | 0.0026377 | 0.0025011 | 0.0023912 | 0.0022879 | 0.0022022 | 0.0021259 | 0.0020572
| 0.8 | 0.00068626 | 0.0028467 | 0.0029067 | 0.0027327 | 0.0025767 | 0.0024389 | 0.0023259 | 0.00223 | 0.0021423 | 0.0020668 | 0.0019992
| 0.85 | 0.00065868 | 0.0028385 | 0.0028549 | 0.0026766 | 0.0025119 | 0.0023825 | 0.002267 | 0.0021716 | 0.0020858 | 0.0020148 | 0.0019451
| 0.9 | 0.00062214 | 0.0028272 | 0.0028035 | 0.0026138 | 0.0024547 | 0.0023252 | 0.0022129 | 0.0021198 | 0.002037 | 0.0019631 | 0.0018944
| 0.95 | 0.00059313 | 0.0028142 | 0.0027627 | 0.0025641 | 0.002404 | 0.002272 | 0.0021677 | 0.00207 | 0.0019854 | 0.0019166 | 0.0018518
| 1 | 0.00057426 | 0.0027936 | 0.0027146 | 0.0025129 | 0.0023532 | 0.0022254 | 0.0021165 | 0.0020267 | 0.0019446 | 0.0018737 | 0.0018117
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.3693 | 1.7383 | 2.0169 | 2.2377 | 2.4086 | 2.5474 | 2.6516 | 2.7488 | 2.8227 | 2.8845 | 2.9363
| 0.1 | 1.2795 | 2.0627 | 2.6018 | 2.9995 | 3.3024 | 3.5354 | 3.7053 | 3.9088 | 3.9562 | 4.0733 | 4.1103
| 0.15 | 1.203 | 2.3404 | 3.0875 | 3.6296 | 4.0316 | 4.3289 | 4.6368 | 4.7077 | 4.8051 | 4.96 | 4.9824
| 0.2 | 1.1472 | 2.588 | 3.5276 | 4.1523 | 4.6524 | 5.0038 | 5.2423 | 5.455 | 5.589 | 5.7071 | 5.7951
| 0.25 | 1.1128 | 2.8225 | 3.8457 | 4.675 | 5.1976 | 5.5778 | 5.8613 | 6.079 | 6.2549 | 6.3741 | 6.4761
| 0.3 | 1.0819 | 3.0789 | 4.2835 | 5.1058 | 5.6778 | 6.1042 | 6.4073 | 6.6523 | 6.8334 | 6.9778 | 7.0648
| 0.35 | 1.0665 | 3.2706 | 4.6135 | 5.4996 | 6.1159 | 6.5773 | 6.9115 | 7.1699 | 7.3713 | 7.5249 | 7.6426
| 0.4 | 1.0486 | 3.6173 | 4.9136 | 5.8588 | 6.5151 | 7.0128 | 7.375 | 7.6597 | 7.8667 | 8.0298 | 8.154
| 0.45 | 1.0301 | 3.6807 | 5.1645 | 6.1942 | 6.903 | 7.4235 | 7.812 | 8.1009 | 8.3384 | 8.5073 | 8.6367
| 0.5 | 1.0262 | 3.7441 | 5.4557 | 6.5137 | 7.2519 | 7.8039 | 8.2192 | 8.5317 | 8.7664 | 8.9611 | 9.0977
| 0.55 | 1.0131 | 4.0039 | 5.7263 | 6.8136 | 7.5915 | 8.1699 | 8.61 | 8.9381 | 9.1902 | 9.3886 | 9.5342
| 0.6 | 1.0137 | 4.2355 | 5.9558 | 7.0962 | 7.9104 | 8.5169 | 8.9783 | 9.3272 | 9.5943 | 9.799 | 9.9502
| 0.65 | 1.0025 | 4.3739 | 6.1811 | 7.3602 | 8.2175 | 8.8528 | 9.3367 | 9.6984 | 9.9775 | 10.1949 | 10.3554
| 0.7 | 1.0019 | 4.5631 | 6.3965 | 7.6204 | 8.5125 | 9.1793 | 9.6818 | 10.0624 | 10.3532 | 10.5798 | 10.7376
| 0.75 | 0.99266 | 4.7145 | 6.6174 | 7.8774 | 8.7962 | 9.4854 | 10.0086 | 10.4125 | 10.7103 | 10.9409 | 11.1086
| 0.8 | 0.99448 | 4.8611 | 6.8133 | 8.1195 | 9.0699 | 9.7875 | 10.3269 | 10.7457 | 11.0439 | 11.2901 | 11.4691
| 0.85 | 0.98648 | 4.9966 | 7.0077 | 8.3598 | 9.3491 | 10.0823 | 10.6439 | 11.059 | 11.3943 | 11.6347 | 11.8164
| 0.9 | 0.98056 | 5.1335 | 7.1948 | 8.583 | 9.6057 | 10.3702 | 10.9511 | 11.3755 | 11.7111 | 11.9653 | 12.1526
| 0.95 | 0.98283 | 5.2649 | 7.3806 | 8.8049 | 9.8608 | 10.6409 | 11.2375 | 11.6855 | 12.0378 | 12.2875 | 12.4866
| 1 | 0.97758 | 5.4087 | 7.5558 | 9.0166 | 10.1066 | 10.9154 | 11.5235 | 11.9871 | 12.3342 | 12.603 | 12.7936
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.027299 | 0.025175 | 0.026181 | 0.027245 | 0.031641 | 0.033309 | 0.034403 | 0.038584 | 0.041617 | 0.042893 | 0.046612
| 0.1 | 0.028088 | 0.036426 | 0.047094 | 0.04799 | 0.052027 | 0.054858 | 0.061699 | 0.064867 | 0.069618 | 0.076052 | 0.077295
| 0.15 | 0.022838 | 0.041492 | 0.058385 | 0.063236 | 0.072413 | 0.076407 | 0.088994 | 0.091149 | 0.09762 | 0.1052 | 0.10564
| 0.2 | 0.016339 | 0.046559 | 0.068437 | 0.081238 | 0.094783 | 0.10612 | 0.11504 | 0.11743 | 0.12562 | 0.13435 | 0.13398
| 0.25 | 0.010429 | 0.051625 | 0.078489 | 0.095644 | 0.11723 | 0.12844 | 0.13658 | 0.14371 | 0.15362 | 0.15562 | 0.15718
| 0.3 | 0.006884 | 0.056691 | 0.088709 | 0.11236 | 0.13561 | 0.14754 | 0.15812 | 0.17 | 0.17266 | 0.17412 | 0.179
| 0.35 | 0.0046273 | 0.061758 | 0.10139 | 0.12907 | 0.15366 | 0.16665 | 0.17559 | 0.18287 | 0.18853 | 0.19191 | 0.19386
| 0.4 | 0.00023239 | 0.066824 | 0.1193 | 0.14579 | 0.1658 | 0.18094 | 0.19508 | 0.19835 | 0.20387 | 0.21019 | 0.21105
| 0.45 | -0.00032594 | 0.069066 | 0.13149 | 0.16148 | 0.17876 | 0.19522 | 0.2077 | 0.21436 | 0.22068 | 0.2221 | 0.22617
| 0.5 | -0.0022584 | 0.073401 | 0.14368 | 0.17622 | 0.19418 | 0.20841 | 0.22099 | 0.22649 | 0.23325 | 0.2383 | 0.24063
| 0.55 | -0.0040517 | 0.078043 | 0.15002 | 0.18091 | 0.20293 | 0.22096 | 0.2312 | 0.23943 | 0.24633 | 0.25155 | 0.25525
| 0.6 | -0.0053788 | 0.083495 | 0.15449 | 0.19091 | 0.21426 | 0.23076 | 0.24273 | 0.25255 | 0.25815 | 0.26299 | 0.26833
| 0.65 | -0.0066564 | 0.087553 | 0.16201 | 0.2006 | 0.22417 | 0.24286 | 0.25573 | 0.26393 | 0.27118 | 0.27622 | 0.28125
| 0.7 | -0.0079171 | 0.099776 | 0.17283 | 0.20891 | 0.2321 | 0.25127 | 0.26684 | 0.27495 | 0.2843 | 0.28957 | 0.29351
| 0.75 | -0.0063821 | 0.10666 | 0.17761 | 0.21637 | 0.24208 | 0.26115 | 0.27554 | 0.28658 | 0.2951 | 0.29922 | 0.30493
| 0.8 | -0.0094273 | 0.11419 | 0.18582 | 0.22649 | 0.25058 | 0.26994 | 0.28499 | 0.29694 | 0.30417 | 0.31326 | 0.31533
| 0.85 | -0.0084187 | 0.1195 | 0.19022 | 0.23096 | 0.26034 | 0.28109 | 0.29637 | 0.30881 | 0.31559 | 0.32402 | 0.3268
| 0.9 | -0.0096091 | 0.12481 | 0.19777 | 0.23858 | 0.26782 | 0.2903 | 0.30454 | 0.31841 | 0.32743 | 0.33339 | 0.34162
| 0.95 | -0.010207 | 0.1327 | 0.204 | 0.24687 | 0.27484 | 0.29886 | 0.31663 | 0.3287 | 0.33541 | 0.34607 | 0.35056
| 1 | -0.011241 | 0.13982 | 0.21209 | 0.25311 | 0.28435 | 0.30805 | 0.32476 | 0.33661 | 0.34831 | 0.35553 | 0.35949
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.00042404 | -0.0087715 | -0.014896 | -0.019104 | -0.022194 | -0.02443 | -0.026477 | -0.027295 | -0.028174 | -0.029125 | -0.02932
| 0.1 | 0.002932 | -0.012981 | -0.022512 | -0.03037 | -0.031858 | -0.036595 | -0.039092 | -0.040716 | -0.041506 | -0.042351 | -0.042148
| 0.15 | 0.0028208 | -0.017992 | -0.029248 | -0.036707 | -0.041522 | -0.044968 | -0.047846 | -0.049475 | -0.051041 | -0.050905 | -0.052032
| 0.2 | 0.0027568 | -0.022518 | -0.035195 | -0.042013 | -0.047127 | -0.051418 | -0.054313 | -0.055606 | -0.057946 | -0.058351 | -0.060057
| 0.25 | 0.0021948 | -0.027586 | -0.039593 | -0.047519 | -0.052012 | -0.057944 | -0.06078 | -0.063247 | -0.064313 | -0.065797 | -0.066791
| 0.3 | 0.001755 | -0.028491 | -0.043876 | -0.053587 | -0.058278 | -0.062461 | -0.065661 | -0.068354 | -0.070527 | -0.071853 | -0.072843
| 0.35 | 0.0014784 | -0.03207 | -0.048159 | -0.055414 | -0.062011 | -0.066733 | -0.070789 | -0.073678 | -0.075798 | -0.07739 | -0.078644
| 0.4 | 0.00137 | -0.034553 | -0.050403 | -0.05878 | -0.065735 | -0.071435 | -0.075231 | -0.078473 | -0.081047 | -0.082932 | -0.084413
| 0.45 | 0.0010723 | -0.037412 | -0.05208 | -0.061593 | -0.069348 | -0.07523 | -0.079837 | -0.083247 | -0.086081 | -0.087814 | -0.089544
| 0.5 | 0.0009592 | -0.040272 | -0.053756 | -0.064366 | -0.072726 | -0.079577 | -0.084419 | -0.088119 | -0.090646 | -0.092794 | -0.0945
| 0.55 | 0.00086283 | -0.04087 | -0.055846 | -0.067322 | -0.076409 | -0.083005 | -0.088301 | -0.09201 | -0.094904 | -0.097275 | -0.099081
| 0.6 | 0.0006228 | -0.042454 | -0.058081 | -0.07015 | -0.079359 | -0.086766 | -0.092263 | -0.096221 | -0.099429 | -0.10181 | -0.10353
| 0.65 | 0.00061832 | -0.043643 | -0.060149 | -0.073136 | -0.08263 | -0.090115 | -0.096143 | -0.10013 | -0.10343 | -0.10597 | -0.10795
| 0.7 | 0.00040261 | -0.04578 | -0.062276 | -0.075423 | -0.085751 | -0.093589 | -0.099737 | -0.10405 | -0.10738 | -0.10973 | -0.11191
| 0.75 | 0.00043963 | -0.047079 | -0.064129 | -0.078116 | -0.089024 | -0.097001 | -0.10287 | -0.10787 | -0.11138 | -0.11399 | -0.1157
| 0.8 | 0.0004584 | -0.048826 | -0.066123 | -0.081084 | -0.091947 | -0.10018 | -0.10632 | -0.11091 | -0.11486 | -0.11754 | -0.11954
| 0.85 | 0.00022448 | -0.049491 | -0.068035 | -0.083189 | -0.09495 | -0.10325 | -0.10979 | -0.11458 | -0.11848 | -0.12102 | -0.12327
| 0.9 | 0.00028245 | -0.052035 | -0.070273 | -0.086012 | -0.09764 | -0.10639 | -0.11283 | -0.11788 | -0.12182 | -0.12451 | -0.127
| 0.95 | 0.00028203 | -0.052698 | -0.071885 | -0.088295 | -0.10016 | -0.10938 | -0.11564 | -0.12119 | -0.12508 | -0.128 | -0.13025
| 1 | 0.00013357 | -0.053362 | -0.073954 | -0.090605 | -0.10277 | -0.11204 | -0.11887 | -0.12412 | -0.12818 | -0.13146 | -0.13367
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-15.79) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-51.89))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-15.79) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-51.89))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS3_LS>= (hidden)
If Iload/Isc x 5.6569 ≥1 | [12 empty] | If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 |  | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.02 | 1.0517 | 1.0833 | 1.1041 | 1.1152 | 1.1194 | 1.1189 | 1.1149 | 1.1086 | 1.1006 | 1.0915 |  | 0.05 | 1.02 | 1.0517 | 1.0833 | 1.1041 | 1.1152 | 1.1194 | 1.1189 | 1.1149 | 1.1086 | 1.1006 | 1.0915
| 0.1 | 1.0122 | 1.0596 | 1.1045 | 1.1328 | 1.1477 | 1.1523 | 1.1505 | 1.1447 | 1.1372 | 1.1279 | 1.1174 |  | 0.1 | 1.0122 | 1.0596 | 1.1045 | 1.1328 | 1.1477 | 1.1523 | 1.1505 | 1.1447 | 1.1372 | 1.1279 | 1.1174
| 0.15 | 0.98432 | 1.0576 | 1.1126 | 1.1443 | 1.1587 | 1.1644 | 1.1637 | 1.1585 | 1.1504 | 1.1403 | 1.1289 |  | 0.15 | 0.98432 | 1.0576 | 1.1126 | 1.1443 | 1.1587 | 1.1644 | 1.1637 | 1.1585 | 1.1504 | 1.1403 | 1.1289
| 0.2 | 0.95186 | 1.0506 | 1.1135 | 1.1491 | 1.1652 | 1.1725 | 1.1724 | 1.1673 | 1.1589 | 1.1484 | 1.1364 |  | 0.2 | 0.95186 | 1.0506 | 1.1135 | 1.1491 | 1.1652 | 1.1725 | 1.1724 | 1.1673 | 1.1589 | 1.1484 | 1.1364
| 0.25 | 0.92133 | 1.0429 | 1.1124 | 1.1508 | 1.1698 | 1.1786 | 1.1789 | 1.1737 | 1.165 | 1.154 | 1.1415 |  | 0.25 | 0.92133 | 1.0429 | 1.1124 | 1.1508 | 1.1698 | 1.1786 | 1.1789 | 1.1737 | 1.165 | 1.154 | 1.1415
| 0.3 | 0.89447 | 1.036 | 1.1116 | 1.1517 | 1.1738 | 1.1833 | 1.1837 | 1.1783 | 1.1693 | 1.158 | 1.1452 |  | 0.3 | 0.89447 | 1.036 | 1.1116 | 1.1517 | 1.1738 | 1.1833 | 1.1837 | 1.1783 | 1.1693 | 1.158 | 1.1452
| 0.35 | 0.87138 | 1.0299 | 1.11 | 1.1525 | 1.1771 | 1.1869 | 1.1872 | 1.1817 | 1.1725 | 1.161 | 1.1479 |  | 0.35 | 0.87138 | 1.0299 | 1.11 | 1.1525 | 1.1771 | 1.1869 | 1.1872 | 1.1817 | 1.1725 | 1.161 | 1.1479
| 0.4 | 0.85165 | 1.0246 | 1.1083 | 1.1537 | 1.1797 | 1.1897 | 1.19 | 1.1844 | 1.1751 | 1.1634 | 1.1502 |  | 0.4 | 0.85165 | 1.0246 | 1.1083 | 1.1537 | 1.1797 | 1.1897 | 1.19 | 1.1844 | 1.1751 | 1.1634 | 1.1502
| 0.45 | 0.83475 | 1.02 | 1.1067 | 1.155 | 1.1818 | 1.1919 | 1.1923 | 1.1866 | 1.1772 | 1.1654 | 1.1521 |  | 0.45 | 0.83475 | 1.02 | 1.1067 | 1.155 | 1.1818 | 1.1919 | 1.1923 | 1.1866 | 1.1772 | 1.1654 | 1.1521
| 0.5 | 0.8202 | 1.016 | 1.1052 | 1.1563 | 1.1834 | 1.1937 | 1.1942 | 1.1885 | 1.179 | 1.1671 | 1.1537 |  | 0.5 | 0.8202 | 1.016 | 1.1052 | 1.1563 | 1.1834 | 1.1937 | 1.1942 | 1.1885 | 1.179 | 1.1671 | 1.1537
| 0.55 | 0.8076 | 1.0125 | 1.1041 | 1.1573 | 1.1848 | 1.1953 | 1.1958 | 1.1901 | 1.1806 | 1.1686 | 1.155 |  | 0.55 | 0.8076 | 1.0125 | 1.1041 | 1.1573 | 1.1848 | 1.1953 | 1.1958 | 1.1901 | 1.1806 | 1.1686 | 1.155
| 0.6 | 0.79661 | 1.0093 | 1.1032 | 1.1582 | 1.186 | 1.1967 | 1.1973 | 1.1916 | 1.1819 | 1.1698 | 1.1562 |  | 0.6 | 0.79661 | 1.0093 | 1.1032 | 1.1582 | 1.186 | 1.1967 | 1.1973 | 1.1916 | 1.1819 | 1.1698 | 1.1562
| 0.65 | 0.78696 | 1.0064 | 1.1028 | 1.1589 | 1.1871 | 1.198 | 1.1986 | 1.1928 | 1.1831 | 1.1709 | 1.1572 |  | 0.65 | 0.78696 | 1.0064 | 1.1028 | 1.1589 | 1.1871 | 1.198 | 1.1986 | 1.1928 | 1.1831 | 1.1709 | 1.1572
| 0.7 | 0.77843 | 1.0038 | 1.1028 | 1.1595 | 1.1881 | 1.1991 | 1.1997 | 1.1939 | 1.1842 | 1.1719 | 1.1581 |  | 0.7 | 0.77843 | 1.0038 | 1.1028 | 1.1595 | 1.1881 | 1.1991 | 1.1997 | 1.1939 | 1.1842 | 1.1719 | 1.1581
| 0.75 | 0.77084 | 1.0015 | 1.1029 | 1.1601 | 1.189 | 1.2001 | 1.2007 | 1.1949 | 1.1851 | 1.1728 | 1.1589 |  | 0.75 | 0.77084 | 1.0015 | 1.1029 | 1.1601 | 1.189 | 1.2001 | 1.2007 | 1.1949 | 1.1851 | 1.1728 | 1.1589
| 0.8 | 0.76405 | 0.99933 | 1.103 | 1.1607 | 1.1898 | 1.201 | 1.2016 | 1.1958 | 1.1859 | 1.1736 | 1.1596 |  | 0.8 | 0.76405 | 0.99933 | 1.103 | 1.1607 | 1.1898 | 1.201 | 1.2016 | 1.1958 | 1.1859 | 1.1736 | 1.1596
| 0.85 | 0.75795 | 0.99739 | 1.103 | 1.1612 | 1.1906 | 1.2018 | 1.2024 | 1.1966 | 1.1867 | 1.1743 | 1.1603 |  | 0.85 | 0.75795 | 0.99739 | 1.103 | 1.1612 | 1.1906 | 1.2018 | 1.2024 | 1.1966 | 1.1867 | 1.1743 | 1.1603
| 0.9 | 0.75244 | 0.99563 | 1.103 | 1.1617 | 1.1912 | 1.2026 | 1.2032 | 1.1973 | 1.1874 | 1.1749 | 1.1609 |  | 0.9 | 0.75244 | 0.99563 | 1.103 | 1.1617 | 1.1912 | 1.2026 | 1.2032 | 1.1973 | 1.1874 | 1.1749 | 1.1609
| 0.95 | 0.74743 | 0.99405 | 1.103 | 1.1621 | 1.1919 | 1.2032 | 1.2039 | 1.198 | 1.188 | 1.1755 | 1.1615 |  | 0.95 | 0.74743 | 0.99405 | 1.103 | 1.1621 | 1.1919 | 1.2032 | 1.2039 | 1.198 | 1.188 | 1.1755 | 1.1615
| 1 | 0.74287 | 0.99263 | 1.1029 | 1.1626 | 1.1925 | 1.2039 | 1.2045 | 1.1986 | 1.1886 | 1.1761 | 1.162 |  | 1 | 0.74287 | 0.99263 | 1.1029 | 1.1626 | 1.1925 | 1.2039 | 1.2045 | 1.1986 | 1.1886 | 1.1761 | 1.162
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 |  | 0 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
| 0.05 | 1.0784 | 1.045 | 1.0131 | 0.98312 | 0.95496 | 0.9285 | 0.90431 | 0.88103 | 0.85933 | 0.83896 | 0.81983 |  | 0.05 | 1.0784 | 1.045 | 1.0131 | 0.98312 | 0.95496 | 0.9285 | 0.90431 | 0.88103 | 0.85933 | 0.83896 | 0.81983
| 0.1 | 0.95465 | 0.89725 | 0.85388 | 0.81738 | 0.78491 | 0.75558 | 0.72901 | 0.70459 | 0.68239 | 0.66201 | 0.64322 |  | 0.1 | 0.95465 | 0.89725 | 0.85388 | 0.81738 | 0.78491 | 0.75558 | 0.72901 | 0.70459 | 0.68239 | 0.66201 | 0.64322
| 0.15 | 0.89423 | 0.81195 | 0.76211 | 0.72247 | 0.68776 | 0.65722 | 0.6304 | 0.60625 | 0.58471 | 0.56518 | 0.54756 |  | 0.15 | 0.89423 | 0.81195 | 0.76211 | 0.72247 | 0.68776 | 0.65722 | 0.6304 | 0.60625 | 0.58471 | 0.56518 | 0.54756
| 0.2 | 0.85996 | 0.75304 | 0.69879 | 0.6563 | 0.62016 | 0.58934 | 0.56296 | 0.53984 | 0.51922 | 0.50097 | 0.48475 |  | 0.2 | 0.85996 | 0.75304 | 0.69879 | 0.6563 | 0.62016 | 0.58934 | 0.56296 | 0.53984 | 0.51922 | 0.50097 | 0.48475
| 0.25 | 0.83795 | 0.70938 | 0.6506 | 0.60558 | 0.56892 | 0.53869 | 0.51314 | 0.4911 | 0.47163 | 0.45477 | 0.4395 |  | 0.25 | 0.83795 | 0.70938 | 0.6506 | 0.60558 | 0.56892 | 0.53869 | 0.51314 | 0.4911 | 0.47163 | 0.45477 | 0.4395
| 0.3 | 0.82199 | 0.67458 | 0.61147 | 0.56481 | 0.5284 | 0.49889 | 0.47441 | 0.45338 | 0.4353 | 0.41925 | 0.40484 |  | 0.3 | 0.82199 | 0.67458 | 0.61147 | 0.56481 | 0.5284 | 0.49889 | 0.47441 | 0.45338 | 0.4353 | 0.41925 | 0.40484
| 0.35 | 0.81088 | 0.64552 | 0.57868 | 0.53107 | 0.49529 | 0.46675 | 0.4433 | 0.42335 | 0.40598 | 0.39084 | 0.37748 |  | 0.35 | 0.81088 | 0.64552 | 0.57868 | 0.53107 | 0.49529 | 0.46675 | 0.4433 | 0.42335 | 0.40598 | 0.39084 | 0.37748
| 0.4 | 0.80175 | 0.62061 | 0.55026 | 0.50265 | 0.46767 | 0.44014 | 0.4176 | 0.39849 | 0.38203 | 0.36771 | 0.35484 |  | 0.4 | 0.80175 | 0.62061 | 0.55026 | 0.50265 | 0.46767 | 0.44014 | 0.4176 | 0.39849 | 0.38203 | 0.36771 | 0.35484
| 0.45 | 0.79512 | 0.59888 | 0.52569 | 0.47834 | 0.44406 | 0.41753 | 0.39585 | 0.37754 | 0.36194 | 0.34819 | 0.33606 |  | 0.45 | 0.79512 | 0.59888 | 0.52569 | 0.47834 | 0.44406 | 0.41753 | 0.39585 | 0.37754 | 0.36194 | 0.34819 | 0.33606
| 0.5 | 0.78989 | 0.57907 | 0.50418 | 0.45698 | 0.42367 | 0.39814 | 0.37739 | 0.35974 | 0.34466 | 0.33155 | 0.31999 |  | 0.5 | 0.78989 | 0.57907 | 0.50418 | 0.45698 | 0.42367 | 0.39814 | 0.37739 | 0.35974 | 0.34466 | 0.33155 | 0.31999
| 0.55 | 0.7849 | 0.56136 | 0.48491 | 0.43837 | 0.40602 | 0.38124 | 0.36106 | 0.34435 | 0.32975 | 0.31722 | 0.30599 |  | 0.55 | 0.7849 | 0.56136 | 0.48491 | 0.43837 | 0.40602 | 0.38124 | 0.36106 | 0.34435 | 0.32975 | 0.31722 | 0.30599
| 0.6 | 0.78129 | 0.5453 | 0.46759 | 0.42186 | 0.39032 | 0.36633 | 0.34703 | 0.3306 | 0.31669 | 0.30432 | 0.29365 |  | 0.6 | 0.78129 | 0.5453 | 0.46759 | 0.42186 | 0.39032 | 0.36633 | 0.34703 | 0.3306 | 0.31669 | 0.30432 | 0.29365
| 0.65 | 0.77762 | 0.53025 | 0.45205 | 0.40704 | 0.37642 | 0.35319 | 0.33428 | 0.31846 | 0.30497 | 0.29309 | 0.28279 |  | 0.65 | 0.77762 | 0.53025 | 0.45205 | 0.40704 | 0.37642 | 0.35319 | 0.33428 | 0.31846 | 0.30497 | 0.29309 | 0.28279
| 0.7 | 0.77509 | 0.5166 | 0.43796 | 0.39375 | 0.36376 | 0.34126 | 0.32293 | 0.30769 | 0.29455 | 0.28317 | 0.27301 |  | 0.7 | 0.77509 | 0.5166 | 0.43796 | 0.39375 | 0.36376 | 0.34126 | 0.32293 | 0.30769 | 0.29455 | 0.28317 | 0.27301
| 0.75 | 0.77292 | 0.50396 | 0.42509 | 0.3816 | 0.35246 | 0.33055 | 0.3128 | 0.29784 | 0.2851 | 0.27391 | 0.26419 |  | 0.75 | 0.77292 | 0.50396 | 0.42509 | 0.3816 | 0.35246 | 0.33055 | 0.3128 | 0.29784 | 0.2851 | 0.27391 | 0.26419
| 0.8 | 0.7703 | 0.49199 | 0.41312 | 0.37066 | 0.34228 | 0.32062 | 0.30342 | 0.28879 | 0.27649 | 0.26565 | 0.25616 |  | 0.8 | 0.7703 | 0.49199 | 0.41312 | 0.37066 | 0.34228 | 0.32062 | 0.30342 | 0.28879 | 0.27649 | 0.26565 | 0.25616
| 0.85 | 0.76877 | 0.48092 | 0.40232 | 0.36055 | 0.33274 | 0.31175 | 0.2948 | 0.28069 | 0.26856 | 0.25804 | 0.24883 |  | 0.85 | 0.76877 | 0.48092 | 0.40232 | 0.36055 | 0.33274 | 0.31175 | 0.2948 | 0.28069 | 0.26856 | 0.25804 | 0.24883
| 0.9 | 0.76658 | 0.47053 | 0.39233 | 0.35127 | 0.32412 | 0.30343 | 0.28694 | 0.27313 | 0.26143 | 0.25112 | 0.24207 |  | 0.9 | 0.76658 | 0.47053 | 0.39233 | 0.35127 | 0.32412 | 0.30343 | 0.28694 | 0.27313 | 0.26143 | 0.25112 | 0.24207
| 0.95 | 0.76536 | 0.46062 | 0.38289 | 0.34264 | 0.31589 | 0.29583 | 0.27961 | 0.26616 | 0.25471 | 0.24472 | 0.23593 |  | 0.95 | 0.76536 | 0.46062 | 0.38289 | 0.34264 | 0.31589 | 0.29583 | 0.27961 | 0.26616 | 0.25471 | 0.24472 | 0.23593
| 1 | 0.76427 | 0.45145 | 0.37407 | 0.33463 | 0.30845 | 0.28887 | 0.27292 | 0.25985 | 0.24839 | 0.23874 | 0.23019 |  | 1 | 0.76427 | 0.45145 | 0.37407 | 0.33463 | 0.30845 | 0.28887 | 0.27292 | 0.25985 | 0.24839 | 0.23874 | 0.23019
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.012754 | 0.013599 | 0.014041 | 0.014362 | 0.014606 | 0.014769 | 0.014871 | 0.014858 | 0.01494 | 0.015013 | 0.014994 |  | 0.05 | 0.012754 | 0.013599 | 0.014041 | 0.014362 | 0.014606 | 0.014769 | 0.014871 | 0.014858 | 0.01494 | 0.015013 | 0.014994
| 0.1 | 0.011232 | 0.013302 | 0.01376 | 0.01402 | 0.014226 | 0.014306 | 0.014267 | 0.014271 | 0.014177 | 0.013993 | 0.013831 |  | 0.1 | 0.011232 | 0.013302 | 0.01376 | 0.01402 | 0.014226 | 0.014306 | 0.014267 | 0.014271 | 0.014177 | 0.013993 | 0.013831
| 0.15 | 0.0096854 | 0.012509 | 0.013172 | 0.013758 | 0.013941 | 0.013887 | 0.013666 | 0.013503 | 0.013227 | 0.012964 | 0.012666 |  | 0.15 | 0.0096854 | 0.012509 | 0.013172 | 0.013758 | 0.013941 | 0.013887 | 0.013666 | 0.013503 | 0.013227 | 0.012964 | 0.012666
| 0.2 | 0.0082681 | 0.012042 | 0.013033 | 0.013484 | 0.013483 | 0.013271 | 0.012908 | 0.012607 | 0.012287 | 0.01196 | 0.01168 |  | 0.2 | 0.0082681 | 0.012042 | 0.013033 | 0.013484 | 0.013483 | 0.013271 | 0.012908 | 0.012607 | 0.012287 | 0.01196 | 0.01168
| 0.25 | 0.0072946 | 0.011605 | 0.012982 | 0.01314 | 0.012965 | 0.012548 | 0.012196 | 0.011818 | 0.011439 | 0.01112 | 0.01079 |  | 0.25 | 0.0072946 | 0.011605 | 0.012982 | 0.01314 | 0.012965 | 0.012548 | 0.012196 | 0.011818 | 0.011439 | 0.01112 | 0.01079
| 0.3 | 0.006766 | 0.011463 | 0.012787 | 0.012693 | 0.012403 | 0.011937 | 0.011516 | 0.011084 | 0.010782 | 0.01041 | 0.010124 |  | 0.3 | 0.006766 | 0.011463 | 0.012787 | 0.012693 | 0.012403 | 0.011937 | 0.011516 | 0.011084 | 0.010782 | 0.01041 | 0.010124
| 0.35 | 0.0060937 | 0.011473 | 0.012508 | 0.01232 | 0.011832 | 0.011369 | 0.01093 | 0.010505 | 0.010118 | 0.0098004 | 0.0095085 |  | 0.35 | 0.0060937 | 0.011473 | 0.012508 | 0.01232 | 0.011832 | 0.011369 | 0.01093 | 0.010505 | 0.010118 | 0.0098004 | 0.0095085
| 0.4 | 0.0056809 | 0.011378 | 0.012214 | 0.011928 | 0.011341 | 0.010851 | 0.010391 | 0.0099886 | 0.009619 | 0.0093137 | 0.0089973 |  | 0.4 | 0.0056809 | 0.011378 | 0.012214 | 0.011928 | 0.011341 | 0.010851 | 0.010391 | 0.0099886 | 0.009619 | 0.0093137 | 0.0089973
| 0.45 | 0.0053534 | 0.01139 | 0.012 | 0.01148 | 0.010897 | 0.010413 | 0.0099528 | 0.0095613 | 0.0091728 | 0.0088843 | 0.0085771 |  | 0.45 | 0.0053534 | 0.01139 | 0.012 | 0.01148 | 0.010897 | 0.010413 | 0.0099528 | 0.0095613 | 0.0091728 | 0.0088843 | 0.0085771
| 0.5 | 0.0050772 | 0.011357 | 0.011641 | 0.011095 | 0.010513 | 0.0099988 | 0.0095238 | 0.0091614 | 0.0087897 | 0.0085183 | 0.0082408 |  | 0.5 | 0.0050772 | 0.011357 | 0.011641 | 0.011095 | 0.010513 | 0.0099988 | 0.0095238 | 0.0091614 | 0.0087897 | 0.0085183 | 0.0082408
| 0.55 | 0.0047117 | 0.011317 | 0.011419 | 0.010759 | 0.010146 | 0.0096073 | 0.0091824 | 0.0088134 | 0.0084679 | 0.0081669 | 0.0079163 |  | 0.55 | 0.0047117 | 0.011317 | 0.011419 | 0.010759 | 0.010146 | 0.0096073 | 0.0091824 | 0.0088134 | 0.0084679 | 0.0081669 | 0.0079163
| 0.6 | 0.0046672 | 0.011203 | 0.011108 | 0.01043 | 0.0098168 | 0.0092979 | 0.0088667 | 0.0085287 | 0.0081706 | 0.0078863 | 0.0076137 |  | 0.6 | 0.0046672 | 0.011203 | 0.011108 | 0.01043 | 0.0098168 | 0.0092979 | 0.0088667 | 0.0085287 | 0.0081706 | 0.0078863 | 0.0076137
| 0.65 | 0.0043509 | 0.01113 | 0.010855 | 0.010137 | 0.0095009 | 0.0090077 | 0.0085576 | 0.0081995 | 0.0079236 | 0.0076261 | 0.0073682 |  | 0.65 | 0.0043509 | 0.01113 | 0.010855 | 0.010137 | 0.0095009 | 0.0090077 | 0.0085576 | 0.0081995 | 0.0079236 | 0.0076261 | 0.0073682
| 0.7 | 0.0042072 | 0.011013 | 0.010615 | 0.0098579 | 0.0092513 | 0.0087682 | 0.0083029 | 0.0079922 | 0.007641 | 0.0073838 | 0.0071352 |  | 0.7 | 0.0042072 | 0.011013 | 0.010615 | 0.0098579 | 0.0092513 | 0.0087682 | 0.0083029 | 0.0079922 | 0.007641 | 0.0073838 | 0.0071352
| 0.75 | 0.0042457 | 0.010934 | 0.010392 | 0.0095953 | 0.008968 | 0.0085034 | 0.0080904 | 0.0077632 | 0.0074211 | 0.0071862 | 0.0069049 |  | 0.75 | 0.0042457 | 0.010934 | 0.010392 | 0.0095953 | 0.008968 | 0.0085034 | 0.0080904 | 0.0077632 | 0.0074211 | 0.0071862 | 0.0069049
| 0.8 | 0.0039967 | 0.010803 | 0.010179 | 0.0093623 | 0.0087515 | 0.0082827 | 0.0078856 | 0.0075113 | 0.0072119 | 0.0069564 | 0.0067338 |  | 0.8 | 0.0039967 | 0.010803 | 0.010179 | 0.0093623 | 0.0087515 | 0.0082827 | 0.0078856 | 0.0075113 | 0.0072119 | 0.0069564 | 0.0067338
| 0.85 | 0.0038984 | 0.010698 | 0.0099417 | 0.0091275 | 0.0085548 | 0.0080929 | 0.0076878 | 0.0073456 | 0.0070553 | 0.0067747 | 0.0065598 |  | 0.85 | 0.0038984 | 0.010698 | 0.0099417 | 0.0091275 | 0.0085548 | 0.0080929 | 0.0076878 | 0.0073456 | 0.0070553 | 0.0067747 | 0.0065598
| 0.9 | 0.0038415 | 0.010607 | 0.0097232 | 0.0089421 | 0.0083257 | 0.0078871 | 0.0075185 | 0.0071616 | 0.0068734 | 0.0066309 | 0.0063643 |  | 0.9 | 0.0038415 | 0.010607 | 0.0097232 | 0.0089421 | 0.0083257 | 0.0078871 | 0.0075185 | 0.0071616 | 0.0068734 | 0.0066309 | 0.0063643
| 0.95 | 0.003754 | 0.010435 | 0.0095673 | 0.0087285 | 0.008145 | 0.0077064 | 0.0072986 | 0.006999 | 0.0067213 | 0.006462 | 0.0062154 |  | 0.95 | 0.003754 | 0.010435 | 0.0095673 | 0.0087285 | 0.008145 | 0.0077064 | 0.0072986 | 0.006999 | 0.0067213 | 0.006462 | 0.0062154
| 1 | 0.003552 | 0.010365 | 0.0093634 | 0.0085633 | 0.0079862 | 0.0075681 | 0.0071547 | 0.0068204 | 0.0065463 | 0.0063031 | 0.0060798 |  | 1 | 0.003552 | 0.010365 | 0.0093634 | 0.0085633 | 0.0079862 | 0.0075681 | 0.0071547 | 0.0068204 | 0.0065463 | 0.0063031 | 0.0060798
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0029204 | 0.003322 | 0.0035683 | 0.003727 | 0.0038428 | 0.0039327 | 0.0039857 | 0.0040515 | 0.0040811 | 0.004103 | 0.0041138 |  | 0.05 | 0.0029204 | 0.003322 | 0.0035683 | 0.003727 | 0.0038428 | 0.0039327 | 0.0039857 | 0.0040515 | 0.0040811 | 0.004103 | 0.0041138
| 0.1 | 0.002528 | 0.0033759 | 0.0036195 | 0.0037536 | 0.0038415 | 0.0038963 | 0.0039029 | 0.0039138 | 0.0038951 | 0.0038587 | 0.0038227 |  | 0.1 | 0.002528 | 0.0033759 | 0.0036195 | 0.0037536 | 0.0038415 | 0.0038963 | 0.0039029 | 0.0039138 | 0.0038951 | 0.0038587 | 0.0038227
| 0.15 | 0.0020416 | 0.0032641 | 0.0035291 | 0.0036935 | 0.0037692 | 0.0037841 | 0.0037599 | 0.0037137 | 0.0036574 | 0.0035914 | 0.0035232 |  | 0.15 | 0.0020416 | 0.0032641 | 0.0035291 | 0.0036935 | 0.0037692 | 0.0037841 | 0.0037599 | 0.0037137 | 0.0036574 | 0.0035914 | 0.0035232
| 0.2 | 0.0016728 | 0.0031336 | 0.0034936 | 0.0036521 | 0.0036791 | 0.0036455 | 0.0035818 | 0.0035024 | 0.0034171 | 0.0033383 | 0.0032579 |  | 0.2 | 0.0016728 | 0.0031336 | 0.0034936 | 0.0036521 | 0.0036791 | 0.0036455 | 0.0035818 | 0.0035024 | 0.0034171 | 0.0033383 | 0.0032579
| 0.25 | 0.001405 | 0.0030666 | 0.0034576 | 0.0035821 | 0.003561 | 0.0034865 | 0.003394 | 0.0032984 | 0.0032045 | 0.0031153 | 0.0030326 |  | 0.25 | 0.001405 | 0.0030666 | 0.0034576 | 0.0035821 | 0.003561 | 0.0034865 | 0.003394 | 0.0032984 | 0.0032045 | 0.0031153 | 0.0030326
| 0.3 | 0.0012231 | 0.0030281 | 0.003437 | 0.0034983 | 0.0034324 | 0.0033281 | 0.0032181 | 0.0031117 | 0.0030113 | 0.0029243 | 0.0028361 |  | 0.3 | 0.0012231 | 0.0030281 | 0.003437 | 0.0034983 | 0.0034324 | 0.0033281 | 0.0032181 | 0.0031117 | 0.0030113 | 0.0029243 | 0.0028361
| 0.35 | 0.0010505 | 0.0030179 | 0.0033906 | 0.0033933 | 0.0032996 | 0.0031774 | 0.0030591 | 0.0029473 | 0.0028459 | 0.0027556 | 0.0026728 |  | 0.35 | 0.0010505 | 0.0030179 | 0.0033906 | 0.0033933 | 0.0032996 | 0.0031774 | 0.0030591 | 0.0029473 | 0.0028459 | 0.0027556 | 0.0026728
| 0.4 | 0.00094797 | 0.0030044 | 0.003336 | 0.003293 | 0.0031689 | 0.0030363 | 0.0029163 | 0.0028065 | 0.0027101 | 0.0026137 | 0.0025345 |  | 0.4 | 0.00094797 | 0.0030044 | 0.003336 | 0.003293 | 0.0031689 | 0.0030363 | 0.0029163 | 0.0028065 | 0.0027101 | 0.0026137 | 0.0025345
| 0.45 | 0.00086409 | 0.0030111 | 0.0032788 | 0.0031952 | 0.0030507 | 0.0029115 | 0.0027898 | 0.0026775 | 0.0025801 | 0.0024942 | 0.0024168 |  | 0.45 | 0.00086409 | 0.0030111 | 0.0032788 | 0.0031952 | 0.0030507 | 0.0029115 | 0.0027898 | 0.0026775 | 0.0025801 | 0.0024942 | 0.0024168
| 0.5 | 0.0007626 | 0.0030075 | 0.0032127 | 0.0030944 | 0.0029418 | 0.0028015 | 0.0026779 | 0.0025708 | 0.0024782 | 0.0023879 | 0.0023123 |  | 0.5 | 0.0007626 | 0.0030075 | 0.0032127 | 0.0030944 | 0.0029418 | 0.0028015 | 0.0026779 | 0.0025708 | 0.0024782 | 0.0023879 | 0.0023123
| 0.55 | 0.00071186 | 0.0030083 | 0.0031439 | 0.0030044 | 0.0028413 | 0.0027002 | 0.002578 | 0.0024735 | 0.0023797 | 0.002294 | 0.0022203 |  | 0.55 | 0.00071186 | 0.0030083 | 0.0031439 | 0.0030044 | 0.0028413 | 0.0027002 | 0.002578 | 0.0024735 | 0.0023797 | 0.002294 | 0.0022203
| 0.6 | 0.00065059 | 0.0029899 | 0.0030856 | 0.002917 | 0.002746 | 0.0026084 | 0.0024906 | 0.0023832 | 0.0022957 | 0.0022151 | 0.0021408 |  | 0.6 | 0.00065059 | 0.0029899 | 0.0030856 | 0.002917 | 0.002746 | 0.0026084 | 0.0024906 | 0.0023832 | 0.0022957 | 0.0022151 | 0.0021408
| 0.65 | 0.0006 | 0.0029822 | 0.0030164 | 0.0028349 | 0.0026648 | 0.0025264 | 0.0024103 | 0.0023074 | 0.0022167 | 0.0021416 | 0.0020666 |  | 0.65 | 0.0006 | 0.0029822 | 0.0030164 | 0.0028349 | 0.0026648 | 0.0025264 | 0.0024103 | 0.0023074 | 0.0022167 | 0.0021416 | 0.0020666
| 0.7 | 0.00055545 | 0.0029655 | 0.0029574 | 0.0027544 | 0.0025872 | 0.0024539 | 0.0023374 | 0.002238 | 0.0021462 | 0.0020689 | 0.0020024 |  | 0.7 | 0.00055545 | 0.0029655 | 0.0029574 | 0.0027544 | 0.0025872 | 0.0024539 | 0.0023374 | 0.002238 | 0.0021462 | 0.0020689 | 0.0020024
| 0.75 | 0.00053032 | 0.0029545 | 0.002895 | 0.0026884 | 0.0025167 | 0.0023829 | 0.002271 | 0.0021722 | 0.0020914 | 0.0020113 | 0.0019427 |  | 0.75 | 0.00053032 | 0.0029545 | 0.002895 | 0.0026884 | 0.0025167 | 0.0023829 | 0.002271 | 0.0021722 | 0.0020914 | 0.0020113 | 0.0019427
| 0.8 | 0.00051468 | 0.0029303 | 0.0028299 | 0.0026233 | 0.0024518 | 0.002319 | 0.002209 | 0.0021141 | 0.0020247 | 0.0019545 | 0.0018861 |  | 0.8 | 0.00051468 | 0.0029303 | 0.0028299 | 0.0026233 | 0.0024518 | 0.002319 | 0.002209 | 0.0021141 | 0.0020247 | 0.0019545 | 0.0018861
| 0.85 | 0.00046317 | 0.0029135 | 0.0027776 | 0.002559 | 0.0023907 | 0.0022659 | 0.0021536 | 0.0020605 | 0.0019759 | 0.001901 | 0.0018391 |  | 0.85 | 0.00046317 | 0.0029135 | 0.0027776 | 0.002559 | 0.0023907 | 0.0022659 | 0.0021536 | 0.0020605 | 0.0019759 | 0.001901 | 0.0018391
| 0.9 | 0.00045063 | 0.0028893 | 0.0027213 | 0.0025032 | 0.0023365 | 0.0022103 | 0.0021043 | 0.002008 | 0.0019272 | 0.0018551 | 0.001788 |  | 0.9 | 0.00045063 | 0.0028893 | 0.0027213 | 0.0025032 | 0.0023365 | 0.0022103 | 0.0021043 | 0.002008 | 0.0019272 | 0.0018551 | 0.001788
| 0.95 | 0.00042178 | 0.0028692 | 0.0026696 | 0.0024476 | 0.0022855 | 0.0021635 | 0.0020538 | 0.001959 | 0.0018828 | 0.0018082 | 0.0017479 |  | 0.95 | 0.00042178 | 0.0028692 | 0.0026696 | 0.0024476 | 0.0022855 | 0.0021635 | 0.0020538 | 0.001959 | 0.0018828 | 0.0018082 | 0.0017479
| 1 | 0.00039926 | 0.0028415 | 0.0026225 | 0.0024032 | 0.0022425 | 0.0021122 | 0.0020072 | 0.0019149 | 0.0018345 | 0.0017713 | 0.0017071 |  | 1 | 0.00039926 | 0.0028415 | 0.0026225 | 0.0024032 | 0.0022425 | 0.0021122 | 0.0020072 | 0.0019149 | 0.0018345 | 0.0017713 | 0.0017071
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | [12 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 0 to 1
| 0.05 | 1.2461 | 1.6405 | 1.936 | 2.1652 | 2.3439 | 2.4883 | 2.596 | 2.691 | 2.7682 | 2.836 | 2.8853 |  | 0.05 | 1.2461 | 1.6405 | 1.936 | 2.1652 | 2.3439 | 2.4883 | 2.596 | 2.691 | 2.7682 | 2.836 | 2.8853
| 0.1 | 1.1537 | 1.9519 | 2.4987 | 2.9002 | 3.2 | 3.4303 | 3.6003 | 3.7587 | 3.8616 | 3.9446 | 4.0091 |  | 0.1 | 1.1537 | 1.9519 | 2.4987 | 2.9002 | 3.2 | 3.4303 | 3.6003 | 3.7587 | 3.8616 | 3.9446 | 4.0091
| 0.15 | 1.0928 | 2.2226 | 2.9881 | 3.5318 | 3.8906 | 4.2144 | 4.4305 | 4.6354 | 4.6858 | 4.8962 | 4.9096 |  | 0.15 | 1.0928 | 2.2226 | 2.9881 | 3.5318 | 3.8906 | 4.2144 | 4.4305 | 4.6354 | 4.6858 | 4.8962 | 4.9096
| 0.2 | 1.0478 | 2.4803 | 3.4121 | 4.0222 | 4.4721 | 4.803 | 5.0279 | 5.2169 | 5.3702 | 5.4957 | 5.574 |  | 0.2 | 1.0478 | 2.4803 | 3.4121 | 4.0222 | 4.4721 | 4.803 | 5.0279 | 5.2169 | 5.3702 | 5.4957 | 5.574
| 0.25 | 1.0175 | 2.715 | 3.8686 | 4.4053 | 4.975 | 5.3465 | 5.6171 | 5.8243 | 5.9838 | 6.1058 | 6.194 |  | 0.25 | 1.0175 | 2.715 | 3.8686 | 4.4053 | 4.975 | 5.3465 | 5.6171 | 5.8243 | 5.9838 | 6.1058 | 6.194
| 0.3 | 1.0039 | 2.9358 | 4.1073 | 4.8253 | 5.4083 | 5.8287 | 6.109 | 6.363 | 6.5289 | 6.6682 | 6.7754 |  | 0.3 | 1.0039 | 2.9358 | 4.1073 | 4.8253 | 5.4083 | 5.8287 | 6.109 | 6.363 | 6.5289 | 6.6682 | 6.7754
| 0.35 | 0.98316 | 3.1724 | 4.4157 | 5.2454 | 5.8305 | 6.2726 | 6.5975 | 6.8495 | 7.0343 | 7.1874 | 7.296 |  | 0.35 | 0.98316 | 3.1724 | 4.4157 | 5.2454 | 5.8305 | 6.2726 | 6.5975 | 6.8495 | 7.0343 | 7.1874 | 7.296
| 0.4 | 0.97693 | 3.3692 | 4.6354 | 5.5808 | 6.2014 | 6.6773 | 7.0266 | 7.305 | 7.5102 | 7.6697 | 7.7876 |  | 0.4 | 0.97693 | 3.3692 | 4.6354 | 5.5808 | 6.2014 | 6.6773 | 7.0266 | 7.305 | 7.5102 | 7.6697 | 7.7876
| 0.45 | 0.96663 | 3.5417 | 4.9377 | 5.8959 | 6.572 | 7.0674 | 7.4416 | 7.7315 | 7.9507 | 8.1149 | 8.2493 |  | 0.45 | 0.96663 | 3.5417 | 4.9377 | 5.8959 | 6.572 | 7.0674 | 7.4416 | 7.7315 | 7.9507 | 8.1149 | 8.2493
| 0.5 | 0.95472 | 3.7283 | 5.2105 | 6.1868 | 6.903 | 7.4317 | 7.8269 | 8.131 | 8.3707 | 8.5435 | 8.6786 |  | 0.5 | 0.95472 | 3.7283 | 5.2105 | 6.1868 | 6.903 | 7.4317 | 7.8269 | 8.131 | 8.3707 | 8.5435 | 8.6786
| 0.55 | 0.95417 | 3.9357 | 5.4223 | 6.4698 | 7.2227 | 7.7781 | 8.1964 | 8.5204 | 8.7679 | 8.9551 | 9.0986 |  | 0.55 | 0.95417 | 3.9357 | 5.4223 | 6.4698 | 7.2227 | 7.7781 | 8.1964 | 8.5204 | 8.7679 | 8.9551 | 9.0986
| 0.6 | 0.94709 | 4.0761 | 5.6466 | 6.7427 | 7.5249 | 8.1026 | 8.551 | 8.8841 | 9.1444 | 9.3429 | 9.4936 |  | 0.6 | 0.94709 | 4.0761 | 5.6466 | 6.7427 | 7.5249 | 8.1026 | 8.551 | 8.8841 | 9.1444 | 9.3429 | 9.4936
| 0.65 | 0.9464 | 4.2165 | 5.8683 | 6.9921 | 7.8104 | 8.4297 | 8.8878 | 9.2381 | 9.5071 | 9.7098 | 9.8679 |  | 0.65 | 0.9464 | 4.2165 | 5.8683 | 6.9921 | 7.8104 | 8.4297 | 8.8878 | 9.2381 | 9.5071 | 9.7098 | 9.8679
| 0.7 | 0.93915 | 4.363 | 6.0726 | 7.244 | 8.0931 | 8.7325 | 9.2154 | 9.5838 | 9.86 | 10.078 | 10.2359 |  | 0.7 | 0.93915 | 4.363 | 6.0726 | 7.244 | 8.0931 | 8.7325 | 9.2154 | 9.5838 | 9.86 | 10.078 | 10.2359
| 0.75 | 0.93419 | 4.5036 | 6.2688 | 7.4755 | 8.3656 | 9.0326 | 9.5312 | 9.912 | 10.2023 | 10.4207 | 10.5894 |  | 0.75 | 0.93419 | 4.5036 | 6.2688 | 7.4755 | 8.3656 | 9.0326 | 9.5312 | 9.912 | 10.2023 | 10.4207 | 10.5894
| 0.8 | 0.93572 | 4.6239 | 6.468 | 7.7043 | 8.6278 | 9.3131 | 9.834 | 10.2238 | 10.5279 | 10.7568 | 10.92 |  | 0.8 | 0.93572 | 4.6239 | 6.468 | 7.7043 | 8.6278 | 9.3131 | 9.834 | 10.2238 | 10.5279 | 10.7568 | 10.92
| 0.85 | 0.92896 | 4.7763 | 6.6511 | 7.9379 | 8.882 | 9.5931 | 10.1248 | 10.5334 | 10.8434 | 11.0717 | 11.2536 |  | 0.85 | 0.92896 | 4.7763 | 6.6511 | 7.9379 | 8.882 | 9.5931 | 10.1248 | 10.5334 | 10.8434 | 11.0717 | 11.2536
| 0.9 | 0.9315 | 4.9022 | 6.828 | 8.1529 | 9.1326 | 9.8591 | 10.4129 | 10.8304 | 11.1482 | 11.3905 | 11.5739 |  | 0.9 | 0.9315 | 4.9022 | 6.828 | 8.1529 | 9.1326 | 9.8591 | 10.4129 | 10.8304 | 11.1482 | 11.3905 | 11.5739
| 0.95 | 0.92768 | 5.025 | 6.9965 | 8.3637 | 9.3758 | 10.1214 | 10.686 | 11.1221 | 11.447 | 11.6996 | 11.8817 |  | 0.95 | 0.92768 | 5.025 | 6.9965 | 8.3637 | 9.3758 | 10.1214 | 10.686 | 11.1221 | 11.447 | 11.6996 | 11.8817
| 1 | 0.92 | 5.1478 | 7.1686 | 8.5684 | 9.6076 | 10.3763 | 10.9594 | 11.3996 | 11.7301 | 11.9971 | 12.1884 |  | 1 | 0.92 | 5.1478 | 7.1686 | 8.5684 | 9.6076 | 10.3763 | 10.9594 | 11.3996 | 11.7301 | 11.9971 | 12.1884
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.018094 | 0.017918 | 0.019047 | 0.0214 | 0.023689 | 0.025519 | 0.027793 | 0.03316 | 0.033109 | 0.03495 | 0.037059 |  | 0.05 | 0.018094 | 0.017918 | 0.019047 | 0.0214 | 0.023689 | 0.025519 | 0.027793 | 0.03316 | 0.033109 | 0.03495 | 0.037059
| 0.1 | 0.01929 | 0.02424 | 0.029654 | 0.039731 | 0.040352 | 0.045327 | 0.055674 | 0.056939 | 0.062861 | 0.068783 | 0.071744 |  | 0.1 | 0.01929 | 0.02424 | 0.029654 | 0.039731 | 0.040352 | 0.045327 | 0.055674 | 0.056939 | 0.062861 | 0.068783 | 0.071744
| 0.15 | 0.012725 | 0.029043 | 0.040053 | 0.048728 | 0.057708 | 0.063874 | 0.072796 | 0.074969 | 0.080485 | 0.086562 | 0.089475 |  | 0.15 | 0.012725 | 0.029043 | 0.040053 | 0.048728 | 0.057708 | 0.063874 | 0.072796 | 0.074969 | 0.080485 | 0.086562 | 0.089475
| 0.2 | 0.011184 | 0.030519 | 0.050568 | 0.066475 | 0.075063 | 0.082421 | 0.089918 | 0.092999 | 0.098109 | 0.10434 | 0.10721 |  | 0.2 | 0.011184 | 0.030519 | 0.050568 | 0.066475 | 0.075063 | 0.082421 | 0.089918 | 0.092999 | 0.098109 | 0.10434 | 0.10721
| 0.25 | 0.0078307 | 0.03984 | 0.061576 | 0.077335 | 0.092419 | 0.10097 | 0.10704 | 0.11103 | 0.11573 | 0.12212 | 0.12494 |  | 0.25 | 0.0078307 | 0.03984 | 0.061576 | 0.077335 | 0.092419 | 0.10097 | 0.10704 | 0.11103 | 0.11573 | 0.12212 | 0.12494
| 0.3 | 0.0040949 | 0.041708 | 0.070647 | 0.088195 | 0.10977 | 0.11952 | 0.12416 | 0.12906 | 0.13336 | 0.13718 | 0.13751 |  | 0.3 | 0.0040949 | 0.041708 | 0.070647 | 0.088195 | 0.10977 | 0.11952 | 0.12416 | 0.12906 | 0.13336 | 0.13718 | 0.13751
| 0.35 | 0.0032426 | 0.052304 | 0.079718 | 0.099055 | 0.12084 | 0.12965 | 0.13673 | 0.14268 | 0.14586 | 0.15169 | 0.15279 |  | 0.35 | 0.0032426 | 0.052304 | 0.079718 | 0.099055 | 0.12084 | 0.12965 | 0.13673 | 0.14268 | 0.14586 | 0.15169 | 0.15279
| 0.4 | 0.0022728 | 0.051461 | 0.08879 | 0.10992 | 0.12918 | 0.14026 | 0.14792 | 0.15534 | 0.15984 | 0.16236 | 0.16751 |  | 0.4 | 0.0022728 | 0.051461 | 0.08879 | 0.10992 | 0.12918 | 0.14026 | 0.14792 | 0.15534 | 0.15984 | 0.16236 | 0.16751
| 0.45 | 0.001252 | 0.056597 | 0.097861 | 0.12078 | 0.13843 | 0.15168 | 0.15912 | 0.16673 | 0.17176 | 0.17548 | 0.17858 |  | 0.45 | 0.001252 | 0.056597 | 0.097861 | 0.12078 | 0.13843 | 0.15168 | 0.15912 | 0.16673 | 0.17176 | 0.17548 | 0.17858
| 0.5 | 8.2397e-05 | 0.061732 | 0.10693 | 0.1328 | 0.15055 | 0.15903 | 0.16936 | 0.17551 | 0.18334 | 0.18805 | 0.19043 |  | 0.5 | 8.2397e-05 | 0.061732 | 0.10693 | 0.1328 | 0.15055 | 0.15903 | 0.16936 | 0.17551 | 0.18334 | 0.18805 | 0.19043
| 0.55 | 0.00058713 | 0.066867 | 0.10942 | 0.13861 | 0.15425 | 0.16768 | 0.17919 | 0.18578 | 0.19267 | 0.19932 | 0.20273 |  | 0.55 | 0.00058713 | 0.066867 | 0.10942 | 0.13861 | 0.15425 | 0.16768 | 0.17919 | 0.18578 | 0.19267 | 0.19932 | 0.20273
| 0.6 | -0.0013396 | 0.072003 | 0.11844 | 0.14342 | 0.16244 | 0.17633 | 0.18797 | 0.19816 | 0.20271 | 0.20852 | 0.21256 |  | 0.6 | -0.0013396 | 0.072003 | 0.11844 | 0.14342 | 0.16244 | 0.17633 | 0.18797 | 0.19816 | 0.20271 | 0.20852 | 0.21256
| 0.65 | -0.00081036 | 0.077138 | 0.12154 | 0.14846 | 0.16958 | 0.18689 | 0.19751 | 0.20664 | 0.21356 | 0.21921 | 0.2235 |  | 0.65 | -0.00081036 | 0.077138 | 0.12154 | 0.14846 | 0.16958 | 0.18689 | 0.19751 | 0.20664 | 0.21356 | 0.21921 | 0.2235
| 0.7 | -0.0013952 | 0.082273 | 0.13062 | 0.15712 | 0.1776 | 0.19555 | 0.20666 | 0.21785 | 0.22334 | 0.22974 | 0.23091 |  | 0.7 | -0.0013952 | 0.082273 | 0.13062 | 0.15712 | 0.1776 | 0.19555 | 0.20666 | 0.21785 | 0.22334 | 0.22974 | 0.23091
| 0.75 | -0.0039209 | 0.084544 | 0.13562 | 0.16364 | 0.18575 | 0.20225 | 0.21561 | 0.22665 | 0.23332 | 0.23834 | 0.2421 |  | 0.75 | -0.0039209 | 0.084544 | 0.13562 | 0.16364 | 0.18575 | 0.20225 | 0.21561 | 0.22665 | 0.23332 | 0.23834 | 0.2421
| 0.8 | -0.0025234 | 0.080393 | 0.14245 | 0.17026 | 0.19338 | 0.21102 | 0.22429 | 0.23406 | 0.23962 | 0.24702 | 0.25203 |  | 0.8 | -0.0025234 | 0.080393 | 0.14245 | 0.17026 | 0.19338 | 0.21102 | 0.22429 | 0.23406 | 0.23962 | 0.24702 | 0.25203
| 0.85 | -0.0032108 | 0.086124 | 0.14707 | 0.17491 | 0.20101 | 0.21875 | 0.23266 | 0.24329 | 0.24998 | 0.25549 | 0.25961 |  | 0.85 | -0.0032108 | 0.086124 | 0.14707 | 0.17491 | 0.20101 | 0.21875 | 0.23266 | 0.24329 | 0.24998 | 0.25549 | 0.25961
| 0.9 | -0.0037316 | 0.092085 | 0.14946 | 0.18151 | 0.20675 | 0.22566 | 0.24131 | 0.24884 | 0.25809 | 0.26327 | 0.2692 |  | 0.9 | -0.0037316 | 0.092085 | 0.14946 | 0.18151 | 0.20675 | 0.22566 | 0.24131 | 0.24884 | 0.25809 | 0.26327 | 0.2692
| 0.95 | -0.0037417 | 0.098045 | 0.15222 | 0.18842 | 0.21407 | 0.23301 | 0.24667 | 0.25744 | 0.26724 | 0.27306 | 0.27781 |  | 0.95 | -0.0037417 | 0.098045 | 0.15222 | 0.18842 | 0.21407 | 0.23301 | 0.24667 | 0.25744 | 0.26724 | 0.27306 | 0.27781
| 1 | -0.0023712 | 0.10258 | 0.15663 | 0.19392 | 0.21983 | 0.24095 | 0.25452 | 0.26412 | 0.27581 | 0.28091 | 0.28383 |  | 1 | -0.0023712 | 0.10258 | 0.15663 | 0.19392 | 0.21983 | 0.24095 | 0.25452 | 0.26412 | 0.27581 | 0.28091 | 0.28383
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.00016021 | -0.0062161 | -0.010434 | -0.013385 | -0.01559 | -0.017083 | -0.018061 | -0.019045 | -0.019676 | -0.020052 | -0.020373 |  | 0.05 | 0.00016021 | -0.0062161 | -0.010434 | -0.013385 | -0.01559 | -0.017083 | -0.018061 | -0.019045 | -0.019676 | -0.020052 | -0.020373
| 0.1 | 0.001009 | -0.009562 | -0.016451 | -0.020874 | -0.02398 | -0.026485 | -0.026685 | -0.028077 | -0.028838 | -0.029098 | -0.029807 |  | 0.1 | 0.001009 | -0.009562 | -0.016451 | -0.020874 | -0.02398 | -0.026485 | -0.026685 | -0.028077 | -0.028838 | -0.029098 | -0.029807
| 0.15 | 0.00091995 | -0.012905 | -0.021478 | -0.026232 | -0.027886 | -0.031199 | -0.032881 | -0.034192 | -0.0346 | -0.035558 | -0.036154 |  | 0.15 | 0.00091995 | -0.012905 | -0.021478 | -0.026232 | -0.027886 | -0.031199 | -0.032881 | -0.034192 | -0.0346 | -0.035558 | -0.036154
| 0.2 | 0.00062681 | -0.015957 | -0.025008 | -0.029619 | -0.0321 | -0.036274 | -0.037549 | -0.039125 | -0.039598 | -0.040997 | -0.041408 |  | 0.2 | 0.00062681 | -0.015957 | -0.025008 | -0.029619 | -0.0321 | -0.036274 | -0.037549 | -0.039125 | -0.039598 | -0.040997 | -0.041408
| 0.25 | 0.00043437 | -0.0184 | -0.025624 | -0.031887 | -0.035344 | -0.041348 | -0.041758 | -0.043534 | -0.044596 | -0.045803 | -0.04718 |  | 0.25 | 0.00043437 | -0.0184 | -0.025624 | -0.031887 | -0.035344 | -0.041348 | -0.041758 | -0.043534 | -0.044596 | -0.045803 | -0.04718
| 0.3 | 0.00013067 | -0.020537 | -0.029118 | -0.034442 | -0.039265 | -0.04389 | -0.046377 | -0.048818 | -0.049459 | -0.050216 | -0.051258 |  | 0.3 | 0.00013067 | -0.020537 | -0.029118 | -0.034442 | -0.039265 | -0.04389 | -0.046377 | -0.048818 | -0.049459 | -0.050216 | -0.051258
| 0.35 | 0.00020022 | -0.022317 | -0.03094 | -0.037402 | -0.043197 | -0.046825 | -0.049257 | -0.051644 | -0.053262 | -0.05461 | -0.055346 |  | 0.35 | 0.00020022 | -0.022317 | -0.03094 | -0.037402 | -0.043197 | -0.046825 | -0.049257 | -0.051644 | -0.053262 | -0.05461 | -0.055346
| 0.4 | -0.00011299 | -0.024539 | -0.032653 | -0.040661 | -0.045883 | -0.049946 | -0.053168 | -0.055031 | -0.056896 | -0.058631 | -0.059675 |  | 0.4 | -0.00011299 | -0.024539 | -0.032653 | -0.040661 | -0.045883 | -0.049946 | -0.053168 | -0.055031 | -0.056896 | -0.058631 | -0.059675
| 0.45 | -0.00035398 | -0.025328 | -0.03466 | -0.042952 | -0.04842 | -0.052884 | -0.056058 | -0.058502 | -0.060653 | -0.061849 | -0.063232 |  | 0.45 | -0.00035398 | -0.025328 | -0.03466 | -0.042952 | -0.04842 | -0.052884 | -0.056058 | -0.058502 | -0.060653 | -0.061849 | -0.063232
| 0.5 | -0.0001539 | -0.026117 | -0.036668 | -0.044972 | -0.050991 | -0.055524 | -0.059461 | -0.061787 | -0.063864 | -0.065511 | -0.066789 |  | 0.5 | -0.0001539 | -0.026117 | -0.036668 | -0.044972 | -0.050991 | -0.055524 | -0.059461 | -0.061787 | -0.063864 | -0.065511 | -0.066789
| 0.55 | -0.00037583 | -0.026675 | -0.038342 | -0.047105 | -0.053771 | -0.058527 | -0.062275 | -0.064861 | -0.06719 | -0.068864 | -0.069883 |  | 0.55 | -0.00037583 | -0.026675 | -0.038342 | -0.047105 | -0.053771 | -0.058527 | -0.062275 | -0.064861 | -0.06719 | -0.068864 | -0.069883
| 0.6 | -0.00046807 | -0.028897 | -0.040039 | -0.049585 | -0.055794 | -0.0611 | -0.065033 | -0.067949 | -0.069943 | -0.071847 | -0.073122 |  | 0.6 | -0.00046807 | -0.028897 | -0.040039 | -0.049585 | -0.055794 | -0.0611 | -0.065033 | -0.067949 | -0.069943 | -0.071847 | -0.073122
| 0.65 | -0.00040653 | -0.030112 | -0.041545 | -0.051323 | -0.058205 | -0.063693 | -0.067748 | -0.07082 | -0.073018 | -0.07484 | -0.076292 |  | 0.65 | -0.00040653 | -0.030112 | -0.041545 | -0.051323 | -0.058205 | -0.063693 | -0.067748 | -0.07082 | -0.073018 | -0.07484 | -0.076292
| 0.7 | -0.00046441 | -0.029546 | -0.043577 | -0.05307 | -0.060759 | -0.065977 | -0.070352 | -0.07341 | -0.07598 | -0.077719 | -0.079234 |  | 0.7 | -0.00046441 | -0.029546 | -0.043577 | -0.05307 | -0.060759 | -0.065977 | -0.070352 | -0.07341 | -0.07598 | -0.077719 | -0.079234
| 0.75 | -0.00060899 | -0.030808 | -0.04475 | -0.055078 | -0.062845 | -0.068385 | -0.07288 | -0.07622 | -0.078552 | -0.080423 | -0.081826 |  | 0.75 | -0.00060899 | -0.030808 | -0.04475 | -0.055078 | -0.062845 | -0.068385 | -0.07288 | -0.07622 | -0.078552 | -0.080423 | -0.081826
| 0.8 | -0.0008259 | -0.032069 | -0.046035 | -0.056871 | -0.064927 | -0.070806 | -0.075304 | -0.078542 | -0.081437 | -0.083469 | -0.084738 |  | 0.8 | -0.0008259 | -0.032069 | -0.046035 | -0.056871 | -0.064927 | -0.070806 | -0.075304 | -0.078542 | -0.081437 | -0.083469 | -0.084738
| 0.85 | -0.00061212 | -0.03333 | -0.047992 | -0.058741 | -0.067044 | -0.072798 | -0.077625 | -0.080986 | -0.083824 | -0.08592 | -0.087582 |  | 0.85 | -0.00061212 | -0.03333 | -0.047992 | -0.058741 | -0.067044 | -0.072798 | -0.077625 | -0.080986 | -0.083824 | -0.08592 | -0.087582
| 0.9 | -0.00077799 | -0.034591 | -0.049144 | -0.060445 | -0.068971 | -0.074942 | -0.07977 | -0.083494 | -0.086352 | -0.088391 | -0.09022 |  | 0.9 | -0.00077799 | -0.034591 | -0.049144 | -0.060445 | -0.068971 | -0.074942 | -0.07977 | -0.083494 | -0.086352 | -0.088391 | -0.09022
| 0.95 | -0.00074801 | -0.034881 | -0.050421 | -0.062124 | -0.070779 | -0.076866 | -0.081898 | -0.085823 | -0.088661 | -0.09115 | -0.092682 |  | 0.95 | -0.00074801 | -0.034881 | -0.050421 | -0.062124 | -0.070779 | -0.076866 | -0.081898 | -0.085823 | -0.088661 | -0.09115 | -0.092682
| 1 | -0.00074398 | -0.035171 | -0.052011 | -0.064002 | -0.072762 | -0.079168 | -0.08411 | -0.088027 | -0.091211 | -0.093001 | -0.094959 |  | 1 | -0.00074398 | -0.035171 | -0.052011 | -0.064002 | -0.072762 | -0.079168 | -0.08411 | -0.088027 | -0.091211 | -0.093001 | -0.094959
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∗∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS3_LS< (hidden)
If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.02 | 1.0517 | 1.0833 | 1.1041 | 1.1152 | 1.1194 | 1.1189 | 1.1149 | 1.1086 | 1.1006 | 1.0915
| 0.1 | 1.0122 | 1.0596 | 1.1045 | 1.1328 | 1.1477 | 1.1523 | 1.1505 | 1.1447 | 1.1372 | 1.1279 | 1.1174
| 0.15 | 0.98432 | 1.0576 | 1.1126 | 1.1443 | 1.1587 | 1.1644 | 1.1637 | 1.1585 | 1.1504 | 1.1403 | 1.1289
| 0.2 | 0.95186 | 1.0506 | 1.1135 | 1.1491 | 1.1652 | 1.1725 | 1.1724 | 1.1673 | 1.1589 | 1.1484 | 1.1364
| 0.25 | 0.92133 | 1.0429 | 1.1124 | 1.1508 | 1.1698 | 1.1786 | 1.1789 | 1.1737 | 1.165 | 1.154 | 1.1415
| 0.3 | 0.89447 | 1.036 | 1.1116 | 1.1517 | 1.1738 | 1.1833 | 1.1837 | 1.1783 | 1.1693 | 1.158 | 1.1452
| 0.35 | 0.87138 | 1.0299 | 1.11 | 1.1525 | 1.1771 | 1.1869 | 1.1872 | 1.1817 | 1.1725 | 1.161 | 1.1479
| 0.4 | 0.85165 | 1.0246 | 1.1083 | 1.1537 | 1.1797 | 1.1897 | 1.19 | 1.1844 | 1.1751 | 1.1634 | 1.1502
| 0.45 | 0.83475 | 1.02 | 1.1067 | 1.155 | 1.1818 | 1.1919 | 1.1923 | 1.1866 | 1.1772 | 1.1654 | 1.1521
| 0.5 | 0.8202 | 1.016 | 1.1052 | 1.1563 | 1.1834 | 1.1937 | 1.1942 | 1.1885 | 1.179 | 1.1671 | 1.1537
| 0.55 | 0.8076 | 1.0125 | 1.1041 | 1.1573 | 1.1848 | 1.1953 | 1.1958 | 1.1901 | 1.1806 | 1.1686 | 1.155
| 0.6 | 0.79661 | 1.0093 | 1.1032 | 1.1582 | 1.186 | 1.1967 | 1.1973 | 1.1916 | 1.1819 | 1.1698 | 1.1562
| 0.65 | 0.78696 | 1.0064 | 1.1028 | 1.1589 | 1.1871 | 1.198 | 1.1986 | 1.1928 | 1.1831 | 1.1709 | 1.1572
| 0.7 | 0.77843 | 1.0038 | 1.1028 | 1.1595 | 1.1881 | 1.1991 | 1.1997 | 1.1939 | 1.1842 | 1.1719 | 1.1581
| 0.75 | 0.77084 | 1.0015 | 1.1029 | 1.1601 | 1.189 | 1.2001 | 1.2007 | 1.1949 | 1.1851 | 1.1728 | 1.1589
| 0.8 | 0.76405 | 0.99933 | 1.103 | 1.1607 | 1.1898 | 1.201 | 1.2016 | 1.1958 | 1.1859 | 1.1736 | 1.1596
| 0.85 | 0.75795 | 0.99739 | 1.103 | 1.1612 | 1.1906 | 1.2018 | 1.2024 | 1.1966 | 1.1867 | 1.1743 | 1.1603
| 0.9 | 0.75244 | 0.99563 | 1.103 | 1.1617 | 1.1912 | 1.2026 | 1.2032 | 1.1973 | 1.1874 | 1.1749 | 1.1609
| 0.95 | 0.74743 | 0.99405 | 1.103 | 1.1621 | 1.1919 | 1.2032 | 1.2039 | 1.198 | 1.188 | 1.1755 | 1.1615
| 1 | 0.74287 | 0.99263 | 1.1029 | 1.1626 | 1.1925 | 1.2039 | 1.2045 | 1.1986 | 1.1886 | 1.1761 | 1.162
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
| 0.05 | 1.0784 | 1.045 | 1.0131 | 0.98312 | 0.95496 | 0.9285 | 0.90431 | 0.88103 | 0.85933 | 0.83896 | 0.81983
| 0.1 | 0.95465 | 0.89725 | 0.85388 | 0.81738 | 0.78491 | 0.75558 | 0.72901 | 0.70459 | 0.68239 | 0.66201 | 0.64322
| 0.15 | 0.89423 | 0.81195 | 0.76211 | 0.72247 | 0.68776 | 0.65722 | 0.6304 | 0.60625 | 0.58471 | 0.56518 | 0.54756
| 0.2 | 0.85996 | 0.75304 | 0.69879 | 0.6563 | 0.62016 | 0.58934 | 0.56296 | 0.53984 | 0.51922 | 0.50097 | 0.48475
| 0.25 | 0.83795 | 0.70938 | 0.6506 | 0.60558 | 0.56892 | 0.53869 | 0.51314 | 0.4911 | 0.47163 | 0.45477 | 0.4395
| 0.3 | 0.82199 | 0.67458 | 0.61147 | 0.56481 | 0.5284 | 0.49889 | 0.47441 | 0.45338 | 0.4353 | 0.41925 | 0.40484
| 0.35 | 0.81088 | 0.64552 | 0.57868 | 0.53107 | 0.49529 | 0.46675 | 0.4433 | 0.42335 | 0.40598 | 0.39084 | 0.37748
| 0.4 | 0.80175 | 0.62061 | 0.55026 | 0.50265 | 0.46767 | 0.44014 | 0.4176 | 0.39849 | 0.38203 | 0.36771 | 0.35484
| 0.45 | 0.79512 | 0.59888 | 0.52569 | 0.47834 | 0.44406 | 0.41753 | 0.39585 | 0.37754 | 0.36194 | 0.34819 | 0.33606
| 0.5 | 0.78989 | 0.57907 | 0.50418 | 0.45698 | 0.42367 | 0.39814 | 0.37739 | 0.35974 | 0.34466 | 0.33155 | 0.31999
| 0.55 | 0.7849 | 0.56136 | 0.48491 | 0.43837 | 0.40602 | 0.38124 | 0.36106 | 0.34435 | 0.32975 | 0.31722 | 0.30599
| 0.6 | 0.78129 | 0.5453 | 0.46759 | 0.42186 | 0.39032 | 0.36633 | 0.34703 | 0.3306 | 0.31669 | 0.30432 | 0.29365
| 0.65 | 0.77762 | 0.53025 | 0.45205 | 0.40704 | 0.37642 | 0.35319 | 0.33428 | 0.31846 | 0.30497 | 0.29309 | 0.28279
| 0.7 | 0.77509 | 0.5166 | 0.43796 | 0.39375 | 0.36376 | 0.34126 | 0.32293 | 0.30769 | 0.29455 | 0.28317 | 0.27301
| 0.75 | 0.77292 | 0.50396 | 0.42509 | 0.3816 | 0.35246 | 0.33055 | 0.3128 | 0.29784 | 0.2851 | 0.27391 | 0.26419
| 0.8 | 0.7703 | 0.49199 | 0.41312 | 0.37066 | 0.34228 | 0.32062 | 0.30342 | 0.28879 | 0.27649 | 0.26565 | 0.25616
| 0.85 | 0.76877 | 0.48092 | 0.40232 | 0.36055 | 0.33274 | 0.31175 | 0.2948 | 0.28069 | 0.26856 | 0.25804 | 0.24883
| 0.9 | 0.76658 | 0.47053 | 0.39233 | 0.35127 | 0.32412 | 0.30343 | 0.28694 | 0.27313 | 0.26143 | 0.25112 | 0.24207
| 0.95 | 0.76536 | 0.46062 | 0.38289 | 0.34264 | 0.31589 | 0.29583 | 0.27961 | 0.26616 | 0.25471 | 0.24472 | 0.23593
| 1 | 0.76427 | 0.45145 | 0.37407 | 0.33463 | 0.30845 | 0.28887 | 0.27292 | 0.25985 | 0.24839 | 0.23874 | 0.23019
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.012754 | 0.013599 | 0.014041 | 0.014362 | 0.014606 | 0.014769 | 0.014871 | 0.014858 | 0.01494 | 0.015013 | 0.014994
| 0.1 | 0.011232 | 0.013302 | 0.01376 | 0.01402 | 0.014226 | 0.014306 | 0.014267 | 0.014271 | 0.014177 | 0.013993 | 0.013831
| 0.15 | 0.0096854 | 0.012509 | 0.013172 | 0.013758 | 0.013941 | 0.013887 | 0.013666 | 0.013503 | 0.013227 | 0.012964 | 0.012666
| 0.2 | 0.0082681 | 0.012042 | 0.013033 | 0.013484 | 0.013483 | 0.013271 | 0.012908 | 0.012607 | 0.012287 | 0.01196 | 0.01168
| 0.25 | 0.0072946 | 0.011605 | 0.012982 | 0.01314 | 0.012965 | 0.012548 | 0.012196 | 0.011818 | 0.011439 | 0.01112 | 0.01079
| 0.3 | 0.006766 | 0.011463 | 0.012787 | 0.012693 | 0.012403 | 0.011937 | 0.011516 | 0.011084 | 0.010782 | 0.01041 | 0.010124
| 0.35 | 0.0060937 | 0.011473 | 0.012508 | 0.01232 | 0.011832 | 0.011369 | 0.01093 | 0.010505 | 0.010118 | 0.0098004 | 0.0095085
| 0.4 | 0.0056809 | 0.011378 | 0.012214 | 0.011928 | 0.011341 | 0.010851 | 0.010391 | 0.0099886 | 0.009619 | 0.0093137 | 0.0089973
| 0.45 | 0.0053534 | 0.01139 | 0.012 | 0.01148 | 0.010897 | 0.010413 | 0.0099528 | 0.0095613 | 0.0091728 | 0.0088843 | 0.0085771
| 0.5 | 0.0050772 | 0.011357 | 0.011641 | 0.011095 | 0.010513 | 0.0099988 | 0.0095238 | 0.0091614 | 0.0087897 | 0.0085183 | 0.0082408
| 0.55 | 0.0047117 | 0.011317 | 0.011419 | 0.010759 | 0.010146 | 0.0096073 | 0.0091824 | 0.0088134 | 0.0084679 | 0.0081669 | 0.0079163
| 0.6 | 0.0046672 | 0.011203 | 0.011108 | 0.01043 | 0.0098168 | 0.0092979 | 0.0088667 | 0.0085287 | 0.0081706 | 0.0078863 | 0.0076137
| 0.65 | 0.0043509 | 0.01113 | 0.010855 | 0.010137 | 0.0095009 | 0.0090077 | 0.0085576 | 0.0081995 | 0.0079236 | 0.0076261 | 0.0073682
| 0.7 | 0.0042072 | 0.011013 | 0.010615 | 0.0098579 | 0.0092513 | 0.0087682 | 0.0083029 | 0.0079922 | 0.007641 | 0.0073838 | 0.0071352
| 0.75 | 0.0042457 | 0.010934 | 0.010392 | 0.0095953 | 0.008968 | 0.0085034 | 0.0080904 | 0.0077632 | 0.0074211 | 0.0071862 | 0.0069049
| 0.8 | 0.0039967 | 0.010803 | 0.010179 | 0.0093623 | 0.0087515 | 0.0082827 | 0.0078856 | 0.0075113 | 0.0072119 | 0.0069564 | 0.0067338
| 0.85 | 0.0038984 | 0.010698 | 0.0099417 | 0.0091275 | 0.0085548 | 0.0080929 | 0.0076878 | 0.0073456 | 0.0070553 | 0.0067747 | 0.0065598
| 0.9 | 0.0038415 | 0.010607 | 0.0097232 | 0.0089421 | 0.0083257 | 0.0078871 | 0.0075185 | 0.0071616 | 0.0068734 | 0.0066309 | 0.0063643
| 0.95 | 0.003754 | 0.010435 | 0.0095673 | 0.0087285 | 0.008145 | 0.0077064 | 0.0072986 | 0.006999 | 0.0067213 | 0.006462 | 0.0062154
| 1 | 0.003552 | 0.010365 | 0.0093634 | 0.0085633 | 0.0079862 | 0.0075681 | 0.0071547 | 0.0068204 | 0.0065463 | 0.0063031 | 0.0060798
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0029204 | 0.003322 | 0.0035683 | 0.003727 | 0.0038428 | 0.0039327 | 0.0039857 | 0.0040515 | 0.0040811 | 0.004103 | 0.0041138
| 0.1 | 0.002528 | 0.0033759 | 0.0036195 | 0.0037536 | 0.0038415 | 0.0038963 | 0.0039029 | 0.0039138 | 0.0038951 | 0.0038587 | 0.0038227
| 0.15 | 0.0020416 | 0.0032641 | 0.0035291 | 0.0036935 | 0.0037692 | 0.0037841 | 0.0037599 | 0.0037137 | 0.0036574 | 0.0035914 | 0.0035232
| 0.2 | 0.0016728 | 0.0031336 | 0.0034936 | 0.0036521 | 0.0036791 | 0.0036455 | 0.0035818 | 0.0035024 | 0.0034171 | 0.0033383 | 0.0032579
| 0.25 | 0.001405 | 0.0030666 | 0.0034576 | 0.0035821 | 0.003561 | 0.0034865 | 0.003394 | 0.0032984 | 0.0032045 | 0.0031153 | 0.0030326
| 0.3 | 0.0012231 | 0.0030281 | 0.003437 | 0.0034983 | 0.0034324 | 0.0033281 | 0.0032181 | 0.0031117 | 0.0030113 | 0.0029243 | 0.0028361
| 0.35 | 0.0010505 | 0.0030179 | 0.0033906 | 0.0033933 | 0.0032996 | 0.0031774 | 0.0030591 | 0.0029473 | 0.0028459 | 0.0027556 | 0.0026728
| 0.4 | 0.00094797 | 0.0030044 | 0.003336 | 0.003293 | 0.0031689 | 0.0030363 | 0.0029163 | 0.0028065 | 0.0027101 | 0.0026137 | 0.0025345
| 0.45 | 0.00086409 | 0.0030111 | 0.0032788 | 0.0031952 | 0.0030507 | 0.0029115 | 0.0027898 | 0.0026775 | 0.0025801 | 0.0024942 | 0.0024168
| 0.5 | 0.0007626 | 0.0030075 | 0.0032127 | 0.0030944 | 0.0029418 | 0.0028015 | 0.0026779 | 0.0025708 | 0.0024782 | 0.0023879 | 0.0023123
| 0.55 | 0.00071186 | 0.0030083 | 0.0031439 | 0.0030044 | 0.0028413 | 0.0027002 | 0.002578 | 0.0024735 | 0.0023797 | 0.002294 | 0.0022203
| 0.6 | 0.00065059 | 0.0029899 | 0.0030856 | 0.002917 | 0.002746 | 0.0026084 | 0.0024906 | 0.0023832 | 0.0022957 | 0.0022151 | 0.0021408
| 0.65 | 0.0006 | 0.0029822 | 0.0030164 | 0.0028349 | 0.0026648 | 0.0025264 | 0.0024103 | 0.0023074 | 0.0022167 | 0.0021416 | 0.0020666
| 0.7 | 0.00055545 | 0.0029655 | 0.0029574 | 0.0027544 | 0.0025872 | 0.0024539 | 0.0023374 | 0.002238 | 0.0021462 | 0.0020689 | 0.0020024
| 0.75 | 0.00053032 | 0.0029545 | 0.002895 | 0.0026884 | 0.0025167 | 0.0023829 | 0.002271 | 0.0021722 | 0.0020914 | 0.0020113 | 0.0019427
| 0.8 | 0.00051468 | 0.0029303 | 0.0028299 | 0.0026233 | 0.0024518 | 0.002319 | 0.002209 | 0.0021141 | 0.0020247 | 0.0019545 | 0.0018861
| 0.85 | 0.00046317 | 0.0029135 | 0.0027776 | 0.002559 | 0.0023907 | 0.0022659 | 0.0021536 | 0.0020605 | 0.0019759 | 0.001901 | 0.0018391
| 0.9 | 0.00045063 | 0.0028893 | 0.0027213 | 0.0025032 | 0.0023365 | 0.0022103 | 0.0021043 | 0.002008 | 0.0019272 | 0.0018551 | 0.001788
| 0.95 | 0.00042178 | 0.0028692 | 0.0026696 | 0.0024476 | 0.0022855 | 0.0021635 | 0.0020538 | 0.001959 | 0.0018828 | 0.0018082 | 0.0017479
| 1 | 0.00039926 | 0.0028415 | 0.0026225 | 0.0024032 | 0.0022425 | 0.0021122 | 0.0020072 | 0.0019149 | 0.0018345 | 0.0017713 | 0.0017071
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.2461 | 1.6405 | 1.936 | 2.1652 | 2.3439 | 2.4883 | 2.596 | 2.691 | 2.7682 | 2.836 | 2.8853
| 0.1 | 1.1537 | 1.9519 | 2.4987 | 2.9002 | 3.2 | 3.4303 | 3.6003 | 3.7587 | 3.8616 | 3.9446 | 4.0091
| 0.15 | 1.0928 | 2.2226 | 2.9881 | 3.5318 | 3.8906 | 4.2144 | 4.4305 | 4.6354 | 4.6858 | 4.8962 | 4.9096
| 0.2 | 1.0478 | 2.4803 | 3.4121 | 4.0222 | 4.4721 | 4.803 | 5.0279 | 5.2169 | 5.3702 | 5.4957 | 5.574
| 0.25 | 1.0175 | 2.715 | 3.8686 | 4.4053 | 4.975 | 5.3465 | 5.6171 | 5.8243 | 5.9838 | 6.1058 | 6.194
| 0.3 | 1.0039 | 2.9358 | 4.1073 | 4.8253 | 5.4083 | 5.8287 | 6.109 | 6.363 | 6.5289 | 6.6682 | 6.7754
| 0.35 | 0.98316 | 3.1724 | 4.4157 | 5.2454 | 5.8305 | 6.2726 | 6.5975 | 6.8495 | 7.0343 | 7.1874 | 7.296
| 0.4 | 0.97693 | 3.3692 | 4.6354 | 5.5808 | 6.2014 | 6.6773 | 7.0266 | 7.305 | 7.5102 | 7.6697 | 7.7876
| 0.45 | 0.96663 | 3.5417 | 4.9377 | 5.8959 | 6.572 | 7.0674 | 7.4416 | 7.7315 | 7.9507 | 8.1149 | 8.2493
| 0.5 | 0.95472 | 3.7283 | 5.2105 | 6.1868 | 6.903 | 7.4317 | 7.8269 | 8.131 | 8.3707 | 8.5435 | 8.6786
| 0.55 | 0.95417 | 3.9357 | 5.4223 | 6.4698 | 7.2227 | 7.7781 | 8.1964 | 8.5204 | 8.7679 | 8.9551 | 9.0986
| 0.6 | 0.94709 | 4.0761 | 5.6466 | 6.7427 | 7.5249 | 8.1026 | 8.551 | 8.8841 | 9.1444 | 9.3429 | 9.4936
| 0.65 | 0.9464 | 4.2165 | 5.8683 | 6.9921 | 7.8104 | 8.4297 | 8.8878 | 9.2381 | 9.5071 | 9.7098 | 9.8679
| 0.7 | 0.93915 | 4.363 | 6.0726 | 7.244 | 8.0931 | 8.7325 | 9.2154 | 9.5838 | 9.86 | 10.078 | 10.2359
| 0.75 | 0.93419 | 4.5036 | 6.2688 | 7.4755 | 8.3656 | 9.0326 | 9.5312 | 9.912 | 10.2023 | 10.4207 | 10.5894
| 0.8 | 0.93572 | 4.6239 | 6.468 | 7.7043 | 8.6278 | 9.3131 | 9.834 | 10.2238 | 10.5279 | 10.7568 | 10.92
| 0.85 | 0.92896 | 4.7763 | 6.6511 | 7.9379 | 8.882 | 9.5931 | 10.1248 | 10.5334 | 10.8434 | 11.0717 | 11.2536
| 0.9 | 0.9315 | 4.9022 | 6.828 | 8.1529 | 9.1326 | 9.8591 | 10.4129 | 10.8304 | 11.1482 | 11.3905 | 11.5739
| 0.95 | 0.92768 | 5.025 | 6.9965 | 8.3637 | 9.3758 | 10.1214 | 10.686 | 11.1221 | 11.447 | 11.6996 | 11.8817
| 1 | 0.92 | 5.1478 | 7.1686 | 8.5684 | 9.6076 | 10.3763 | 10.9594 | 11.3996 | 11.7301 | 11.9971 | 12.1884
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.018094 | 0.017918 | 0.019047 | 0.0214 | 0.023689 | 0.025519 | 0.027793 | 0.03316 | 0.033109 | 0.03495 | 0.037059
| 0.1 | 0.01929 | 0.02424 | 0.029654 | 0.039731 | 0.040352 | 0.045327 | 0.055674 | 0.056939 | 0.062861 | 0.068783 | 0.071744
| 0.15 | 0.012725 | 0.029043 | 0.040053 | 0.048728 | 0.057708 | 0.063874 | 0.072796 | 0.074969 | 0.080485 | 0.086562 | 0.089475
| 0.2 | 0.011184 | 0.030519 | 0.050568 | 0.066475 | 0.075063 | 0.082421 | 0.089918 | 0.092999 | 0.098109 | 0.10434 | 0.10721
| 0.25 | 0.0078307 | 0.03984 | 0.061576 | 0.077335 | 0.092419 | 0.10097 | 0.10704 | 0.11103 | 0.11573 | 0.12212 | 0.12494
| 0.3 | 0.0040949 | 0.041708 | 0.070647 | 0.088195 | 0.10977 | 0.11952 | 0.12416 | 0.12906 | 0.13336 | 0.13718 | 0.13751
| 0.35 | 0.0032426 | 0.052304 | 0.079718 | 0.099055 | 0.12084 | 0.12965 | 0.13673 | 0.14268 | 0.14586 | 0.15169 | 0.15279
| 0.4 | 0.0022728 | 0.051461 | 0.08879 | 0.10992 | 0.12918 | 0.14026 | 0.14792 | 0.15534 | 0.15984 | 0.16236 | 0.16751
| 0.45 | 0.001252 | 0.056597 | 0.097861 | 0.12078 | 0.13843 | 0.15168 | 0.15912 | 0.16673 | 0.17176 | 0.17548 | 0.17858
| 0.5 | 8.2397e-05 | 0.061732 | 0.10693 | 0.1328 | 0.15055 | 0.15903 | 0.16936 | 0.17551 | 0.18334 | 0.18805 | 0.19043
| 0.55 | 0.00058713 | 0.066867 | 0.10942 | 0.13861 | 0.15425 | 0.16768 | 0.17919 | 0.18578 | 0.19267 | 0.19932 | 0.20273
| 0.6 | -0.0013396 | 0.072003 | 0.11844 | 0.14342 | 0.16244 | 0.17633 | 0.18797 | 0.19816 | 0.20271 | 0.20852 | 0.21256
| 0.65 | -0.00081036 | 0.077138 | 0.12154 | 0.14846 | 0.16958 | 0.18689 | 0.19751 | 0.20664 | 0.21356 | 0.21921 | 0.2235
| 0.7 | -0.0013952 | 0.082273 | 0.13062 | 0.15712 | 0.1776 | 0.19555 | 0.20666 | 0.21785 | 0.22334 | 0.22974 | 0.23091
| 0.75 | -0.0039209 | 0.084544 | 0.13562 | 0.16364 | 0.18575 | 0.20225 | 0.21561 | 0.22665 | 0.23332 | 0.23834 | 0.2421
| 0.8 | -0.0025234 | 0.080393 | 0.14245 | 0.17026 | 0.19338 | 0.21102 | 0.22429 | 0.23406 | 0.23962 | 0.24702 | 0.25203
| 0.85 | -0.0032108 | 0.086124 | 0.14707 | 0.17491 | 0.20101 | 0.21875 | 0.23266 | 0.24329 | 0.24998 | 0.25549 | 0.25961
| 0.9 | -0.0037316 | 0.092085 | 0.14946 | 0.18151 | 0.20675 | 0.22566 | 0.24131 | 0.24884 | 0.25809 | 0.26327 | 0.2692
| 0.95 | -0.0037417 | 0.098045 | 0.15222 | 0.18842 | 0.21407 | 0.23301 | 0.24667 | 0.25744 | 0.26724 | 0.27306 | 0.27781
| 1 | -0.0023712 | 0.10258 | 0.15663 | 0.19392 | 0.21983 | 0.24095 | 0.25452 | 0.26412 | 0.27581 | 0.28091 | 0.28383
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.00016021 | -0.0062161 | -0.010434 | -0.013385 | -0.01559 | -0.017083 | -0.018061 | -0.019045 | -0.019676 | -0.020052 | -0.020373
| 0.1 | 0.001009 | -0.009562 | -0.016451 | -0.020874 | -0.02398 | -0.026485 | -0.026685 | -0.028077 | -0.028838 | -0.029098 | -0.029807
| 0.15 | 0.00091995 | -0.012905 | -0.021478 | -0.026232 | -0.027886 | -0.031199 | -0.032881 | -0.034192 | -0.0346 | -0.035558 | -0.036154
| 0.2 | 0.00062681 | -0.015957 | -0.025008 | -0.029619 | -0.0321 | -0.036274 | -0.037549 | -0.039125 | -0.039598 | -0.040997 | -0.041408
| 0.25 | 0.00043437 | -0.0184 | -0.025624 | -0.031887 | -0.035344 | -0.041348 | -0.041758 | -0.043534 | -0.044596 | -0.045803 | -0.04718
| 0.3 | 0.00013067 | -0.020537 | -0.029118 | -0.034442 | -0.039265 | -0.04389 | -0.046377 | -0.048818 | -0.049459 | -0.050216 | -0.051258
| 0.35 | 0.00020022 | -0.022317 | -0.03094 | -0.037402 | -0.043197 | -0.046825 | -0.049257 | -0.051644 | -0.053262 | -0.05461 | -0.055346
| 0.4 | -0.00011299 | -0.024539 | -0.032653 | -0.040661 | -0.045883 | -0.049946 | -0.053168 | -0.055031 | -0.056896 | -0.058631 | -0.059675
| 0.45 | -0.00035398 | -0.025328 | -0.03466 | -0.042952 | -0.04842 | -0.052884 | -0.056058 | -0.058502 | -0.060653 | -0.061849 | -0.063232
| 0.5 | -0.0001539 | -0.026117 | -0.036668 | -0.044972 | -0.050991 | -0.055524 | -0.059461 | -0.061787 | -0.063864 | -0.065511 | -0.066789
| 0.55 | -0.00037583 | -0.026675 | -0.038342 | -0.047105 | -0.053771 | -0.058527 | -0.062275 | -0.064861 | -0.06719 | -0.068864 | -0.069883
| 0.6 | -0.00046807 | -0.028897 | -0.040039 | -0.049585 | -0.055794 | -0.0611 | -0.065033 | -0.067949 | -0.069943 | -0.071847 | -0.073122
| 0.65 | -0.00040653 | -0.030112 | -0.041545 | -0.051323 | -0.058205 | -0.063693 | -0.067748 | -0.07082 | -0.073018 | -0.07484 | -0.076292
| 0.7 | -0.00046441 | -0.029546 | -0.043577 | -0.05307 | -0.060759 | -0.065977 | -0.070352 | -0.07341 | -0.07598 | -0.077719 | -0.079234
| 0.75 | -0.00060899 | -0.030808 | -0.04475 | -0.055078 | -0.062845 | -0.068385 | -0.07288 | -0.07622 | -0.078552 | -0.080423 | -0.081826
| 0.8 | -0.0008259 | -0.032069 | -0.046035 | -0.056871 | -0.064927 | -0.070806 | -0.075304 | -0.078542 | -0.081437 | -0.083469 | -0.084738
| 0.85 | -0.00061212 | -0.03333 | -0.047992 | -0.058741 | -0.067044 | -0.072798 | -0.077625 | -0.080986 | -0.083824 | -0.08592 | -0.087582
| 0.9 | -0.00077799 | -0.034591 | -0.049144 | -0.060445 | -0.068971 | -0.074942 | -0.07977 | -0.083494 | -0.086352 | -0.088391 | -0.09022
| 0.95 | -0.00074801 | -0.034881 | -0.050421 | -0.062124 | -0.070779 | -0.076866 | -0.081898 | -0.085823 | -0.088661 | -0.09115 | -0.092682
| 1 | -0.00074398 | -0.035171 | -0.052011 | -0.064002 | -0.072762 | -0.079168 | -0.08411 | -0.088027 | -0.091211 | -0.093001 | -0.094959
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∗∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-18.05) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-65.87))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-18.05) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-65.87))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS4_LS>= (hidden)
If Iload/Isc x 5.6569 ≥1 | [12 empty] | If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 |  | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0226 | 1.0387 | 1.0502 | 1.06 | 1.0649 | 1.0669 | 1.0666 | 1.0644 | 1.0608 | 1.0559 | 1.0509 |  | 0.05 | 1.0226 | 1.0387 | 1.0502 | 1.06 | 1.0649 | 1.0669 | 1.0666 | 1.0644 | 1.0608 | 1.0559 | 1.0509
| 0.1 | 1.0438 | 1.0719 | 1.0989 | 1.1165 | 1.1251 | 1.1275 | 1.1254 | 1.1201 | 1.1127 | 1.1038 | 1.0934 |  | 0.1 | 1.0438 | 1.0719 | 1.0989 | 1.1165 | 1.1251 | 1.1275 | 1.1254 | 1.1201 | 1.1127 | 1.1038 | 1.0934
| 0.15 | 1.0438 | 1.0826 | 1.1156 | 1.1384 | 1.1489 | 1.1511 | 1.1481 | 1.1423 | 1.1349 | 1.1257 | 1.1146 |  | 0.15 | 1.0438 | 1.0826 | 1.1156 | 1.1384 | 1.1489 | 1.1511 | 1.1481 | 1.1423 | 1.1349 | 1.1257 | 1.1146
| 0.2 | 1.0332 | 1.0864 | 1.127 | 1.1515 | 1.1631 | 1.1662 | 1.1636 | 1.1573 | 1.1484 | 1.1379 | 1.1252 |  | 0.2 | 1.0332 | 1.0864 | 1.127 | 1.1515 | 1.1631 | 1.1662 | 1.1636 | 1.1573 | 1.1484 | 1.1379 | 1.1252
| 0.25 | 1.0226 | 1.0838 | 1.1329 | 1.1602 | 1.1727 | 1.1757 | 1.1727 | 1.1657 | 1.1562 | 1.145 | 1.1323 |  | 0.25 | 1.0226 | 1.0838 | 1.1329 | 1.1602 | 1.1727 | 1.1757 | 1.1727 | 1.1657 | 1.1562 | 1.145 | 1.1323
| 0.3 | 1.0049 | 1.0787 | 1.1348 | 1.1646 | 1.178 | 1.1814 | 1.1784 | 1.1712 | 1.1614 | 1.1497 | 1.1358 |  | 0.3 | 1.0049 | 1.0787 | 1.1348 | 1.1646 | 1.178 | 1.1814 | 1.1784 | 1.1712 | 1.1614 | 1.1497 | 1.1358
| 0.35 | 0.98723 | 1.0727 | 1.1347 | 1.1669 | 1.1814 | 1.1852 | 1.1823 | 1.1751 | 1.1651 | 1.1533 | 1.1394 |  | 0.35 | 0.98723 | 1.0727 | 1.1347 | 1.1669 | 1.1814 | 1.1852 | 1.1823 | 1.1751 | 1.1651 | 1.1533 | 1.1394
| 0.4 | 0.96954 | 1.0666 | 1.1337 | 1.168 | 1.1836 | 1.1879 | 1.1852 | 1.1781 | 1.1681 | 1.1563 | 1.1429 |  | 0.4 | 0.96954 | 1.0666 | 1.1337 | 1.168 | 1.1836 | 1.1879 | 1.1852 | 1.1781 | 1.1681 | 1.1563 | 1.1429
| 0.45 | 0.95185 | 1.0609 | 1.1322 | 1.1685 | 1.1851 | 1.19 | 1.1876 | 1.1807 | 1.1709 | 1.1591 | 1.1465 |  | 0.45 | 0.95185 | 1.0609 | 1.1322 | 1.1685 | 1.1851 | 1.19 | 1.1876 | 1.1807 | 1.1709 | 1.1591 | 1.1465
| 0.5 | 0.93769 | 1.0558 | 1.1305 | 1.1687 | 1.1862 | 1.1917 | 1.1898 | 1.1832 | 1.1735 | 1.1617 | 1.15 |  | 0.5 | 0.93769 | 1.0558 | 1.1305 | 1.1687 | 1.1862 | 1.1917 | 1.1898 | 1.1832 | 1.1735 | 1.1617 | 1.15
| 0.55 | 0.92354 | 1.0511 | 1.1289 | 1.1686 | 1.1871 | 1.1933 | 1.1919 | 1.1855 | 1.1759 | 1.164 | 1.15 |  | 0.55 | 0.92354 | 1.0511 | 1.1289 | 1.1686 | 1.1871 | 1.1933 | 1.1919 | 1.1855 | 1.1759 | 1.164 | 1.15
| 0.6 | 0.90938 | 1.0468 | 1.1272 | 1.1684 | 1.188 | 1.195 | 1.194 | 1.1877 | 1.178 | 1.166 | 1.1535 |  | 0.6 | 0.90938 | 1.0468 | 1.1272 | 1.1684 | 1.188 | 1.195 | 1.194 | 1.1877 | 1.178 | 1.166 | 1.1535
| 0.65 | 0.89523 | 1.0428 | 1.1256 | 1.1682 | 1.1889 | 1.1966 | 1.1959 | 1.1896 | 1.1798 | 1.1676 | 1.1535 |  | 0.65 | 0.89523 | 1.0428 | 1.1256 | 1.1682 | 1.1889 | 1.1966 | 1.1959 | 1.1896 | 1.1798 | 1.1676 | 1.1535
| 0.7 | 0.88462 | 1.0392 | 1.124 | 1.168 | 1.1899 | 1.1982 | 1.1977 | 1.1913 | 1.1813 | 1.169 | 1.1535 |  | 0.7 | 0.88462 | 1.0392 | 1.124 | 1.168 | 1.1899 | 1.1982 | 1.1977 | 1.1913 | 1.1813 | 1.169 | 1.1535
| 0.75 | 0.874 | 1.0359 | 1.1225 | 1.168 | 1.1911 | 1.1998 | 1.1992 | 1.1928 | 1.1826 | 1.1702 | 1.1571 |  | 0.75 | 0.874 | 1.0359 | 1.1225 | 1.168 | 1.1911 | 1.1998 | 1.1992 | 1.1928 | 1.1826 | 1.1702 | 1.1571
| 0.8 | 0.86338 | 1.0329 | 1.1211 | 1.1682 | 1.1922 | 1.2011 | 1.2005 | 1.194 | 1.1838 | 1.1713 | 1.1571 |  | 0.8 | 0.86338 | 1.0329 | 1.1211 | 1.1682 | 1.1922 | 1.2011 | 1.2005 | 1.194 | 1.1838 | 1.1713 | 1.1571
| 0.85 | 0.85631 | 1.0301 | 1.1199 | 1.1685 | 1.1933 | 1.2023 | 1.2017 | 1.1951 | 1.1848 | 1.1722 | 1.1571 |  | 0.85 | 0.85631 | 1.0301 | 1.1199 | 1.1685 | 1.1933 | 1.2023 | 1.2017 | 1.1951 | 1.1848 | 1.1722 | 1.1571
| 0.9 | 0.84923 | 1.0275 | 1.1187 | 1.1689 | 1.1943 | 1.2034 | 1.2026 | 1.196 | 1.1856 | 1.1729 | 1.1606 |  | 0.9 | 0.84923 | 1.0275 | 1.1187 | 1.1689 | 1.1943 | 1.2034 | 1.2026 | 1.196 | 1.1856 | 1.1729 | 1.1606
| 0.95 | 0.83862 | 1.0251 | 1.1177 | 1.1694 | 1.1952 | 1.2043 | 1.2035 | 1.1968 | 1.1864 | 1.1736 | 1.1606 |  | 0.95 | 0.83862 | 1.0251 | 1.1177 | 1.1694 | 1.1952 | 1.2043 | 1.2035 | 1.1968 | 1.1864 | 1.1736 | 1.1606
| 1 | 0.83154 | 1.0228 | 1.1169 | 1.1699 | 1.1959 | 1.2051 | 1.2043 | 1.1975 | 1.187 | 1.1743 | 1.1606 |  | 1 | 0.83154 | 1.0228 | 1.1169 | 1.1699 | 1.1959 | 1.2051 | 1.2043 | 1.1975 | 1.187 | 1.1743 | 1.1606
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 |  | 0 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
| 0.05 | 1.1236 | 1.099 | 1.0781 | 1.058 | 1.0384 | 1.0194 | 1.0016 | 0.98387 | 0.96664 | 0.95022 | 0.93436 |  | 0.05 | 1.1236 | 1.099 | 1.0781 | 1.058 | 1.0384 | 1.0194 | 1.0016 | 0.98387 | 0.96664 | 0.95022 | 0.93436
| 0.1 | 0.99612 | 0.96563 | 0.93789 | 0.91136 | 0.8861 | 0.86219 | 0.84013 | 0.81889 | 0.79883 | 0.7803 | 0.76259 |  | 0.1 | 0.99612 | 0.96563 | 0.93789 | 0.91136 | 0.8861 | 0.86219 | 0.84013 | 0.81889 | 0.79883 | 0.7803 | 0.76259
| 0.15 | 0.91918 | 0.88125 | 0.8484 | 0.8183 | 0.79079 | 0.76517 | 0.74188 | 0.71988 | 0.69954 | 0.68089 | 0.6634 |  | 0.15 | 0.91918 | 0.88125 | 0.8484 | 0.8183 | 0.79079 | 0.76517 | 0.74188 | 0.71988 | 0.69954 | 0.68089 | 0.6634
| 0.2 | 0.86961 | 0.82158 | 0.78474 | 0.75275 | 0.72401 | 0.69785 | 0.67419 | 0.65217 | 0.63201 | 0.6136 | 0.59668 |  | 0.2 | 0.86961 | 0.82158 | 0.78474 | 0.75275 | 0.72401 | 0.69785 | 0.67419 | 0.65217 | 0.63201 | 0.6136 | 0.59668
| 0.25 | 0.83529 | 0.77675 | 0.73629 | 0.70338 | 0.67407 | 0.64739 | 0.62361 | 0.60163 | 0.58167 | 0.56363 | 0.54709 |  | 0.25 | 0.83529 | 0.77675 | 0.73629 | 0.70338 | 0.67407 | 0.64739 | 0.62361 | 0.60163 | 0.58167 | 0.56363 | 0.54709
| 0.3 | 0.8099 | 0.74094 | 0.69815 | 0.66441 | 0.63427 | 0.60724 | 0.58309 | 0.56128 | 0.54178 | 0.52408 | 0.50797 |  | 0.3 | 0.8099 | 0.74094 | 0.69815 | 0.66441 | 0.63427 | 0.60724 | 0.58309 | 0.56128 | 0.54178 | 0.52408 | 0.50797
| 0.35 | 0.79098 | 0.71153 | 0.66688 | 0.63185 | 0.60102 | 0.57344 | 0.54941 | 0.52794 | 0.50893 | 0.49156 | 0.47611 |  | 0.35 | 0.79098 | 0.71153 | 0.66688 | 0.63185 | 0.60102 | 0.57344 | 0.54941 | 0.52794 | 0.50893 | 0.49156 | 0.47611
| 0.4 | 0.77627 | 0.68607 | 0.64033 | 0.60403 | 0.57267 | 0.545 | 0.52089 | 0.49968 | 0.48118 | 0.46451 | 0.44947 |  | 0.4 | 0.77627 | 0.68607 | 0.64033 | 0.60403 | 0.57267 | 0.545 | 0.52089 | 0.49968 | 0.48118 | 0.46451 | 0.44947
| 0.45 | 0.76397 | 0.66442 | 0.61733 | 0.57962 | 0.54752 | 0.52 | 0.49628 | 0.47558 | 0.45749 | 0.44135 | 0.42684 |  | 0.45 | 0.76397 | 0.66442 | 0.61733 | 0.57962 | 0.54752 | 0.52 | 0.49628 | 0.47558 | 0.45749 | 0.44135 | 0.42684
| 0.5 | 0.75429 | 0.64558 | 0.5968 | 0.558 | 0.52553 | 0.49798 | 0.47466 | 0.45454 | 0.43692 | 0.42136 | 0.40726 |  | 0.5 | 0.75429 | 0.64558 | 0.5968 | 0.558 | 0.52553 | 0.49798 | 0.47466 | 0.45454 | 0.43692 | 0.42136 | 0.40726
| 0.55 | 0.74632 | 0.62866 | 0.57841 | 0.5384 | 0.50559 | 0.47846 | 0.45569 | 0.43611 | 0.41882 | 0.40373 | 0.39022 |  | 0.55 | 0.74632 | 0.62866 | 0.57841 | 0.5384 | 0.50559 | 0.47846 | 0.45569 | 0.43611 | 0.41882 | 0.40373 | 0.39022
| 0.6 | 0.73912 | 0.61368 | 0.56168 | 0.52073 | 0.48792 | 0.46111 | 0.43892 | 0.41956 | 0.40279 | 0.38817 | 0.37502 |  | 0.6 | 0.73912 | 0.61368 | 0.56168 | 0.52073 | 0.48792 | 0.46111 | 0.43892 | 0.41956 | 0.40279 | 0.38817 | 0.37502
| 0.65 | 0.73334 | 0.60016 | 0.54623 | 0.50447 | 0.47164 | 0.44572 | 0.42358 | 0.40479 | 0.38855 | 0.37427 | 0.36154 |  | 0.65 | 0.73334 | 0.60016 | 0.54623 | 0.50447 | 0.47164 | 0.44572 | 0.42358 | 0.40479 | 0.38855 | 0.37427 | 0.36154
| 0.7 | 0.72832 | 0.58784 | 0.53168 | 0.48967 | 0.45724 | 0.43131 | 0.40965 | 0.39164 | 0.37581 | 0.36194 | 0.34945 |  | 0.7 | 0.72832 | 0.58784 | 0.53168 | 0.48967 | 0.45724 | 0.43131 | 0.40965 | 0.39164 | 0.37581 | 0.36194 | 0.34945
| 0.75 | 0.72358 | 0.57622 | 0.51856 | 0.47603 | 0.44386 | 0.41835 | 0.39733 | 0.37952 | 0.3641 | 0.35047 | 0.3385 |  | 0.75 | 0.72358 | 0.57622 | 0.51856 | 0.47603 | 0.44386 | 0.41835 | 0.39733 | 0.37952 | 0.3641 | 0.35047 | 0.3385
| 0.8 | 0.71985 | 0.56558 | 0.50608 | 0.46348 | 0.43164 | 0.40655 | 0.38598 | 0.36848 | 0.35343 | 0.34017 | 0.32846 |  | 0.8 | 0.71985 | 0.56558 | 0.50608 | 0.46348 | 0.43164 | 0.40655 | 0.38598 | 0.36848 | 0.35343 | 0.34017 | 0.32846
| 0.85 | 0.71644 | 0.55586 | 0.49463 | 0.45178 | 0.4204 | 0.39577 | 0.37544 | 0.35831 | 0.34365 | 0.33078 | 0.31935 |  | 0.85 | 0.71644 | 0.55586 | 0.49463 | 0.45178 | 0.4204 | 0.39577 | 0.37544 | 0.35831 | 0.34365 | 0.33078 | 0.31935
| 0.9 | 0.71303 | 0.54648 | 0.48374 | 0.44103 | 0.40994 | 0.38544 | 0.36565 | 0.34905 | 0.33464 | 0.32217 | 0.31097 |  | 0.9 | 0.71303 | 0.54648 | 0.48374 | 0.44103 | 0.40994 | 0.38544 | 0.36565 | 0.34905 | 0.33464 | 0.32217 | 0.31097
| 0.95 | 0.71033 | 0.5375 | 0.47353 | 0.43084 | 0.40012 | 0.37619 | 0.3569 | 0.34055 | 0.32642 | 0.31418 | 0.30333 |  | 0.95 | 0.71033 | 0.5375 | 0.47353 | 0.43084 | 0.40012 | 0.37619 | 0.3569 | 0.34055 | 0.32642 | 0.31418 | 0.30333
| 1 | 0.70796 | 0.52914 | 0.46394 | 0.42131 | 0.39109 | 0.3677 | 0.34841 | 0.33245 | 0.31883 | 0.30661 | 0.296 |  | 1 | 0.70796 | 0.52914 | 0.46394 | 0.42131 | 0.39109 | 0.3677 | 0.34841 | 0.33245 | 0.31883 | 0.30661 | 0.296
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0026704 | 0.0040617 | 0.0051823 | 0.0061689 | 0.0070455 | 0.0077837 | 0.0082753 | 0.0089295 | 0.009388 | 0.0098101 | 0.010136 |  | 0.05 | 0.0026704 | 0.0040617 | 0.0051823 | 0.0061689 | 0.0070455 | 0.0077837 | 0.0082753 | 0.0089295 | 0.009388 | 0.0098101 | 0.010136
| 0.1 | 0.0032786 | 0.0054378 | 0.0068831 | 0.0078993 | 0.00872 | 0.0093558 | 0.0098246 | 0.01029 | 0.010579 | 0.010834 | 0.01104 |  | 0.1 | 0.0032786 | 0.0054378 | 0.0068831 | 0.0078993 | 0.00872 | 0.0093558 | 0.0098246 | 0.01029 | 0.010579 | 0.010834 | 0.01104
| 0.15 | 0.0022707 | 0.0056608 | 0.0072713 | 0.0083899 | 0.0092731 | 0.0099011 | 0.010343 | 0.010666 | 0.010858 | 0.011042 | 0.011092 |  | 0.15 | 0.0022707 | 0.0056608 | 0.0072713 | 0.0083899 | 0.0092731 | 0.0099011 | 0.010343 | 0.010666 | 0.010858 | 0.011042 | 0.011092
| 0.2 | 0.0013504 | 0.0055589 | 0.0074519 | 0.0088679 | 0.0097513 | 0.010326 | 0.010743 | 0.010922 | 0.010966 | 0.011017 | 0.010976 |  | 0.2 | 0.0013504 | 0.0055589 | 0.0074519 | 0.0088679 | 0.0097513 | 0.010326 | 0.010743 | 0.010922 | 0.010966 | 0.011017 | 0.010976
| 0.25 | 0.00036437 | 0.0055964 | 0.0077494 | 0.0093175 | 0.010189 | 0.010637 | 0.010879 | 0.010894 | 0.010891 | 0.010802 | 0.010671 |  | 0.25 | 0.00036437 | 0.0055964 | 0.0077494 | 0.0093175 | 0.010189 | 0.010637 | 0.010879 | 0.010894 | 0.010891 | 0.010802 | 0.010671
| 0.3 | -0.00055001 | 0.005602 | 0.0081877 | 0.0096547 | 0.010405 | 0.010699 | 0.010767 | 0.01077 | 0.010662 | 0.010486 | 0.010313 |  | 0.3 | -0.00055001 | 0.005602 | 0.0081877 | 0.0096547 | 0.010405 | 0.010699 | 0.010767 | 0.01077 | 0.010662 | 0.010486 | 0.010313
| 0.35 | -0.0010687 | 0.0055984 | 0.0085631 | 0.0099003 | 0.010522 | 0.010666 | 0.010627 | 0.010489 | 0.01039 | 0.01015 | 0.0099868 |  | 0.35 | -0.0010687 | 0.0055984 | 0.0085631 | 0.0099003 | 0.010522 | 0.010666 | 0.010627 | 0.010489 | 0.01039 | 0.01015 | 0.0099868
| 0.4 | -0.0017181 | 0.0057447 | 0.0088309 | 0.010087 | 0.010473 | 0.010557 | 0.010419 | 0.010263 | 0.010017 | 0.0097936 | 0.0096019 |  | 0.4 | -0.0017181 | 0.0057447 | 0.0088309 | 0.010087 | 0.010473 | 0.010557 | 0.010419 | 0.010263 | 0.010017 | 0.0097936 | 0.0096019
| 0.45 | -0.0021633 | 0.0059931 | 0.0090563 | 0.010142 | 0.010377 | 0.010312 | 0.010198 | 0.0099216 | 0.0096656 | 0.0094682 | 0.0091779 |  | 0.45 | -0.0021633 | 0.0059931 | 0.0090563 | 0.010142 | 0.010377 | 0.010312 | 0.010198 | 0.0099216 | 0.0096656 | 0.0094682 | 0.0091779
| 0.5 | -0.0025096 | 0.0061587 | 0.0091617 | 0.010099 | 0.010237 | 0.010148 | 0.0098472 | 0.0096237 | 0.0093662 | 0.0091174 | 0.0089373 |  | 0.5 | -0.0025096 | 0.0061587 | 0.0091617 | 0.010099 | 0.010237 | 0.010148 | 0.0098472 | 0.0096237 | 0.0093662 | 0.0091174 | 0.0089373
| 0.55 | -0.0027901 | 0.0063277 | 0.0093589 | 0.010089 | 0.010066 | 0.0098757 | 0.009602 | 0.0093927 | 0.0090832 | 0.0088077 | 0.008598 |  | 0.55 | -0.0027901 | 0.0063277 | 0.0093589 | 0.010089 | 0.010066 | 0.0098757 | 0.009602 | 0.0093927 | 0.0090832 | 0.0088077 | 0.008598
| 0.6 | -0.0030495 | 0.0065684 | 0.0094517 | 0.0099669 | 0.0099246 | 0.009684 | 0.0093665 | 0.0091036 | 0.0087779 | 0.0085346 | 0.008297 |  | 0.6 | -0.0030495 | 0.0065684 | 0.0094517 | 0.0099669 | 0.0099246 | 0.009684 | 0.0093665 | 0.0091036 | 0.0087779 | 0.0085346 | 0.008297
| 0.65 | -0.003259 | 0.0067604 | 0.0094068 | 0.0098652 | 0.0097277 | 0.0094394 | 0.0090888 | 0.0087786 | 0.00853 | 0.0082994 | 0.0080181 |  | 0.65 | -0.003259 | 0.0067604 | 0.0094068 | 0.0098652 | 0.0097277 | 0.0094394 | 0.0090888 | 0.0087786 | 0.00853 | 0.0082994 | 0.0080181
| 0.7 | -0.0033779 | 0.0069269 | 0.009465 | 0.0097854 | 0.0095543 | 0.0092181 | 0.0089212 | 0.0085823 | 0.0083472 | 0.0080449 | 0.0077957 |  | 0.7 | -0.0033779 | 0.0069269 | 0.009465 | 0.0097854 | 0.0095543 | 0.0092181 | 0.0089212 | 0.0085823 | 0.0083472 | 0.0080449 | 0.0077957
| 0.75 | -0.0035677 | 0.0070705 | 0.0094027 | 0.0096359 | 0.0093653 | 0.0089992 | 0.0086537 | 0.0083639 | 0.008089 | 0.0078184 | 0.0076069 |  | 0.75 | -0.0035677 | 0.0070705 | 0.0094027 | 0.0096359 | 0.0093653 | 0.0089992 | 0.0086537 | 0.0083639 | 0.008089 | 0.0078184 | 0.0076069
| 0.8 | -0.0037929 | 0.0072466 | 0.0094213 | 0.0095027 | 0.0092005 | 0.0088137 | 0.0084267 | 0.0081222 | 0.0078718 | 0.0076051 | 0.0074074 |  | 0.8 | -0.0037929 | 0.0072466 | 0.0094213 | 0.0095027 | 0.0092005 | 0.0088137 | 0.0084267 | 0.0081222 | 0.0078718 | 0.0076051 | 0.0074074
| 0.85 | -0.0037831 | 0.0073899 | 0.0093922 | 0.0093707 | 0.0089625 | 0.0086139 | 0.0082769 | 0.0079677 | 0.0076475 | 0.0074194 | 0.0071943 |  | 0.85 | -0.0037831 | 0.0073899 | 0.0093922 | 0.0093707 | 0.0089625 | 0.0086139 | 0.0082769 | 0.0079677 | 0.0076475 | 0.0074194 | 0.0071943
| 0.9 | -0.0038815 | 0.0075154 | 0.0092978 | 0.0092427 | 0.008788 | 0.00846 | 0.008095 | 0.0077802 | 0.0075087 | 0.0073202 | 0.0070762 |  | 0.9 | -0.0038815 | 0.0075154 | 0.0092978 | 0.0092427 | 0.008788 | 0.00846 | 0.008095 | 0.0077802 | 0.0075087 | 0.0073202 | 0.0070762
| 0.95 | -0.0040634 | 0.0076067 | 0.0091805 | 0.0090339 | 0.0086209 | 0.0082511 | 0.0079206 | 0.0075786 | 0.0073196 | 0.0070984 | 0.0069472 |  | 0.95 | -0.0040634 | 0.0076067 | 0.0091805 | 0.0090339 | 0.0086209 | 0.0082511 | 0.0079206 | 0.0075786 | 0.0073196 | 0.0070984 | 0.0069472
| 1 | -0.0041507 | 0.0076767 | 0.009225 | 0.0089161 | 0.0084567 | 0.008112 | 0.007767 | 0.0074501 | 0.0072191 | 0.007014 | 0.0067837 |  | 1 | -0.0041507 | 0.0076767 | 0.009225 | 0.0089161 | 0.0084567 | 0.008112 | 0.007767 | 0.0074501 | 0.0072191 | 0.007014 | 0.0067837
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0016027 | 0.001767 | 0.0019169 | 0.0020561 | 0.0021748 | 0.0022801 | 0.0023755 | 0.0024579 | 0.0025196 | 0.0025778 | 0.0026242 |  | 0.05 | 0.0016027 | 0.001767 | 0.0019169 | 0.0020561 | 0.0021748 | 0.0022801 | 0.0023755 | 0.0024579 | 0.0025196 | 0.0025778 | 0.0026242
| 0.1 | 0.0019202 | 0.0021925 | 0.0023554 | 0.0024638 | 0.002539 | 0.0025931 | 0.0026383 | 0.0026697 | 0.0026901 | 0.0027066 | 0.0027105 |  | 0.1 | 0.0019202 | 0.0021925 | 0.0023554 | 0.0024638 | 0.002539 | 0.0025931 | 0.0026383 | 0.0026697 | 0.0026901 | 0.0027066 | 0.0027105
| 0.15 | 0.001831 | 0.0022425 | 0.0023914 | 0.0024728 | 0.0025281 | 0.0025643 | 0.0025844 | 0.0025982 | 0.0026036 | 0.0025965 | 0.0025832 |  | 0.15 | 0.001831 | 0.0022425 | 0.0023914 | 0.0024728 | 0.0025281 | 0.0025643 | 0.0025844 | 0.0025982 | 0.0026036 | 0.0025965 | 0.0025832
| 0.2 | 0.0016199 | 0.0021959 | 0.0023439 | 0.0024087 | 0.0024617 | 0.0024955 | 0.0025177 | 0.0025238 | 0.0025198 | 0.0024994 | 0.0024802 |  | 0.2 | 0.0016199 | 0.0021959 | 0.0023439 | 0.0024087 | 0.0024617 | 0.0024955 | 0.0025177 | 0.0025238 | 0.0025198 | 0.0024994 | 0.0024802
| 0.25 | 0.0014332 | 0.0021257 | 0.0022745 | 0.0023553 | 0.0024209 | 0.0024614 | 0.0024762 | 0.0024666 | 0.0024452 | 0.0024249 | 0.0023902 |  | 0.25 | 0.0014332 | 0.0021257 | 0.0022745 | 0.0023553 | 0.0024209 | 0.0024614 | 0.0024762 | 0.0024666 | 0.0024452 | 0.0024249 | 0.0023902
| 0.3 | 0.0012662 | 0.0020776 | 0.0022131 | 0.0023369 | 0.0024041 | 0.0024323 | 0.0024338 | 0.0024144 | 0.0023775 | 0.0023444 | 0.0023015 |  | 0.3 | 0.0012662 | 0.0020776 | 0.0022131 | 0.0023369 | 0.0024041 | 0.0024323 | 0.0024338 | 0.0024144 | 0.0023775 | 0.0023444 | 0.0023015
| 0.35 | 0.0011313 | 0.0020186 | 0.0021788 | 0.002324 | 0.0023904 | 0.0024028 | 0.0023861 | 0.0023499 | 0.0023079 | 0.002262 | 0.002216 |  | 0.35 | 0.0011313 | 0.0020186 | 0.0021788 | 0.002324 | 0.0023904 | 0.0024028 | 0.0023861 | 0.0023499 | 0.0023079 | 0.002262 | 0.002216
| 0.4 | 0.00099513 | 0.0019663 | 0.0021737 | 0.0023237 | 0.0023701 | 0.0023615 | 0.002326 | 0.0022831 | 0.0022351 | 0.0021849 | 0.0021297 |  | 0.4 | 0.00099513 | 0.0019663 | 0.0021737 | 0.0023237 | 0.0023701 | 0.0023615 | 0.002326 | 0.0022831 | 0.0022351 | 0.0021849 | 0.0021297
| 0.45 | 0.00089003 | 0.0019253 | 0.0021673 | 0.0023119 | 0.0023392 | 0.0023107 | 0.0022697 | 0.0022088 | 0.002163 | 0.0021061 | 0.0020551 |  | 0.45 | 0.00089003 | 0.0019253 | 0.0021673 | 0.0023119 | 0.0023392 | 0.0023107 | 0.0022697 | 0.0022088 | 0.002163 | 0.0021061 | 0.0020551
| 0.5 | 0.00080944 | 0.0018867 | 0.0021742 | 0.002293 | 0.0023036 | 0.0022605 | 0.0022108 | 0.0021467 | 0.0020917 | 0.002036 | 0.0019858 |  | 0.5 | 0.00080944 | 0.0018867 | 0.0021742 | 0.002293 | 0.0023036 | 0.0022605 | 0.0022108 | 0.0021467 | 0.0020917 | 0.002036 | 0.0019858
| 0.55 | 0.00072262 | 0.0018608 | 0.0021797 | 0.0022792 | 0.0022688 | 0.0022152 | 0.0021503 | 0.0020895 | 0.0020277 | 0.0019664 | 0.0019211 |  | 0.55 | 0.00072262 | 0.0018608 | 0.0021797 | 0.0022792 | 0.0022688 | 0.0022152 | 0.0021503 | 0.0020895 | 0.0020277 | 0.0019664 | 0.0019211
| 0.6 | 0.00066493 | 0.0018462 | 0.0021708 | 0.0022484 | 0.0022266 | 0.0021631 | 0.0020975 | 0.0020309 | 0.0019678 | 0.0019103 | 0.0018537 |  | 0.6 | 0.00066493 | 0.0018462 | 0.0021708 | 0.0022484 | 0.0022266 | 0.0021631 | 0.0020975 | 0.0020309 | 0.0019678 | 0.0019103 | 0.0018537
| 0.65 | 0.00060767 | 0.0018346 | 0.0021684 | 0.0022245 | 0.0021796 | 0.002116 | 0.0020485 | 0.0019761 | 0.0019118 | 0.0018562 | 0.0017987 |  | 0.65 | 0.00060767 | 0.0018346 | 0.0021684 | 0.0022245 | 0.0021796 | 0.002116 | 0.0020485 | 0.0019761 | 0.0019118 | 0.0018562 | 0.0017987
| 0.7 | 0.00056913 | 0.001825 | 0.0021599 | 0.0021915 | 0.0021397 | 0.0020698 | 0.0019966 | 0.0019254 | 0.0018602 | 0.0018047 | 0.0017506 |  | 0.7 | 0.00056913 | 0.001825 | 0.0021599 | 0.0021915 | 0.0021397 | 0.0020698 | 0.0019966 | 0.0019254 | 0.0018602 | 0.0018047 | 0.0017506
| 0.75 | 0.00050797 | 0.0018305 | 0.0021501 | 0.0021615 | 0.0021001 | 0.0020192 | 0.0019457 | 0.001876 | 0.0018103 | 0.0017528 | 0.0016996 |  | 0.75 | 0.00050797 | 0.0018305 | 0.0021501 | 0.0021615 | 0.0021001 | 0.0020192 | 0.0019457 | 0.001876 | 0.0018103 | 0.0017528 | 0.0016996
| 0.8 | 0.00046728 | 0.0018291 | 0.002134 | 0.0021274 | 0.0020618 | 0.001981 | 0.0019011 | 0.0018276 | 0.0017665 | 0.0017054 | 0.0016569 |  | 0.8 | 0.00046728 | 0.0018291 | 0.002134 | 0.0021274 | 0.0020618 | 0.001981 | 0.0019011 | 0.0018276 | 0.0017665 | 0.0017054 | 0.0016569
| 0.85 | 0.00043986 | 0.001843 | 0.0021181 | 0.0020961 | 0.0020211 | 0.0019393 | 0.0018601 | 0.0017865 | 0.0017234 | 0.0016629 | 0.0016115 |  | 0.85 | 0.00043986 | 0.001843 | 0.0021181 | 0.0020961 | 0.0020211 | 0.0019393 | 0.0018601 | 0.0017865 | 0.0017234 | 0.0016629 | 0.0016115
| 0.9 | 0.00040637 | 0.0018435 | 0.002097 | 0.0020685 | 0.0019826 | 0.0019009 | 0.0018178 | 0.0017452 | 0.0016857 | 0.0016316 | 0.001574 |  | 0.9 | 0.00040637 | 0.0018435 | 0.002097 | 0.0020685 | 0.0019826 | 0.0019009 | 0.0018178 | 0.0017452 | 0.0016857 | 0.0016316 | 0.001574
| 0.95 | 0.00037368 | 0.0018461 | 0.0020819 | 0.0020354 | 0.0019482 | 0.0018626 | 0.0017747 | 0.0017077 | 0.0016509 | 0.0015905 | 0.0015426 |  | 0.95 | 0.00037368 | 0.0018461 | 0.0020819 | 0.0020354 | 0.0019482 | 0.0018626 | 0.0017747 | 0.0017077 | 0.0016509 | 0.0015905 | 0.0015426
| 1 | 0.0003436 | 0.0018587 | 0.0020622 | 0.0020087 | 0.0019136 | 0.0018188 | 0.0017431 | 0.0016708 | 0.0016083 | 0.0015581 | 0.001507 |  | 1 | 0.0003436 | 0.0018587 | 0.0020622 | 0.0020087 | 0.0019136 | 0.0018188 | 0.0017431 | 0.0016708 | 0.0016083 | 0.0015581 | 0.001507
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | [12 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 0 to 1
| 0.05 | 1.3303 | 1.595 | 1.8077 | 1.9804 | 2.1238 | 2.2412 | 2.333 | 2.4162 | 2.4846 | 2.5465 | 2.5945 |  | 0.05 | 1.3303 | 1.595 | 1.8077 | 1.9804 | 2.1238 | 2.2412 | 2.333 | 2.4162 | 2.4846 | 2.5465 | 2.5945
| 0.1 | 1.3099 | 1.8945 | 2.3271 | 2.6754 | 2.8983 | 3.1154 | 3.2468 | 3.3916 | 3.4725 | 3.5554 | 3.6386 |  | 0.1 | 1.3099 | 1.8945 | 2.3271 | 2.6754 | 2.8983 | 3.1154 | 3.2468 | 3.3916 | 3.4725 | 3.5554 | 3.6386
| 0.15 | 1.2265 | 2.1201 | 2.6755 | 3.1432 | 3.4309 | 3.8207 | 4.0589 | 4.1374 | 4.2604 | 4.3601 | 4.4386 |  | 0.15 | 1.2265 | 2.1201 | 2.6755 | 3.1432 | 3.4309 | 3.8207 | 4.0589 | 4.1374 | 4.2604 | 4.3601 | 4.4386
| 0.2 | 1.1409 | 2.3179 | 3.0895 | 3.6323 | 4.0686 | 4.3795 | 4.6111 | 4.7952 | 4.7198 | 5.0505 | 5.1272 |  | 0.2 | 1.1409 | 2.3179 | 3.0895 | 3.6323 | 4.0686 | 4.3795 | 4.6111 | 4.7952 | 4.7198 | 5.0505 | 5.1272
| 0.25 | 1.0779 | 2.5194 | 3.42 | 4.0632 | 4.5321 | 4.8999 | 5.1627 | 5.3784 | 5.535 | 5.6494 | 5.7433 |  | 0.25 | 1.0779 | 2.5194 | 3.42 | 4.0632 | 4.5321 | 4.8999 | 5.1627 | 5.3784 | 5.535 | 5.6494 | 5.7433
| 0.3 | 1.0416 | 2.6924 | 3.7343 | 4.4801 | 5.0078 | 5.3814 | 5.6802 | 5.9014 | 6.0728 | 6.1927 | 6.2923 |  | 0.3 | 1.0416 | 2.6924 | 3.7343 | 4.4801 | 5.0078 | 5.3814 | 5.6802 | 5.9014 | 6.0728 | 6.1927 | 6.2923
| 0.35 | 1.0094 | 2.869 | 4.0312 | 4.8395 | 5.376 | 5.8131 | 6.1301 | 6.3747 | 6.5503 | 6.6801 | 6.7954 |  | 0.35 | 1.0094 | 2.869 | 4.0312 | 4.8395 | 5.376 | 5.8131 | 6.1301 | 6.3747 | 6.5503 | 6.6801 | 6.7954
| 0.4 | 0.9811 | 3.0504 | 4.3237 | 5.1776 | 5.7874 | 6.2297 | 6.5539 | 6.8097 | 6.9928 | 7.1398 | 7.2427 |  | 0.4 | 0.9811 | 3.0504 | 4.3237 | 5.1776 | 5.7874 | 6.2297 | 6.5539 | 6.8097 | 6.9928 | 7.1398 | 7.2427
| 0.45 | 0.96786 | 3.2045 | 4.5722 | 5.486 | 6.1407 | 6.606 | 6.9457 | 7.2117 | 7.4135 | 7.5706 | 7.6765 |  | 0.45 | 0.96786 | 3.2045 | 4.5722 | 5.486 | 6.1407 | 6.606 | 6.9457 | 7.2117 | 7.4135 | 7.5706 | 7.6765
| 0.5 | 0.95197 | 3.3618 | 4.8348 | 5.7945 | 6.4615 | 6.9575 | 7.3181 | 7.6 | 7.8066 | 7.9597 | 8.0831 |  | 0.5 | 0.95197 | 3.3618 | 4.8348 | 5.7945 | 6.4615 | 6.9575 | 7.3181 | 7.6 | 7.8066 | 7.9597 | 8.0831
| 0.55 | 0.93558 | 3.5334 | 5.0713 | 6.0649 | 6.7802 | 7.2816 | 7.6663 | 7.9528 | 8.1769 | 8.339 | 8.4632 |  | 0.55 | 0.93558 | 3.5334 | 5.0713 | 6.0649 | 6.7802 | 7.2816 | 7.6663 | 7.9528 | 8.1769 | 8.339 | 8.4632
| 0.6 | 0.93149 | 3.6679 | 5.3027 | 6.3355 | 7.0705 | 7.5975 | 7.9976 | 8.2894 | 8.5267 | 8.7017 | 8.8312 |  | 0.6 | 0.93149 | 3.6679 | 5.3027 | 6.3355 | 7.0705 | 7.5975 | 7.9976 | 8.2894 | 8.5267 | 8.7017 | 8.8312
| 0.65 | 0.91954 | 3.83 | 5.5088 | 6.5915 | 7.3386 | 7.8981 | 8.3097 | 8.6241 | 8.8674 | 9.0486 | 9.1873 |  | 0.65 | 0.91954 | 3.83 | 5.5088 | 6.5915 | 7.3386 | 7.8981 | 8.3097 | 8.6241 | 8.8674 | 9.0486 | 9.1873
| 0.7 | 0.90895 | 3.9732 | 5.7226 | 6.8252 | 7.6042 | 8.173 | 8.6076 | 8.9402 | 9.1879 | 9.3762 | 9.5287 |  | 0.7 | 0.90895 | 3.9732 | 5.7226 | 6.8252 | 7.6042 | 8.173 | 8.6076 | 8.9402 | 9.1879 | 9.3762 | 9.5287
| 0.75 | 0.90932 | 4.1067 | 5.9182 | 7.0583 | 7.8612 | 8.4517 | 8.9039 | 9.2433 | 9.5012 | 9.6958 | 9.8481 |  | 0.75 | 0.90932 | 4.1067 | 5.9182 | 7.0583 | 7.8612 | 8.4517 | 8.9039 | 9.2433 | 9.5012 | 9.6958 | 9.8481
| 0.8 | 0.89962 | 4.2544 | 6.1002 | 7.2702 | 8.1029 | 8.705 | 9.1861 | 9.5373 | 9.8059 | 10.0074 | 10.1624 |  | 0.8 | 0.89962 | 4.2544 | 6.1002 | 7.2702 | 8.1029 | 8.705 | 9.1861 | 9.5373 | 9.8059 | 10.0074 | 10.1624
| 0.85 | 0.89052 | 4.3877 | 6.2803 | 7.4634 | 8.3412 | 8.977 | 9.4559 | 9.8205 | 10.0982 | 10.3117 | 10.4741 |  | 0.85 | 0.89052 | 4.3877 | 6.2803 | 7.4634 | 8.3412 | 8.977 | 9.4559 | 9.8205 | 10.0982 | 10.3117 | 10.4741
| 0.9 | 0.89299 | 4.5156 | 6.4435 | 7.6846 | 8.5698 | 9.2192 | 9.717 | 10.0979 | 10.3832 | 10.6083 | 10.7738 |  | 0.9 | 0.89299 | 4.5156 | 6.4435 | 7.6846 | 8.5698 | 9.2192 | 9.717 | 10.0979 | 10.3832 | 10.6083 | 10.7738
| 0.95 | 0.88494 | 4.6383 | 6.6193 | 7.8825 | 8.7883 | 9.458 | 9.9778 | 10.368 | 10.6655 | 10.8862 | 11.0609 |  | 0.95 | 0.88494 | 4.6383 | 6.6193 | 7.8825 | 8.7883 | 9.458 | 9.9778 | 10.368 | 10.6655 | 10.8862 | 11.0609
| 1 | 0.87925 | 4.7584 | 6.7847 | 8.0812 | 9.006 | 9.7025 | 10.2246 | 10.6272 | 10.93 | 11.1614 | 11.3426 |  | 1 | 0.87925 | 4.7584 | 6.7847 | 8.0812 | 9.006 | 9.7025 | 10.2246 | 10.6272 | 10.93 | 11.1614 | 11.3426
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0031316 | -0.0011301 | 0.00043156 | 0.0026968 | 0.0052471 | 0.00707 | 0.010407 | 0.01101 | 0.013108 | 0.015041 | 0.016065 |  | 0.05 | -0.0031316 | -0.0011301 | 0.00043156 | 0.0026968 | 0.0052471 | 0.00707 | 0.010407 | 0.01101 | 0.013108 | 0.015041 | 0.016065
| 0.1 | 0.00091112 | 0.0051015 | 0.010143 | 0.014242 | 0.018472 | 0.026652 | 0.024401 | 0.027987 | 0.03353 | 0.036052 | 0.036331 |  | 0.1 | 0.00091112 | 0.0051015 | 0.010143 | 0.014242 | 0.018472 | 0.026652 | 0.024401 | 0.027987 | 0.03353 | 0.036052 | 0.036331
| 0.15 | 0.00036667 | 0.0085789 | 0.01799 | 0.022431 | 0.030361 | 0.038817 | 0.042472 | 0.045341 | 0.053218 | 0.053544 | 0.057008 |  | 0.15 | 0.00036667 | 0.0085789 | 0.01799 | 0.022431 | 0.030361 | 0.038817 | 0.042472 | 0.045341 | 0.053218 | 0.053544 | 0.057008
| 0.2 | -0.0043506 | 0.012341 | 0.025837 | 0.033967 | 0.044719 | 0.054949 | 0.060544 | 0.061712 | 0.072543 | 0.076639 | 0.084946 |  | 0.2 | -0.0043506 | 0.012341 | 0.025837 | 0.033967 | 0.044719 | 0.054949 | 0.060544 | 0.061712 | 0.072543 | 0.076639 | 0.084946
| 0.25 | -0.0071191 | 0.015663 | 0.033684 | 0.041088 | 0.059078 | 0.070148 | 0.078616 | 0.085807 | 0.090672 | 0.096033 | 0.096247 |  | 0.25 | -0.0071191 | 0.015663 | 0.033684 | 0.041088 | 0.059078 | 0.070148 | 0.078616 | 0.085807 | 0.090672 | 0.096033 | 0.096247
| 0.3 | -0.0082421 | 0.018986 | 0.041531 | 0.057399 | 0.073436 | 0.085346 | 0.096688 | 0.10535 | 0.10367 | 0.10906 | 0.1162 |  | 0.3 | -0.0082421 | 0.018986 | 0.041531 | 0.057399 | 0.073436 | 0.085346 | 0.096688 | 0.10535 | 0.10367 | 0.10906 | 0.1162
| 0.35 | -0.011983 | 0.022308 | 0.049378 | 0.073404 | 0.087795 | 0.10055 | 0.11383 | 0.11789 | 0.12008 | 0.12333 | 0.12317 |  | 0.35 | -0.011983 | 0.022308 | 0.049378 | 0.073404 | 0.087795 | 0.10055 | 0.11383 | 0.11789 | 0.12008 | 0.12333 | 0.12317
| 0.4 | -0.011744 | 0.02563 | 0.057225 | 0.087784 | 0.10215 | 0.11549 | 0.12132 | 0.12821 | 0.13139 | 0.13545 | 0.13701 |  | 0.4 | -0.011744 | 0.02563 | 0.057225 | 0.087784 | 0.10215 | 0.11549 | 0.12132 | 0.12821 | 0.13139 | 0.13545 | 0.13701
| 0.45 | -0.013185 | 0.028953 | 0.065072 | 0.091954 | 0.11356 | 0.12515 | 0.13403 | 0.13995 | 0.14403 | 0.14727 | 0.14895 |  | 0.45 | -0.013185 | 0.028953 | 0.065072 | 0.091954 | 0.11356 | 0.12515 | 0.13403 | 0.13995 | 0.14403 | 0.14727 | 0.14895
| 0.5 | -0.014475 | 0.032275 | 0.072919 | 0.1028 | 0.12334 | 0.13398 | 0.14171 | 0.14691 | 0.15317 | 0.15565 | 0.15884 |  | 0.5 | -0.014475 | 0.032275 | 0.072919 | 0.1028 | 0.12334 | 0.13398 | 0.14171 | 0.14691 | 0.15317 | 0.15565 | 0.15884
| 0.55 | -0.015788 | 0.035598 | 0.080877 | 0.11309 | 0.13295 | 0.14302 | 0.15116 | 0.1574 | 0.16326 | 0.16647 | 0.16836 |  | 0.55 | -0.015788 | 0.035598 | 0.080877 | 0.11309 | 0.13295 | 0.14302 | 0.15116 | 0.1574 | 0.16326 | 0.16647 | 0.16836
| 0.6 | -0.016881 | 0.03892 | 0.092317 | 0.12134 | 0.14108 | 0.15209 | 0.16062 | 0.16503 | 0.16945 | 0.17579 | 0.17653 |  | 0.6 | -0.016881 | 0.03892 | 0.092317 | 0.12134 | 0.14108 | 0.15209 | 0.16062 | 0.16503 | 0.16945 | 0.17579 | 0.17653
| 0.65 | -0.016695 | 0.042242 | 0.096022 | 0.12763 | 0.14651 | 0.15943 | 0.16717 | 0.17291 | 0.17754 | 0.1835 | 0.18536 |  | 0.65 | -0.016695 | 0.042242 | 0.096022 | 0.12763 | 0.14651 | 0.15943 | 0.16717 | 0.17291 | 0.17754 | 0.1835 | 0.18536
| 0.7 | -0.017475 | 0.045565 | 0.10334 | 0.1351 | 0.15341 | 0.16689 | 0.17733 | 0.18216 | 0.18818 | 0.1905 | 0.19395 |  | 0.7 | -0.017475 | 0.045565 | 0.10334 | 0.1351 | 0.15341 | 0.16689 | 0.17733 | 0.18216 | 0.18818 | 0.1905 | 0.19395
| 0.75 | -0.018148 | 0.049467 | 0.10655 | 0.13981 | 0.16034 | 0.17365 | 0.18285 | 0.18973 | 0.19592 | 0.19815 | 0.20277 |  | 0.75 | -0.018148 | 0.049467 | 0.10655 | 0.13981 | 0.16034 | 0.17365 | 0.18285 | 0.18973 | 0.19592 | 0.19815 | 0.20277
| 0.8 | -0.01688 | 0.054094 | 0.11294 | 0.14529 | 0.16627 | 0.18039 | 0.18926 | 0.19592 | 0.20291 | 0.20757 | 0.21005 |  | 0.8 | -0.01688 | 0.054094 | 0.11294 | 0.14529 | 0.16627 | 0.18039 | 0.18926 | 0.19592 | 0.20291 | 0.20757 | 0.21005
| 0.85 | -0.018734 | 0.05201 | 0.12141 | 0.1518 | 0.17171 | 0.18641 | 0.19691 | 0.20435 | 0.20883 | 0.21341 | 0.21664 |  | 0.85 | -0.018734 | 0.05201 | 0.12141 | 0.1518 | 0.17171 | 0.18641 | 0.19691 | 0.20435 | 0.20883 | 0.21341 | 0.21664
| 0.9 | -0.019411 | 0.057161 | 0.12602 | 0.15922 | 0.17741 | 0.19333 | 0.2038 | 0.21083 | 0.21508 | 0.22319 | 0.22568 |  | 0.9 | -0.019411 | 0.057161 | 0.12602 | 0.15922 | 0.17741 | 0.19333 | 0.2038 | 0.21083 | 0.21508 | 0.22319 | 0.22568
| 0.95 | -0.018059 | 0.065486 | 0.12968 | 0.16327 | 0.18233 | 0.19803 | 0.2098 | 0.21693 | 0.22105 | 0.22751 | 0.23416 |  | 0.95 | -0.018059 | 0.065486 | 0.12968 | 0.16327 | 0.18233 | 0.19803 | 0.2098 | 0.21693 | 0.22105 | 0.22751 | 0.23416
| 1 | -0.018236 | 0.073812 | 0.13847 | 0.16858 | 0.18937 | 0.2046 | 0.21562 | 0.22191 | 0.22963 | 0.23704 | 0.2389 |  | 1 | -0.018236 | 0.073812 | 0.13847 | 0.16858 | 0.18937 | 0.2046 | 0.21562 | 0.22191 | 0.22963 | 0.23704 | 0.2389
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0016675 | -0.0047474 | -0.0069572 | -0.0085816 | -0.0098708 | -0.010733 | -0.01148 | -0.012005 | -0.012328 | -0.012582 | -0.012842 |  | 0.05 | -0.0016675 | -0.0047474 | -0.0069572 | -0.0085816 | -0.0098708 | -0.010733 | -0.01148 | -0.012005 | -0.012328 | -0.012582 | -0.012842
| 0.1 | 0.00084407 | -0.0054089 | -0.0098573 | -0.012762 | -0.014495 | -0.016603 | -0.016892 | -0.017956 | -0.018515 | -0.018636 | -0.019036 |  | 0.1 | 0.00084407 | -0.0054089 | -0.0098573 | -0.012762 | -0.014495 | -0.016603 | -0.016892 | -0.017956 | -0.018515 | -0.018636 | -0.019036
| 0.15 | 0.0017766 | -0.0068689 | -0.01216 | -0.016544 | -0.019473 | -0.020068 | -0.021296 | -0.021571 | -0.022524 | -0.02329 | -0.023089 |  | 0.15 | 0.0017766 | -0.0068689 | -0.01216 | -0.016544 | -0.019473 | -0.020068 | -0.021296 | -0.021571 | -0.022524 | -0.02329 | -0.023089
| 0.2 | 0.0022557 | -0.0099008 | -0.013714 | -0.019184 | -0.02156 | -0.023534 | -0.025381 | -0.025776 | -0.026172 | -0.028324 | -0.027038 |  | 0.2 | 0.0022557 | -0.0099008 | -0.013714 | -0.019184 | -0.02156 | -0.023534 | -0.025381 | -0.025776 | -0.026172 | -0.028324 | -0.027038
| 0.25 | 0.001929 | -0.010488 | -0.015268 | -0.021824 | -0.023647 | -0.026404 | -0.028654 | -0.029237 | -0.029821 | -0.031249 | -0.030986 |  | 0.25 | 0.001929 | -0.010488 | -0.015268 | -0.021824 | -0.023647 | -0.026404 | -0.028654 | -0.029237 | -0.029821 | -0.031249 | -0.030986
| 0.3 | 0.0017152 | -0.012978 | -0.017471 | -0.024464 | -0.025735 | -0.029274 | -0.031143 | -0.032018 | -0.032542 | -0.033364 | -0.033328 |  | 0.3 | 0.0017152 | -0.012978 | -0.017471 | -0.024464 | -0.025735 | -0.029274 | -0.031143 | -0.032018 | -0.032542 | -0.033364 | -0.033328
| 0.35 | 0.0013198 | -0.013399 | -0.021087 | -0.026139 | -0.027822 | -0.030742 | -0.032565 | -0.034141 | -0.034551 | -0.035388 | -0.035857 |  | 0.35 | 0.0013198 | -0.013399 | -0.021087 | -0.026139 | -0.027822 | -0.030742 | -0.032565 | -0.034141 | -0.034551 | -0.035388 | -0.035857
| 0.4 | 0.0013603 | -0.014459 | -0.022596 | -0.027002 | -0.030336 | -0.03282 | -0.034739 | -0.036112 | -0.037224 | -0.037547 | -0.038564 |  | 0.4 | 0.0013603 | -0.014459 | -0.022596 | -0.027002 | -0.030336 | -0.03282 | -0.034739 | -0.036112 | -0.037224 | -0.037547 | -0.038564
| 0.45 | 0.0012511 | -0.01552 | -0.024876 | -0.028819 | -0.032271 | -0.034536 | -0.036347 | -0.037971 | -0.039065 | -0.039779 | -0.040626 |  | 0.45 | 0.0012511 | -0.01552 | -0.024876 | -0.028819 | -0.032271 | -0.034536 | -0.036347 | -0.037971 | -0.039065 | -0.039779 | -0.040626
| 0.5 | 0.00080866 | -0.016722 | -0.025733 | -0.02947 | -0.033577 | -0.036102 | -0.038218 | -0.039708 | -0.041163 | -0.041849 | -0.042762 |  | 0.5 | 0.00080866 | -0.016722 | -0.025733 | -0.02947 | -0.033577 | -0.036102 | -0.038218 | -0.039708 | -0.041163 | -0.041849 | -0.042762
| 0.55 | 0.00091992 | -0.017875 | -0.026389 | -0.031222 | -0.034861 | -0.037942 | -0.040088 | -0.041536 | -0.042852 | -0.043924 | -0.044657 |  | 0.55 | 0.00091992 | -0.017875 | -0.026389 | -0.031222 | -0.034861 | -0.037942 | -0.040088 | -0.041536 | -0.042852 | -0.043924 | -0.044657
| 0.6 | 0.00067612 | -0.019824 | -0.027148 | -0.032342 | -0.036196 | -0.03892 | -0.041559 | -0.043297 | -0.044725 | -0.045882 | -0.046674 |  | 0.6 | 0.00067612 | -0.019824 | -0.027148 | -0.032342 | -0.036196 | -0.03892 | -0.041559 | -0.043297 | -0.044725 | -0.045882 | -0.046674
| 0.65 | 0.00054623 | -0.020158 | -0.027919 | -0.033319 | -0.03771 | -0.040524 | -0.043403 | -0.045224 | -0.046646 | -0.047726 | -0.048551 |  | 0.65 | 0.00054623 | -0.020158 | -0.027919 | -0.033319 | -0.03771 | -0.040524 | -0.043403 | -0.045224 | -0.046646 | -0.047726 | -0.048551
| 0.7 | 0.0002636 | -0.020774 | -0.028741 | -0.034555 | -0.038658 | -0.042008 | -0.044813 | -0.047115 | -0.048469 | -0.049647 | -0.0507 |  | 0.7 | 0.0002636 | -0.020774 | -0.028741 | -0.034555 | -0.038658 | -0.042008 | -0.044813 | -0.047115 | -0.048469 | -0.049647 | -0.0507
| 0.75 | 0.00041474 | -0.021479 | -0.029702 | -0.035541 | -0.039828 | -0.043595 | -0.046418 | -0.048703 | -0.050293 | -0.051258 | -0.052363 |  | 0.75 | 0.00041474 | -0.021479 | -0.029702 | -0.035541 | -0.039828 | -0.043595 | -0.046418 | -0.048703 | -0.050293 | -0.051258 | -0.052363
| 0.8 | 0.00037067 | -0.022301 | -0.03077 | -0.036489 | -0.041001 | -0.045019 | -0.048067 | -0.050342 | -0.051755 | -0.053229 | -0.054097 |  | 0.8 | 0.00037067 | -0.022301 | -0.03077 | -0.036489 | -0.041001 | -0.045019 | -0.048067 | -0.050342 | -0.051755 | -0.053229 | -0.054097
| 0.85 | 0.00017807 | -0.023595 | -0.031304 | -0.03748 | -0.043274 | -0.046268 | -0.049522 | -0.051701 | -0.053577 | -0.055197 | -0.055832 |  | 0.85 | 0.00017807 | -0.023595 | -0.031304 | -0.03748 | -0.043274 | -0.046268 | -0.049522 | -0.051701 | -0.053577 | -0.055197 | -0.055832
| 0.9 | 7.7039e-05 | -0.023425 | -0.031828 | -0.038364 | -0.043834 | -0.047662 | -0.051084 | -0.053271 | -0.054987 | -0.05654 | -0.05772 |  | 0.9 | 7.7039e-05 | -0.023425 | -0.031828 | -0.038364 | -0.043834 | -0.047662 | -0.051084 | -0.053271 | -0.054987 | -0.05654 | -0.05772
| 0.95 | 6.642e-05 | -0.024236 | -0.032659 | -0.039466 | -0.045016 | -0.049315 | -0.052643 | -0.054822 | -0.056631 | -0.058187 | -0.059227 |  | 0.95 | 6.642e-05 | -0.024236 | -0.032659 | -0.039466 | -0.045016 | -0.049315 | -0.052643 | -0.054822 | -0.056631 | -0.058187 | -0.059227
| 1 | -9.495e-06 | -0.025742 | -0.033421 | -0.040356 | -0.04619 | -0.050544 | -0.054003 | -0.056286 | -0.058455 | -0.059616 | -0.060631 |  | 1 | -9.495e-06 | -0.025742 | -0.033421 | -0.040356 | -0.04619 | -0.050544 | -0.054003 | -0.056286 | -0.058455 | -0.059616 | -0.060631
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS4_LS< (hidden)
If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0226 | 1.0387 | 1.0502 | 1.06 | 1.0649 | 1.0669 | 1.0666 | 1.0644 | 1.0608 | 1.0559 | 1.0509
| 0.1 | 1.0438 | 1.0719 | 1.0989 | 1.1165 | 1.1251 | 1.1275 | 1.1254 | 1.1201 | 1.1127 | 1.1038 | 1.0934
| 0.15 | 1.0438 | 1.0826 | 1.1156 | 1.1384 | 1.1489 | 1.1511 | 1.1481 | 1.1423 | 1.1349 | 1.1257 | 1.1146
| 0.2 | 1.0332 | 1.0864 | 1.127 | 1.1515 | 1.1631 | 1.1662 | 1.1636 | 1.1573 | 1.1484 | 1.1379 | 1.1252
| 0.25 | 1.0226 | 1.0838 | 1.1329 | 1.1602 | 1.1727 | 1.1757 | 1.1727 | 1.1657 | 1.1562 | 1.145 | 1.1323
| 0.3 | 1.0049 | 1.0787 | 1.1348 | 1.1646 | 1.178 | 1.1814 | 1.1784 | 1.1712 | 1.1614 | 1.1497 | 1.1358
| 0.35 | 0.98723 | 1.0727 | 1.1347 | 1.1669 | 1.1814 | 1.1852 | 1.1823 | 1.1751 | 1.1651 | 1.1533 | 1.1394
| 0.4 | 0.96954 | 1.0666 | 1.1337 | 1.168 | 1.1836 | 1.1879 | 1.1852 | 1.1781 | 1.1681 | 1.1563 | 1.1429
| 0.45 | 0.95185 | 1.0609 | 1.1322 | 1.1685 | 1.1851 | 1.19 | 1.1876 | 1.1807 | 1.1709 | 1.1591 | 1.1465
| 0.5 | 0.93769 | 1.0558 | 1.1305 | 1.1687 | 1.1862 | 1.1917 | 1.1898 | 1.1832 | 1.1735 | 1.1617 | 1.15
| 0.55 | 0.92354 | 1.0511 | 1.1289 | 1.1686 | 1.1871 | 1.1933 | 1.1919 | 1.1855 | 1.1759 | 1.164 | 1.15
| 0.6 | 0.90938 | 1.0468 | 1.1272 | 1.1684 | 1.188 | 1.195 | 1.194 | 1.1877 | 1.178 | 1.166 | 1.1535
| 0.65 | 0.89523 | 1.0428 | 1.1256 | 1.1682 | 1.1889 | 1.1966 | 1.1959 | 1.1896 | 1.1798 | 1.1676 | 1.1535
| 0.7 | 0.88462 | 1.0392 | 1.124 | 1.168 | 1.1899 | 1.1982 | 1.1977 | 1.1913 | 1.1813 | 1.169 | 1.1535
| 0.75 | 0.874 | 1.0359 | 1.1225 | 1.168 | 1.1911 | 1.1998 | 1.1992 | 1.1928 | 1.1826 | 1.1702 | 1.1571
| 0.8 | 0.86338 | 1.0329 | 1.1211 | 1.1682 | 1.1922 | 1.2011 | 1.2005 | 1.194 | 1.1838 | 1.1713 | 1.1571
| 0.85 | 0.85631 | 1.0301 | 1.1199 | 1.1685 | 1.1933 | 1.2023 | 1.2017 | 1.1951 | 1.1848 | 1.1722 | 1.1571
| 0.9 | 0.84923 | 1.0275 | 1.1187 | 1.1689 | 1.1943 | 1.2034 | 1.2026 | 1.196 | 1.1856 | 1.1729 | 1.1606
| 0.95 | 0.83862 | 1.0251 | 1.1177 | 1.1694 | 1.1952 | 1.2043 | 1.2035 | 1.1968 | 1.1864 | 1.1736 | 1.1606
| 1 | 0.83154 | 1.0228 | 1.1169 | 1.1699 | 1.1959 | 1.2051 | 1.2043 | 1.1975 | 1.187 | 1.1743 | 1.1606
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
| 0.05 | 1.1236 | 1.099 | 1.0781 | 1.058 | 1.0384 | 1.0194 | 1.0016 | 0.98387 | 0.96664 | 0.95022 | 0.93436
| 0.1 | 0.99612 | 0.96563 | 0.93789 | 0.91136 | 0.8861 | 0.86219 | 0.84013 | 0.81889 | 0.79883 | 0.7803 | 0.76259
| 0.15 | 0.91918 | 0.88125 | 0.8484 | 0.8183 | 0.79079 | 0.76517 | 0.74188 | 0.71988 | 0.69954 | 0.68089 | 0.6634
| 0.2 | 0.86961 | 0.82158 | 0.78474 | 0.75275 | 0.72401 | 0.69785 | 0.67419 | 0.65217 | 0.63201 | 0.6136 | 0.59668
| 0.25 | 0.83529 | 0.77675 | 0.73629 | 0.70338 | 0.67407 | 0.64739 | 0.62361 | 0.60163 | 0.58167 | 0.56363 | 0.54709
| 0.3 | 0.8099 | 0.74094 | 0.69815 | 0.66441 | 0.63427 | 0.60724 | 0.58309 | 0.56128 | 0.54178 | 0.52408 | 0.50797
| 0.35 | 0.79098 | 0.71153 | 0.66688 | 0.63185 | 0.60102 | 0.57344 | 0.54941 | 0.52794 | 0.50893 | 0.49156 | 0.47611
| 0.4 | 0.77627 | 0.68607 | 0.64033 | 0.60403 | 0.57267 | 0.545 | 0.52089 | 0.49968 | 0.48118 | 0.46451 | 0.44947
| 0.45 | 0.76397 | 0.66442 | 0.61733 | 0.57962 | 0.54752 | 0.52 | 0.49628 | 0.47558 | 0.45749 | 0.44135 | 0.42684
| 0.5 | 0.75429 | 0.64558 | 0.5968 | 0.558 | 0.52553 | 0.49798 | 0.47466 | 0.45454 | 0.43692 | 0.42136 | 0.40726
| 0.55 | 0.74632 | 0.62866 | 0.57841 | 0.5384 | 0.50559 | 0.47846 | 0.45569 | 0.43611 | 0.41882 | 0.40373 | 0.39022
| 0.6 | 0.73912 | 0.61368 | 0.56168 | 0.52073 | 0.48792 | 0.46111 | 0.43892 | 0.41956 | 0.40279 | 0.38817 | 0.37502
| 0.65 | 0.73334 | 0.60016 | 0.54623 | 0.50447 | 0.47164 | 0.44572 | 0.42358 | 0.40479 | 0.38855 | 0.37427 | 0.36154
| 0.7 | 0.72832 | 0.58784 | 0.53168 | 0.48967 | 0.45724 | 0.43131 | 0.40965 | 0.39164 | 0.37581 | 0.36194 | 0.34945
| 0.75 | 0.72358 | 0.57622 | 0.51856 | 0.47603 | 0.44386 | 0.41835 | 0.39733 | 0.37952 | 0.3641 | 0.35047 | 0.3385
| 0.8 | 0.71985 | 0.56558 | 0.50608 | 0.46348 | 0.43164 | 0.40655 | 0.38598 | 0.36848 | 0.35343 | 0.34017 | 0.32846
| 0.85 | 0.71644 | 0.55586 | 0.49463 | 0.45178 | 0.4204 | 0.39577 | 0.37544 | 0.35831 | 0.34365 | 0.33078 | 0.31935
| 0.9 | 0.71303 | 0.54648 | 0.48374 | 0.44103 | 0.40994 | 0.38544 | 0.36565 | 0.34905 | 0.33464 | 0.32217 | 0.31097
| 0.95 | 0.71033 | 0.5375 | 0.47353 | 0.43084 | 0.40012 | 0.37619 | 0.3569 | 0.34055 | 0.32642 | 0.31418 | 0.30333
| 1 | 0.70796 | 0.52914 | 0.46394 | 0.42131 | 0.39109 | 0.3677 | 0.34841 | 0.33245 | 0.31883 | 0.30661 | 0.296
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0026704 | 0.0040617 | 0.0051823 | 0.0061689 | 0.0070455 | 0.0077837 | 0.0082753 | 0.0089295 | 0.009388 | 0.0098101 | 0.010136
| 0.1 | 0.0032786 | 0.0054378 | 0.0068831 | 0.0078993 | 0.00872 | 0.0093558 | 0.0098246 | 0.01029 | 0.010579 | 0.010834 | 0.01104
| 0.15 | 0.0022707 | 0.0056608 | 0.0072713 | 0.0083899 | 0.0092731 | 0.0099011 | 0.010343 | 0.010666 | 0.010858 | 0.011042 | 0.011092
| 0.2 | 0.0013504 | 0.0055589 | 0.0074519 | 0.0088679 | 0.0097513 | 0.010326 | 0.010743 | 0.010922 | 0.010966 | 0.011017 | 0.010976
| 0.25 | 0.00036437 | 0.0055964 | 0.0077494 | 0.0093175 | 0.010189 | 0.010637 | 0.010879 | 0.010894 | 0.010891 | 0.010802 | 0.010671
| 0.3 | -0.00055001 | 0.005602 | 0.0081877 | 0.0096547 | 0.010405 | 0.010699 | 0.010767 | 0.01077 | 0.010662 | 0.010486 | 0.010313
| 0.35 | -0.0010687 | 0.0055984 | 0.0085631 | 0.0099003 | 0.010522 | 0.010666 | 0.010627 | 0.010489 | 0.01039 | 0.01015 | 0.0099868
| 0.4 | -0.0017181 | 0.0057447 | 0.0088309 | 0.010087 | 0.010473 | 0.010557 | 0.010419 | 0.010263 | 0.010017 | 0.0097936 | 0.0096019
| 0.45 | -0.0021633 | 0.0059931 | 0.0090563 | 0.010142 | 0.010377 | 0.010312 | 0.010198 | 0.0099216 | 0.0096656 | 0.0094682 | 0.0091779
| 0.5 | -0.0025096 | 0.0061587 | 0.0091617 | 0.010099 | 0.010237 | 0.010148 | 0.0098472 | 0.0096237 | 0.0093662 | 0.0091174 | 0.0089373
| 0.55 | -0.0027901 | 0.0063277 | 0.0093589 | 0.010089 | 0.010066 | 0.0098757 | 0.009602 | 0.0093927 | 0.0090832 | 0.0088077 | 0.008598
| 0.6 | -0.0030495 | 0.0065684 | 0.0094517 | 0.0099669 | 0.0099246 | 0.009684 | 0.0093665 | 0.0091036 | 0.0087779 | 0.0085346 | 0.008297
| 0.65 | -0.003259 | 0.0067604 | 0.0094068 | 0.0098652 | 0.0097277 | 0.0094394 | 0.0090888 | 0.0087786 | 0.00853 | 0.0082994 | 0.0080181
| 0.7 | -0.0033779 | 0.0069269 | 0.009465 | 0.0097854 | 0.0095543 | 0.0092181 | 0.0089212 | 0.0085823 | 0.0083472 | 0.0080449 | 0.0077957
| 0.75 | -0.0035677 | 0.0070705 | 0.0094027 | 0.0096359 | 0.0093653 | 0.0089992 | 0.0086537 | 0.0083639 | 0.008089 | 0.0078184 | 0.0076069
| 0.8 | -0.0037929 | 0.0072466 | 0.0094213 | 0.0095027 | 0.0092005 | 0.0088137 | 0.0084267 | 0.0081222 | 0.0078718 | 0.0076051 | 0.0074074
| 0.85 | -0.0037831 | 0.0073899 | 0.0093922 | 0.0093707 | 0.0089625 | 0.0086139 | 0.0082769 | 0.0079677 | 0.0076475 | 0.0074194 | 0.0071943
| 0.9 | -0.0038815 | 0.0075154 | 0.0092978 | 0.0092427 | 0.008788 | 0.00846 | 0.008095 | 0.0077802 | 0.0075087 | 0.0073202 | 0.0070762
| 0.95 | -0.0040634 | 0.0076067 | 0.0091805 | 0.0090339 | 0.0086209 | 0.0082511 | 0.0079206 | 0.0075786 | 0.0073196 | 0.0070984 | 0.0069472
| 1 | -0.0041507 | 0.0076767 | 0.009225 | 0.0089161 | 0.0084567 | 0.008112 | 0.007767 | 0.0074501 | 0.0072191 | 0.007014 | 0.0067837
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0016027 | 0.001767 | 0.0019169 | 0.0020561 | 0.0021748 | 0.0022801 | 0.0023755 | 0.0024579 | 0.0025196 | 0.0025778 | 0.0026242
| 0.1 | 0.0019202 | 0.0021925 | 0.0023554 | 0.0024638 | 0.002539 | 0.0025931 | 0.0026383 | 0.0026697 | 0.0026901 | 0.0027066 | 0.0027105
| 0.15 | 0.001831 | 0.0022425 | 0.0023914 | 0.0024728 | 0.0025281 | 0.0025643 | 0.0025844 | 0.0025982 | 0.0026036 | 0.0025965 | 0.0025832
| 0.2 | 0.0016199 | 0.0021959 | 0.0023439 | 0.0024087 | 0.0024617 | 0.0024955 | 0.0025177 | 0.0025238 | 0.0025198 | 0.0024994 | 0.0024802
| 0.25 | 0.0014332 | 0.0021257 | 0.0022745 | 0.0023553 | 0.0024209 | 0.0024614 | 0.0024762 | 0.0024666 | 0.0024452 | 0.0024249 | 0.0023902
| 0.3 | 0.0012662 | 0.0020776 | 0.0022131 | 0.0023369 | 0.0024041 | 0.0024323 | 0.0024338 | 0.0024144 | 0.0023775 | 0.0023444 | 0.0023015
| 0.35 | 0.0011313 | 0.0020186 | 0.0021788 | 0.002324 | 0.0023904 | 0.0024028 | 0.0023861 | 0.0023499 | 0.0023079 | 0.002262 | 0.002216
| 0.4 | 0.00099513 | 0.0019663 | 0.0021737 | 0.0023237 | 0.0023701 | 0.0023615 | 0.002326 | 0.0022831 | 0.0022351 | 0.0021849 | 0.0021297
| 0.45 | 0.00089003 | 0.0019253 | 0.0021673 | 0.0023119 | 0.0023392 | 0.0023107 | 0.0022697 | 0.0022088 | 0.002163 | 0.0021061 | 0.0020551
| 0.5 | 0.00080944 | 0.0018867 | 0.0021742 | 0.002293 | 0.0023036 | 0.0022605 | 0.0022108 | 0.0021467 | 0.0020917 | 0.002036 | 0.0019858
| 0.55 | 0.00072262 | 0.0018608 | 0.0021797 | 0.0022792 | 0.0022688 | 0.0022152 | 0.0021503 | 0.0020895 | 0.0020277 | 0.0019664 | 0.0019211
| 0.6 | 0.00066493 | 0.0018462 | 0.0021708 | 0.0022484 | 0.0022266 | 0.0021631 | 0.0020975 | 0.0020309 | 0.0019678 | 0.0019103 | 0.0018537
| 0.65 | 0.00060767 | 0.0018346 | 0.0021684 | 0.0022245 | 0.0021796 | 0.002116 | 0.0020485 | 0.0019761 | 0.0019118 | 0.0018562 | 0.0017987
| 0.7 | 0.00056913 | 0.001825 | 0.0021599 | 0.0021915 | 0.0021397 | 0.0020698 | 0.0019966 | 0.0019254 | 0.0018602 | 0.0018047 | 0.0017506
| 0.75 | 0.00050797 | 0.0018305 | 0.0021501 | 0.0021615 | 0.0021001 | 0.0020192 | 0.0019457 | 0.001876 | 0.0018103 | 0.0017528 | 0.0016996
| 0.8 | 0.00046728 | 0.0018291 | 0.002134 | 0.0021274 | 0.0020618 | 0.001981 | 0.0019011 | 0.0018276 | 0.0017665 | 0.0017054 | 0.0016569
| 0.85 | 0.00043986 | 0.001843 | 0.0021181 | 0.0020961 | 0.0020211 | 0.0019393 | 0.0018601 | 0.0017865 | 0.0017234 | 0.0016629 | 0.0016115
| 0.9 | 0.00040637 | 0.0018435 | 0.002097 | 0.0020685 | 0.0019826 | 0.0019009 | 0.0018178 | 0.0017452 | 0.0016857 | 0.0016316 | 0.001574
| 0.95 | 0.00037368 | 0.0018461 | 0.0020819 | 0.0020354 | 0.0019482 | 0.0018626 | 0.0017747 | 0.0017077 | 0.0016509 | 0.0015905 | 0.0015426
| 1 | 0.0003436 | 0.0018587 | 0.0020622 | 0.0020087 | 0.0019136 | 0.0018188 | 0.0017431 | 0.0016708 | 0.0016083 | 0.0015581 | 0.001507
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.3303 | 1.595 | 1.8077 | 1.9804 | 2.1238 | 2.2412 | 2.333 | 2.4162 | 2.4846 | 2.5465 | 2.5945
| 0.1 | 1.3099 | 1.8945 | 2.3271 | 2.6754 | 2.8983 | 3.1154 | 3.2468 | 3.3916 | 3.4725 | 3.5554 | 3.6386
| 0.15 | 1.2265 | 2.1201 | 2.6755 | 3.1432 | 3.4309 | 3.8207 | 4.0589 | 4.1374 | 4.2604 | 4.3601 | 4.4386
| 0.2 | 1.1409 | 2.3179 | 3.0895 | 3.6323 | 4.0686 | 4.3795 | 4.6111 | 4.7952 | 4.7198 | 5.0505 | 5.1272
| 0.25 | 1.0779 | 2.5194 | 3.42 | 4.0632 | 4.5321 | 4.8999 | 5.1627 | 5.3784 | 5.535 | 5.6494 | 5.7433
| 0.3 | 1.0416 | 2.6924 | 3.7343 | 4.4801 | 5.0078 | 5.3814 | 5.6802 | 5.9014 | 6.0728 | 6.1927 | 6.2923
| 0.35 | 1.0094 | 2.869 | 4.0312 | 4.8395 | 5.376 | 5.8131 | 6.1301 | 6.3747 | 6.5503 | 6.6801 | 6.7954
| 0.4 | 0.9811 | 3.0504 | 4.3237 | 5.1776 | 5.7874 | 6.2297 | 6.5539 | 6.8097 | 6.9928 | 7.1398 | 7.2427
| 0.45 | 0.96786 | 3.2045 | 4.5722 | 5.486 | 6.1407 | 6.606 | 6.9457 | 7.2117 | 7.4135 | 7.5706 | 7.6765
| 0.5 | 0.95197 | 3.3618 | 4.8348 | 5.7945 | 6.4615 | 6.9575 | 7.3181 | 7.6 | 7.8066 | 7.9597 | 8.0831
| 0.55 | 0.93558 | 3.5334 | 5.0713 | 6.0649 | 6.7802 | 7.2816 | 7.6663 | 7.9528 | 8.1769 | 8.339 | 8.4632
| 0.6 | 0.93149 | 3.6679 | 5.3027 | 6.3355 | 7.0705 | 7.5975 | 7.9976 | 8.2894 | 8.5267 | 8.7017 | 8.8312
| 0.65 | 0.91954 | 3.83 | 5.5088 | 6.5915 | 7.3386 | 7.8981 | 8.3097 | 8.6241 | 8.8674 | 9.0486 | 9.1873
| 0.7 | 0.90895 | 3.9732 | 5.7226 | 6.8252 | 7.6042 | 8.173 | 8.6076 | 8.9402 | 9.1879 | 9.3762 | 9.5287
| 0.75 | 0.90932 | 4.1067 | 5.9182 | 7.0583 | 7.8612 | 8.4517 | 8.9039 | 9.2433 | 9.5012 | 9.6958 | 9.8481
| 0.8 | 0.89962 | 4.2544 | 6.1002 | 7.2702 | 8.1029 | 8.705 | 9.1861 | 9.5373 | 9.8059 | 10.0074 | 10.1624
| 0.85 | 0.89052 | 4.3877 | 6.2803 | 7.4634 | 8.3412 | 8.977 | 9.4559 | 9.8205 | 10.0982 | 10.3117 | 10.4741
| 0.9 | 0.89299 | 4.5156 | 6.4435 | 7.6846 | 8.5698 | 9.2192 | 9.717 | 10.0979 | 10.3832 | 10.6083 | 10.7738
| 0.95 | 0.88494 | 4.6383 | 6.6193 | 7.8825 | 8.7883 | 9.458 | 9.9778 | 10.368 | 10.6655 | 10.8862 | 11.0609
| 1 | 0.87925 | 4.7584 | 6.7847 | 8.0812 | 9.006 | 9.7025 | 10.2246 | 10.6272 | 10.93 | 11.1614 | 11.3426
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0031316 | -0.0011301 | 0.00043156 | 0.0026968 | 0.0052471 | 0.00707 | 0.010407 | 0.01101 | 0.013108 | 0.015041 | 0.016065
| 0.1 | 0.00091112 | 0.0051015 | 0.010143 | 0.014242 | 0.018472 | 0.026652 | 0.024401 | 0.027987 | 0.03353 | 0.036052 | 0.036331
| 0.15 | 0.00036667 | 0.0085789 | 0.01799 | 0.022431 | 0.030361 | 0.038817 | 0.042472 | 0.045341 | 0.053218 | 0.053544 | 0.057008
| 0.2 | -0.0043506 | 0.012341 | 0.025837 | 0.033967 | 0.044719 | 0.054949 | 0.060544 | 0.061712 | 0.072543 | 0.076639 | 0.084946
| 0.25 | -0.0071191 | 0.015663 | 0.033684 | 0.041088 | 0.059078 | 0.070148 | 0.078616 | 0.085807 | 0.090672 | 0.096033 | 0.096247
| 0.3 | -0.0082421 | 0.018986 | 0.041531 | 0.057399 | 0.073436 | 0.085346 | 0.096688 | 0.10535 | 0.10367 | 0.10906 | 0.1162
| 0.35 | -0.011983 | 0.022308 | 0.049378 | 0.073404 | 0.087795 | 0.10055 | 0.11383 | 0.11789 | 0.12008 | 0.12333 | 0.12317
| 0.4 | -0.011744 | 0.02563 | 0.057225 | 0.087784 | 0.10215 | 0.11549 | 0.12132 | 0.12821 | 0.13139 | 0.13545 | 0.13701
| 0.45 | -0.013185 | 0.028953 | 0.065072 | 0.091954 | 0.11356 | 0.12515 | 0.13403 | 0.13995 | 0.14403 | 0.14727 | 0.14895
| 0.5 | -0.014475 | 0.032275 | 0.072919 | 0.1028 | 0.12334 | 0.13398 | 0.14171 | 0.14691 | 0.15317 | 0.15565 | 0.15884
| 0.55 | -0.015788 | 0.035598 | 0.080877 | 0.11309 | 0.13295 | 0.14302 | 0.15116 | 0.1574 | 0.16326 | 0.16647 | 0.16836
| 0.6 | -0.016881 | 0.03892 | 0.092317 | 0.12134 | 0.14108 | 0.15209 | 0.16062 | 0.16503 | 0.16945 | 0.17579 | 0.17653
| 0.65 | -0.016695 | 0.042242 | 0.096022 | 0.12763 | 0.14651 | 0.15943 | 0.16717 | 0.17291 | 0.17754 | 0.1835 | 0.18536
| 0.7 | -0.017475 | 0.045565 | 0.10334 | 0.1351 | 0.15341 | 0.16689 | 0.17733 | 0.18216 | 0.18818 | 0.1905 | 0.19395
| 0.75 | -0.018148 | 0.049467 | 0.10655 | 0.13981 | 0.16034 | 0.17365 | 0.18285 | 0.18973 | 0.19592 | 0.19815 | 0.20277
| 0.8 | -0.01688 | 0.054094 | 0.11294 | 0.14529 | 0.16627 | 0.18039 | 0.18926 | 0.19592 | 0.20291 | 0.20757 | 0.21005
| 0.85 | -0.018734 | 0.05201 | 0.12141 | 0.1518 | 0.17171 | 0.18641 | 0.19691 | 0.20435 | 0.20883 | 0.21341 | 0.21664
| 0.9 | -0.019411 | 0.057161 | 0.12602 | 0.15922 | 0.17741 | 0.19333 | 0.2038 | 0.21083 | 0.21508 | 0.22319 | 0.22568
| 0.95 | -0.018059 | 0.065486 | 0.12968 | 0.16327 | 0.18233 | 0.19803 | 0.2098 | 0.21693 | 0.22105 | 0.22751 | 0.23416
| 1 | -0.018236 | 0.073812 | 0.13847 | 0.16858 | 0.18937 | 0.2046 | 0.21562 | 0.22191 | 0.22963 | 0.23704 | 0.2389
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0016675 | -0.0047474 | -0.0069572 | -0.0085816 | -0.0098708 | -0.010733 | -0.01148 | -0.012005 | -0.012328 | -0.012582 | -0.012842
| 0.1 | 0.00084407 | -0.0054089 | -0.0098573 | -0.012762 | -0.014495 | -0.016603 | -0.016892 | -0.017956 | -0.018515 | -0.018636 | -0.019036
| 0.15 | 0.0017766 | -0.0068689 | -0.01216 | -0.016544 | -0.019473 | -0.020068 | -0.021296 | -0.021571 | -0.022524 | -0.02329 | -0.023089
| 0.2 | 0.0022557 | -0.0099008 | -0.013714 | -0.019184 | -0.02156 | -0.023534 | -0.025381 | -0.025776 | -0.026172 | -0.028324 | -0.027038
| 0.25 | 0.001929 | -0.010488 | -0.015268 | -0.021824 | -0.023647 | -0.026404 | -0.028654 | -0.029237 | -0.029821 | -0.031249 | -0.030986
| 0.3 | 0.0017152 | -0.012978 | -0.017471 | -0.024464 | -0.025735 | -0.029274 | -0.031143 | -0.032018 | -0.032542 | -0.033364 | -0.033328
| 0.35 | 0.0013198 | -0.013399 | -0.021087 | -0.026139 | -0.027822 | -0.030742 | -0.032565 | -0.034141 | -0.034551 | -0.035388 | -0.035857
| 0.4 | 0.0013603 | -0.014459 | -0.022596 | -0.027002 | -0.030336 | -0.03282 | -0.034739 | -0.036112 | -0.037224 | -0.037547 | -0.038564
| 0.45 | 0.0012511 | -0.01552 | -0.024876 | -0.028819 | -0.032271 | -0.034536 | -0.036347 | -0.037971 | -0.039065 | -0.039779 | -0.040626
| 0.5 | 0.00080866 | -0.016722 | -0.025733 | -0.02947 | -0.033577 | -0.036102 | -0.038218 | -0.039708 | -0.041163 | -0.041849 | -0.042762
| 0.55 | 0.00091992 | -0.017875 | -0.026389 | -0.031222 | -0.034861 | -0.037942 | -0.040088 | -0.041536 | -0.042852 | -0.043924 | -0.044657
| 0.6 | 0.00067612 | -0.019824 | -0.027148 | -0.032342 | -0.036196 | -0.03892 | -0.041559 | -0.043297 | -0.044725 | -0.045882 | -0.046674
| 0.65 | 0.00054623 | -0.020158 | -0.027919 | -0.033319 | -0.03771 | -0.040524 | -0.043403 | -0.045224 | -0.046646 | -0.047726 | -0.048551
| 0.7 | 0.0002636 | -0.020774 | -0.028741 | -0.034555 | -0.038658 | -0.042008 | -0.044813 | -0.047115 | -0.048469 | -0.049647 | -0.0507
| 0.75 | 0.00041474 | -0.021479 | -0.029702 | -0.035541 | -0.039828 | -0.043595 | -0.046418 | -0.048703 | -0.050293 | -0.051258 | -0.052363
| 0.8 | 0.00037067 | -0.022301 | -0.03077 | -0.036489 | -0.041001 | -0.045019 | -0.048067 | -0.050342 | -0.051755 | -0.053229 | -0.054097
| 0.85 | 0.00017807 | -0.023595 | -0.031304 | -0.03748 | -0.043274 | -0.046268 | -0.049522 | -0.051701 | -0.053577 | -0.055197 | -0.055832
| 0.9 | 7.7039e-05 | -0.023425 | -0.031828 | -0.038364 | -0.043834 | -0.047662 | -0.051084 | -0.053271 | -0.054987 | -0.05654 | -0.05772
| 0.95 | 6.642e-05 | -0.024236 | -0.032659 | -0.039466 | -0.045016 | -0.049315 | -0.052643 | -0.054822 | -0.056631 | -0.058187 | -0.059227
| 1 | -9.495e-06 | -0.025742 | -0.033421 | -0.040356 | -0.04619 | -0.050544 | -0.054003 | -0.056286 | -0.058455 | -0.059616 | -0.060631
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-21.52) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-92.41))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-21.52) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-92.41))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS5_LS>= (hidden)
If Iload/Isc x 5.6569 ≥1 | [12 empty] | If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 |  | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0236 | 1.0379 | 1.049 | 1.0569 | 1.0619 | 1.0643 | 1.0646 | 1.0632 | 1.0605 | 1.0567 | 1.052 |  | 0.05 | 1.0236 | 1.0379 | 1.049 | 1.0569 | 1.0619 | 1.0643 | 1.0646 | 1.0632 | 1.0605 | 1.0567 | 1.052
| 0.1 | 1.0338 | 1.0676 | 1.0939 | 1.1108 | 1.12 | 1.1233 | 1.1225 | 1.1186 | 1.1125 | 1.1049 | 1.0961 |  | 0.1 | 1.0338 | 1.0676 | 1.0939 | 1.1108 | 1.12 | 1.1233 | 1.1225 | 1.1186 | 1.1125 | 1.1049 | 1.0961
| 0.15 | 1.0333 | 1.0708 | 1.1104 | 1.1337 | 1.1453 | 1.1489 | 1.1472 | 1.1418 | 1.134 | 1.1245 | 1.1138 |  | 0.15 | 1.0333 | 1.0708 | 1.1104 | 1.1337 | 1.1453 | 1.1489 | 1.1472 | 1.1418 | 1.134 | 1.1245 | 1.1138
| 0.2 | 1.0217 | 1.0728 | 1.1165 | 1.1446 | 1.158 | 1.162 | 1.1599 | 1.1539 | 1.1452 | 1.1348 | 1.1232 |  | 0.2 | 1.0217 | 1.0728 | 1.1165 | 1.1446 | 1.158 | 1.162 | 1.1599 | 1.1539 | 1.1452 | 1.1348 | 1.1232
| 0.25 | 1.0045 | 1.0707 | 1.1183 | 1.1503 | 1.1651 | 1.1696 | 1.1675 | 1.1613 | 1.1523 | 1.1415 | 1.1295 |  | 0.25 | 1.0045 | 1.0707 | 1.1183 | 1.1503 | 1.1651 | 1.1696 | 1.1675 | 1.1613 | 1.1523 | 1.1415 | 1.1295
| 0.3 | 0.98547 | 1.0665 | 1.1199 | 1.1532 | 1.1694 | 1.1746 | 1.1728 | 1.1667 | 1.1576 | 1.1467 | 1.1344 |  | 0.3 | 0.98547 | 1.0665 | 1.1199 | 1.1532 | 1.1694 | 1.1746 | 1.1728 | 1.1667 | 1.1576 | 1.1467 | 1.1344
| 0.35 | 0.96623 | 1.0616 | 1.1213 | 1.1548 | 1.1724 | 1.1784 | 1.1771 | 1.1711 | 1.1621 | 1.1509 | 1.1385 |  | 0.35 | 0.96623 | 1.0616 | 1.1213 | 1.1548 | 1.1724 | 1.1784 | 1.1771 | 1.1711 | 1.1621 | 1.1509 | 1.1385
| 0.4 | 0.9477 | 1.0565 | 1.1217 | 1.1557 | 1.1748 | 1.1816 | 1.1808 | 1.1749 | 1.1658 | 1.1545 | 1.1418 |  | 0.4 | 0.9477 | 1.0565 | 1.1217 | 1.1557 | 1.1748 | 1.1816 | 1.1808 | 1.1749 | 1.1658 | 1.1545 | 1.1418
| 0.45 | 0.93031 | 1.0516 | 1.1215 | 1.1569 | 1.1769 | 1.1845 | 1.184 | 1.1781 | 1.1689 | 1.1574 | 1.1445 |  | 0.45 | 0.93031 | 1.0516 | 1.1215 | 1.1569 | 1.1769 | 1.1845 | 1.184 | 1.1781 | 1.1689 | 1.1574 | 1.1445
| 0.5 | 0.91419 | 1.0471 | 1.1208 | 1.1578 | 1.1789 | 1.1871 | 1.1867 | 1.1809 | 1.1715 | 1.1599 | 1.1468 |  | 0.5 | 0.91419 | 1.0471 | 1.1208 | 1.1578 | 1.1789 | 1.1871 | 1.1867 | 1.1809 | 1.1715 | 1.1599 | 1.1468
| 0.55 | 0.89938 | 1.0428 | 1.1198 | 1.1584 | 1.1807 | 1.1894 | 1.1891 | 1.1832 | 1.1737 | 1.1619 | 1.1486 |  | 0.55 | 0.89938 | 1.0428 | 1.1198 | 1.1584 | 1.1807 | 1.1894 | 1.1891 | 1.1832 | 1.1737 | 1.1619 | 1.1486
| 0.6 | 0.88582 | 1.039 | 1.1188 | 1.1588 | 1.1824 | 1.1914 | 1.1911 | 1.1851 | 1.1755 | 1.1636 | 1.1502 |  | 0.6 | 0.88582 | 1.039 | 1.1188 | 1.1588 | 1.1824 | 1.1914 | 1.1911 | 1.1851 | 1.1755 | 1.1636 | 1.1502
| 0.65 | 0.87342 | 1.0355 | 1.1176 | 1.1593 | 1.1839 | 1.1931 | 1.1929 | 1.1868 | 1.1771 | 1.1651 | 1.1516 |  | 0.65 | 0.87342 | 1.0355 | 1.1176 | 1.1593 | 1.1839 | 1.1931 | 1.1929 | 1.1868 | 1.1771 | 1.1651 | 1.1516
| 0.7 | 0.86208 | 1.0322 | 1.1165 | 1.1601 | 1.1853 | 1.1946 | 1.1943 | 1.1882 | 1.1784 | 1.1664 | 1.1528 |  | 0.7 | 0.86208 | 1.0322 | 1.1165 | 1.1601 | 1.1853 | 1.1946 | 1.1943 | 1.1882 | 1.1784 | 1.1664 | 1.1528
| 0.75 | 0.85171 | 1.0292 | 1.1154 | 1.1608 | 1.1865 | 1.1959 | 1.1956 | 1.1895 | 1.1797 | 1.1675 | 1.1539 |  | 0.75 | 0.85171 | 1.0292 | 1.1154 | 1.1608 | 1.1865 | 1.1959 | 1.1956 | 1.1895 | 1.1797 | 1.1675 | 1.1539
| 0.8 | 0.84221 | 1.0265 | 1.1144 | 1.1616 | 1.1875 | 1.197 | 1.1968 | 1.1906 | 1.1808 | 1.1686 | 1.1549 |  | 0.8 | 0.84221 | 1.0265 | 1.1144 | 1.1616 | 1.1875 | 1.197 | 1.1968 | 1.1906 | 1.1808 | 1.1686 | 1.1549
| 0.85 | 0.83348 | 1.0239 | 1.1135 | 1.1622 | 1.1885 | 1.198 | 1.1978 | 1.1916 | 1.1818 | 1.1695 | 1.1558 |  | 0.85 | 0.83348 | 1.0239 | 1.1135 | 1.1622 | 1.1885 | 1.198 | 1.1978 | 1.1916 | 1.1818 | 1.1695 | 1.1558
| 0.9 | 0.82546 | 1.0215 | 1.1126 | 1.1628 | 1.1893 | 1.1989 | 1.1987 | 1.1926 | 1.1827 | 1.1704 | 1.1567 |  | 0.9 | 0.82546 | 1.0215 | 1.1126 | 1.1628 | 1.1893 | 1.1989 | 1.1987 | 1.1926 | 1.1827 | 1.1704 | 1.1567
| 0.95 | 0.81806 | 1.0193 | 1.1119 | 1.1634 | 1.19 | 1.1997 | 1.1996 | 1.1935 | 1.1835 | 1.1712 | 1.1574 |  | 0.95 | 0.81806 | 1.0193 | 1.1119 | 1.1634 | 1.19 | 1.1997 | 1.1996 | 1.1935 | 1.1835 | 1.1712 | 1.1574
| 1 | 0.81122 | 1.0172 | 1.1113 | 1.1638 | 1.1906 | 1.2004 | 1.2004 | 1.1943 | 1.1843 | 1.172 | 1.1581 |  | 1 | 0.81122 | 1.0172 | 1.1113 | 1.1638 | 1.1906 | 1.2004 | 1.2004 | 1.1943 | 1.1843 | 1.172 | 1.1581
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 |  | 0 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| 0.05 | 1.338 | 1.3118 | 1.2858 | 1.2602 | 1.2352 | 1.2112 | 1.1882 | 1.1669 | 1.1456 | 1.1255 | 1.1063 |  | 0.05 | 1.338 | 1.3118 | 1.2858 | 1.2602 | 1.2352 | 1.2112 | 1.1882 | 1.1669 | 1.1456 | 1.1255 | 1.1063
| 0.1 | 1.1924 | 1.1532 | 1.1169 | 1.0832 | 1.0517 | 1.0224 | 0.99528 | 0.96949 | 0.94558 | 0.923 | 0.90196 |  | 0.1 | 1.1924 | 1.1532 | 1.1169 | 1.0832 | 1.0517 | 1.0224 | 0.99528 | 0.96949 | 0.94558 | 0.923 | 0.90196
| 0.15 | 1.1048 | 1.0529 | 1.0104 | 0.97298 | 0.93888 | 0.90788 | 0.87955 | 0.85268 | 0.82854 | 0.80572 | 0.78492 |  | 0.15 | 1.1048 | 1.0529 | 1.0104 | 0.97298 | 0.93888 | 0.90788 | 0.87955 | 0.85268 | 0.82854 | 0.80572 | 0.78492
| 0.2 | 1.0472 | 0.98183 | 0.93542 | 0.89572 | 0.8605 | 0.82805 | 0.79926 | 0.77245 | 0.74801 | 0.72562 | 0.70504 |  | 0.2 | 1.0472 | 0.98183 | 0.93542 | 0.89572 | 0.8605 | 0.82805 | 0.79926 | 0.77245 | 0.74801 | 0.72562 | 0.70504
| 0.25 | 1.0076 | 0.92854 | 0.87857 | 0.8373 | 0.80072 | 0.76729 | 0.73821 | 0.7114 | 0.68751 | 0.66566 | 0.64611 |  | 0.25 | 1.0076 | 0.92854 | 0.87857 | 0.8373 | 0.80072 | 0.76729 | 0.73821 | 0.7114 | 0.68751 | 0.66566 | 0.64611
| 0.3 | 0.97887 | 0.88594 | 0.83321 | 0.7902 | 0.7521 | 0.71863 | 0.68902 | 0.66284 | 0.63939 | 0.61835 | 0.59916 |  | 0.3 | 0.97887 | 0.88594 | 0.83321 | 0.7902 | 0.7521 | 0.71863 | 0.68902 | 0.66284 | 0.63939 | 0.61835 | 0.59916
| 0.35 | 0.9564 | 0.85093 | 0.79566 | 0.75056 | 0.71144 | 0.67781 | 0.64859 | 0.62317 | 0.5999 | 0.57983 | 0.5616 |  | 0.35 | 0.9564 | 0.85093 | 0.79566 | 0.75056 | 0.71144 | 0.67781 | 0.64859 | 0.62317 | 0.5999 | 0.57983 | 0.5616
| 0.4 | 0.93943 | 0.82139 | 0.76346 | 0.71633 | 0.67685 | 0.64318 | 0.61464 | 0.58927 | 0.56721 | 0.5475 | 0.52993 |  | 0.4 | 0.93943 | 0.82139 | 0.76346 | 0.71633 | 0.67685 | 0.64318 | 0.61464 | 0.58927 | 0.56721 | 0.5475 | 0.52993
| 0.45 | 0.92576 | 0.7956 | 0.73514 | 0.68625 | 0.64668 | 0.61328 | 0.58523 | 0.56086 | 0.53943 | 0.52013 | 0.50326 |  | 0.45 | 0.92576 | 0.7956 | 0.73514 | 0.68625 | 0.64668 | 0.61328 | 0.58523 | 0.56086 | 0.53943 | 0.52013 | 0.50326
| 0.5 | 0.91472 | 0.77324 | 0.70967 | 0.65987 | 0.61991 | 0.58729 | 0.55974 | 0.53575 | 0.51515 | 0.49643 | 0.48024 |  | 0.5 | 0.91472 | 0.77324 | 0.70967 | 0.65987 | 0.61991 | 0.58729 | 0.55974 | 0.53575 | 0.51515 | 0.49643 | 0.48024
| 0.55 | 0.90466 | 0.75317 | 0.68649 | 0.6363 | 0.59656 | 0.56404 | 0.53743 | 0.51388 | 0.49395 | 0.4758 | 0.46001 |  | 0.55 | 0.90466 | 0.75317 | 0.68649 | 0.6363 | 0.59656 | 0.56404 | 0.53743 | 0.51388 | 0.49395 | 0.4758 | 0.46001
| 0.6 | 0.89687 | 0.73525 | 0.66564 | 0.61484 | 0.57537 | 0.54365 | 0.51734 | 0.49458 | 0.47506 | 0.45783 | 0.44209 |  | 0.6 | 0.89687 | 0.73525 | 0.66564 | 0.61484 | 0.57537 | 0.54365 | 0.51734 | 0.49458 | 0.47506 | 0.45783 | 0.44209
| 0.65 | 0.89021 | 0.71849 | 0.64676 | 0.59544 | 0.55615 | 0.52499 | 0.4992 | 0.47723 | 0.45825 | 0.44131 | 0.42642 |  | 0.65 | 0.89021 | 0.71849 | 0.64676 | 0.59544 | 0.55615 | 0.52499 | 0.4992 | 0.47723 | 0.45825 | 0.44131 | 0.42642
| 0.7 | 0.88391 | 0.70327 | 0.62927 | 0.57768 | 0.53897 | 0.50853 | 0.4832 | 0.46163 | 0.44314 | 0.42664 | 0.41199 |  | 0.7 | 0.88391 | 0.70327 | 0.62927 | 0.57768 | 0.53897 | 0.50853 | 0.4832 | 0.46163 | 0.44314 | 0.42664 | 0.41199
| 0.75 | 0.87877 | 0.68916 | 0.61321 | 0.56139 | 0.52339 | 0.49323 | 0.46858 | 0.44741 | 0.42946 | 0.4133 | 0.3991 |  | 0.75 | 0.87877 | 0.68916 | 0.61321 | 0.56139 | 0.52339 | 0.49323 | 0.46858 | 0.44741 | 0.42946 | 0.4133 | 0.3991
| 0.8 | 0.87436 | 0.67587 | 0.59782 | 0.54638 | 0.50898 | 0.47939 | 0.45497 | 0.43458 | 0.41683 | 0.40115 | 0.38752 |  | 0.8 | 0.87436 | 0.67587 | 0.59782 | 0.54638 | 0.50898 | 0.47939 | 0.45497 | 0.43458 | 0.41683 | 0.40115 | 0.38752
| 0.85 | 0.86986 | 0.66328 | 0.58421 | 0.53274 | 0.49555 | 0.46643 | 0.44255 | 0.42276 | 0.40527 | 0.39036 | 0.37696 |  | 0.85 | 0.86986 | 0.66328 | 0.58421 | 0.53274 | 0.49555 | 0.46643 | 0.44255 | 0.42276 | 0.40527 | 0.39036 | 0.37696
| 0.9 | 0.86658 | 0.65157 | 0.57124 | 0.51975 | 0.48325 | 0.45472 | 0.43149 | 0.41192 | 0.39472 | 0.38006 | 0.36693 |  | 0.9 | 0.86658 | 0.65157 | 0.57124 | 0.51975 | 0.48325 | 0.45472 | 0.43149 | 0.41192 | 0.39472 | 0.38006 | 0.36693
| 0.95 | 0.86334 | 0.64046 | 0.55894 | 0.50783 | 0.47162 | 0.44361 | 0.42097 | 0.40165 | 0.38495 | 0.37054 | 0.3579 |  | 0.95 | 0.86334 | 0.64046 | 0.55894 | 0.50783 | 0.47162 | 0.44361 | 0.42097 | 0.40165 | 0.38495 | 0.37054 | 0.3579
| 1 | 0.86054 | 0.62995 | 0.54761 | 0.49684 | 0.46078 | 0.43355 | 0.41119 | 0.39213 | 0.37592 | 0.36177 | 0.34928 |  | 1 | 0.86054 | 0.62995 | 0.54761 | 0.49684 | 0.46078 | 0.43355 | 0.41119 | 0.39213 | 0.37592 | 0.36177 | 0.34928
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0069409 | 0.0077604 | 0.0084833 | 0.0091355 | 0.0096876 | 0.010177 | 0.010732 | 0.011063 | 0.011382 | 0.011607 | 0.011825 |  | 0.05 | 0.0069409 | 0.0077604 | 0.0084833 | 0.0091355 | 0.0096876 | 0.010177 | 0.010732 | 0.011063 | 0.011382 | 0.011607 | 0.011825
| 0.1 | 0.0078005 | 0.00903 | 0.0098351 | 0.010484 | 0.010956 | 0.011318 | 0.011744 | 0.011957 | 0.012022 | 0.012137 | 0.012221 |  | 0.1 | 0.0078005 | 0.00903 | 0.0098351 | 0.010484 | 0.010956 | 0.011318 | 0.011744 | 0.011957 | 0.012022 | 0.012137 | 0.012221
| 0.15 | 0.0072742 | 0.0090248 | 0.0099973 | 0.010706 | 0.011249 | 0.011639 | 0.01199 | 0.012124 | 0.012088 | 0.012098 | 0.012051 |  | 0.15 | 0.0072742 | 0.0090248 | 0.0099973 | 0.010706 | 0.011249 | 0.011639 | 0.01199 | 0.012124 | 0.012088 | 0.012098 | 0.012051
| 0.2 | 0.0061592 | 0.0087911 | 0.010065 | 0.01092 | 0.011523 | 0.011861 | 0.012041 | 0.012011 | 0.01192 | 0.011892 | 0.011752 |  | 0.2 | 0.0061592 | 0.0087911 | 0.010065 | 0.01092 | 0.011523 | 0.011861 | 0.012041 | 0.012011 | 0.01192 | 0.011892 | 0.011752
| 0.25 | 0.0052603 | 0.0085994 | 0.010169 | 0.01117 | 0.01168 | 0.011887 | 0.011909 | 0.01175 | 0.011653 | 0.011521 | 0.011314 |  | 0.25 | 0.0052603 | 0.0085994 | 0.010169 | 0.01117 | 0.01168 | 0.011887 | 0.011909 | 0.01175 | 0.011653 | 0.011521 | 0.011314
| 0.3 | 0.0044711 | 0.0084851 | 0.010309 | 0.011338 | 0.011672 | 0.011702 | 0.011659 | 0.011452 | 0.011214 | 0.011068 | 0.010802 |  | 0.3 | 0.0044711 | 0.0084851 | 0.010309 | 0.011338 | 0.011672 | 0.011702 | 0.011659 | 0.011452 | 0.011214 | 0.011068 | 0.010802
| 0.35 | 0.0038917 | 0.0084003 | 0.010524 | 0.011392 | 0.011563 | 0.011453 | 0.01133 | 0.011075 | 0.010883 | 0.010611 | 0.010362 |  | 0.35 | 0.0038917 | 0.0084003 | 0.010524 | 0.011392 | 0.011563 | 0.011453 | 0.01133 | 0.011075 | 0.010883 | 0.010611 | 0.010362
| 0.4 | 0.0033594 | 0.0083857 | 0.010667 | 0.011337 | 0.011373 | 0.011213 | 0.011053 | 0.010705 | 0.010481 | 0.01021 | 0.0099171 |  | 0.4 | 0.0033594 | 0.0083857 | 0.010667 | 0.011337 | 0.011373 | 0.011213 | 0.011053 | 0.010705 | 0.010481 | 0.01021 | 0.0099171
| 0.45 | 0.0028737 | 0.0085365 | 0.010698 | 0.011237 | 0.011192 | 0.010942 | 0.010639 | 0.010351 | 0.010042 | 0.0097356 | 0.0095192 |  | 0.45 | 0.0028737 | 0.0085365 | 0.010698 | 0.011237 | 0.011192 | 0.010942 | 0.010639 | 0.010351 | 0.010042 | 0.0097356 | 0.0095192
| 0.5 | 0.0023812 | 0.0086256 | 0.010679 | 0.011107 | 0.01094 | 0.010611 | 0.010324 | 0.009994 | 0.0097229 | 0.0094796 | 0.0091613 |  | 0.5 | 0.0023812 | 0.0086256 | 0.010679 | 0.011107 | 0.01094 | 0.010611 | 0.010324 | 0.009994 | 0.0097229 | 0.0094796 | 0.0091613
| 0.55 | 0.002199 | 0.008745 | 0.010683 | 0.010922 | 0.010711 | 0.010377 | 0.010005 | 0.0097525 | 0.0093481 | 0.0091312 | 0.0088646 |  | 0.55 | 0.002199 | 0.008745 | 0.010683 | 0.010922 | 0.010711 | 0.010377 | 0.010005 | 0.0097525 | 0.0093481 | 0.0091312 | 0.0088646
| 0.6 | 0.0019184 | 0.0087903 | 0.010641 | 0.010785 | 0.01046 | 0.010106 | 0.0097017 | 0.009409 | 0.0090802 | 0.0088523 | 0.0085505 |  | 0.6 | 0.0019184 | 0.0087903 | 0.010641 | 0.010785 | 0.01046 | 0.010106 | 0.0097017 | 0.009409 | 0.0090802 | 0.0088523 | 0.0085505
| 0.65 | 0.0015446 | 0.0089405 | 0.010583 | 0.010555 | 0.010183 | 0.0098152 | 0.0094284 | 0.0091245 | 0.0088093 | 0.0085942 | 0.0083332 |  | 0.65 | 0.0015446 | 0.0089405 | 0.010583 | 0.010555 | 0.010183 | 0.0098152 | 0.0094284 | 0.0091245 | 0.0088093 | 0.0085942 | 0.0083332
| 0.7 | 0.0013403 | 0.0090279 | 0.010497 | 0.01033 | 0.0099984 | 0.0095564 | 0.0092173 | 0.0088788 | 0.0086346 | 0.0083014 | 0.0080956 |  | 0.7 | 0.0013403 | 0.0090279 | 0.010497 | 0.01033 | 0.0099984 | 0.0095564 | 0.0092173 | 0.0088788 | 0.0086346 | 0.0083014 | 0.0080956
| 0.75 | 0.0012773 | 0.0091103 | 0.010317 | 0.010147 | 0.0097544 | 0.0093123 | 0.0089626 | 0.0086487 | 0.0083724 | 0.0081356 | 0.0078886 |  | 0.75 | 0.0012773 | 0.0091103 | 0.010317 | 0.010147 | 0.0097544 | 0.0093123 | 0.0089626 | 0.0086487 | 0.0083724 | 0.0081356 | 0.0078886
| 0.8 | 0.0010022 | 0.0091201 | 0.010247 | 0.0099688 | 0.0095564 | 0.0091164 | 0.0087362 | 0.0083856 | 0.0081458 | 0.0078588 | 0.007668 |  | 0.8 | 0.0010022 | 0.0091201 | 0.010247 | 0.0099688 | 0.0095564 | 0.0091164 | 0.0087362 | 0.0083856 | 0.0081458 | 0.0078588 | 0.007668
| 0.85 | 0.00083829 | 0.0091217 | 0.010214 | 0.0098095 | 0.0093625 | 0.0088793 | 0.0085379 | 0.0082266 | 0.0079659 | 0.0076894 | 0.0075047 |  | 0.85 | 0.00083829 | 0.0091217 | 0.010214 | 0.0098095 | 0.0093625 | 0.0088793 | 0.0085379 | 0.0082266 | 0.0079659 | 0.0076894 | 0.0075047
| 0.9 | 0.00069909 | 0.009227 | 0.010062 | 0.0096429 | 0.0091194 | 0.008728 | 0.0083773 | 0.0080059 | 0.0077586 | 0.0075085 | 0.0072957 |  | 0.9 | 0.00069909 | 0.009227 | 0.010062 | 0.0096429 | 0.0091194 | 0.008728 | 0.0083773 | 0.0080059 | 0.0077586 | 0.0075085 | 0.0072957
| 0.95 | 0.00062337 | 0.0092012 | 0.0098914 | 0.0094825 | 0.0089387 | 0.008523 | 0.0081774 | 0.0078521 | 0.0076054 | 0.0073763 | 0.0071737 |  | 0.95 | 0.00062337 | 0.0092012 | 0.0098914 | 0.0094825 | 0.0089387 | 0.008523 | 0.0081774 | 0.0078521 | 0.0076054 | 0.0073763 | 0.0071737
| 1 | 0.00051999 | 0.0092405 | 0.0098139 | 0.0092723 | 0.0087843 | 0.0083511 | 0.0079918 | 0.0076929 | 0.0074608 | 0.007194 | 0.006999 |  | 1 | 0.00051999 | 0.0092405 | 0.0098139 | 0.0092723 | 0.0087843 | 0.0083511 | 0.0079918 | 0.0076929 | 0.0074608 | 0.007194 | 0.006999
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0015898 | 0.0017159 | 0.0018428 | 0.001954 | 0.0020553 | 0.0021462 | 0.0022389 | 0.0023103 | 0.0023644 | 0.0024085 | 0.0024517 |  | 0.05 | 0.0015898 | 0.0017159 | 0.0018428 | 0.001954 | 0.0020553 | 0.0021462 | 0.0022389 | 0.0023103 | 0.0023644 | 0.0024085 | 0.0024517
| 0.1 | 0.0018446 | 0.0020661 | 0.0022032 | 0.0022835 | 0.0023536 | 0.0024059 | 0.0024584 | 0.0024813 | 0.0024999 | 0.0025139 | 0.0025096 |  | 0.1 | 0.0018446 | 0.0020661 | 0.0022032 | 0.0022835 | 0.0023536 | 0.0024059 | 0.0024584 | 0.0024813 | 0.0024999 | 0.0025139 | 0.0025096
| 0.15 | 0.0017326 | 0.0020918 | 0.0022388 | 0.002316 | 0.0023541 | 0.0023864 | 0.0024175 | 0.0024311 | 0.0024291 | 0.0024194 | 0.0024115 |  | 0.15 | 0.0017326 | 0.0020918 | 0.0022388 | 0.002316 | 0.0023541 | 0.0023864 | 0.0024175 | 0.0024311 | 0.0024291 | 0.0024194 | 0.0024115
| 0.2 | 0.0015367 | 0.0020553 | 0.0021962 | 0.0022674 | 0.0023106 | 0.0023407 | 0.0023732 | 0.0023736 | 0.0023593 | 0.0023348 | 0.0023159 |  | 0.2 | 0.0015367 | 0.0020553 | 0.0021962 | 0.0022674 | 0.0023106 | 0.0023407 | 0.0023732 | 0.0023736 | 0.0023593 | 0.0023348 | 0.0023159
| 0.25 | 0.0013772 | 0.0020032 | 0.0021433 | 0.0022316 | 0.0022927 | 0.00231 | 0.0023347 | 0.0023115 | 0.0022856 | 0.0022692 | 0.002235 |  | 0.25 | 0.0013772 | 0.0020032 | 0.0021433 | 0.0022316 | 0.0022927 | 0.00231 | 0.0023347 | 0.0023115 | 0.0022856 | 0.0022692 | 0.002235
| 0.3 | 0.0012322 | 0.0019565 | 0.002108 | 0.0022077 | 0.0022781 | 0.0022792 | 0.0022797 | 0.0022412 | 0.0022142 | 0.0021809 | 0.002137 |  | 0.3 | 0.0012322 | 0.0019565 | 0.002108 | 0.0022077 | 0.0022781 | 0.0022792 | 0.0022797 | 0.0022412 | 0.0022142 | 0.0021809 | 0.002137
| 0.35 | 0.0011218 | 0.0019083 | 0.0020827 | 0.0022057 | 0.0022476 | 0.0022461 | 0.0022261 | 0.0021892 | 0.0021454 | 0.0021001 | 0.0020627 |  | 0.35 | 0.0011218 | 0.0019083 | 0.0020827 | 0.0022057 | 0.0022476 | 0.0022461 | 0.0022261 | 0.0021892 | 0.0021454 | 0.0021001 | 0.0020627
| 0.4 | 0.0009907 | 0.0018706 | 0.0020734 | 0.0021973 | 0.0022155 | 0.0022057 | 0.002169 | 0.0021179 | 0.0020798 | 0.0020357 | 0.001985 |  | 0.4 | 0.0009907 | 0.0018706 | 0.0020734 | 0.0021973 | 0.0022155 | 0.0022057 | 0.002169 | 0.0021179 | 0.0020798 | 0.0020357 | 0.001985
| 0.45 | 0.00090036 | 0.0018411 | 0.0020665 | 0.0021679 | 0.0021841 | 0.0021528 | 0.0021122 | 0.0020607 | 0.0020116 | 0.0019526 | 0.0019076 |  | 0.45 | 0.00090036 | 0.0018411 | 0.0020665 | 0.0021679 | 0.0021841 | 0.0021528 | 0.0021122 | 0.0020607 | 0.0020116 | 0.0019526 | 0.0019076
| 0.5 | 0.00083946 | 0.0018084 | 0.0020636 | 0.0021482 | 0.0021503 | 0.0021064 | 0.0020594 | 0.0020038 | 0.0019483 | 0.0018934 | 0.0018475 |  | 0.5 | 0.00083946 | 0.0018084 | 0.0020636 | 0.0021482 | 0.0021503 | 0.0021064 | 0.0020594 | 0.0020038 | 0.0019483 | 0.0018934 | 0.0018475
| 0.55 | 0.00077059 | 0.0017846 | 0.0020682 | 0.0021301 | 0.002111 | 0.002065 | 0.0020038 | 0.0019447 | 0.0018875 | 0.0018331 | 0.0017866 |  | 0.55 | 0.00077059 | 0.0017846 | 0.0020682 | 0.0021301 | 0.002111 | 0.002065 | 0.0020038 | 0.0019447 | 0.0018875 | 0.0018331 | 0.0017866
| 0.6 | 0.00069364 | 0.0017837 | 0.0020468 | 0.0020999 | 0.0020753 | 0.0020106 | 0.0019562 | 0.0018967 | 0.0018322 | 0.0017818 | 0.0017299 |  | 0.6 | 0.00069364 | 0.0017837 | 0.0020468 | 0.0020999 | 0.0020753 | 0.0020106 | 0.0019562 | 0.0018967 | 0.0018322 | 0.0017818 | 0.0017299
| 0.65 | 0.00066017 | 0.0017732 | 0.0020375 | 0.0020734 | 0.0020261 | 0.0019691 | 0.0019012 | 0.0018345 | 0.0017861 | 0.0017242 | 0.001671 |  | 0.65 | 0.00066017 | 0.0017732 | 0.0020375 | 0.0020734 | 0.0020261 | 0.0019691 | 0.0019012 | 0.0018345 | 0.0017861 | 0.0017242 | 0.001671
| 0.7 | 0.00061588 | 0.001769 | 0.0020276 | 0.0020457 | 0.0019991 | 0.0019282 | 0.00186 | 0.0017953 | 0.0017323 | 0.0016787 | 0.0016269 |  | 0.7 | 0.00061588 | 0.001769 | 0.0020276 | 0.0020457 | 0.0019991 | 0.0019282 | 0.00186 | 0.0017953 | 0.0017323 | 0.0016787 | 0.0016269
| 0.75 | 0.00057388 | 0.0017623 | 0.0020114 | 0.0020161 | 0.0019544 | 0.0018858 | 0.0018122 | 0.0017498 | 0.0016923 | 0.0016278 | 0.0015774 |  | 0.75 | 0.00057388 | 0.0017623 | 0.0020114 | 0.0020161 | 0.0019544 | 0.0018858 | 0.0018122 | 0.0017498 | 0.0016923 | 0.0016278 | 0.0015774
| 0.8 | 0.00053996 | 0.0017689 | 0.001996 | 0.001987 | 0.0019226 | 0.0018433 | 0.0017702 | 0.0017062 | 0.00164 | 0.0015883 | 0.0015435 |  | 0.8 | 0.00053996 | 0.0017689 | 0.001996 | 0.001987 | 0.0019226 | 0.0018433 | 0.0017702 | 0.0017062 | 0.00164 | 0.0015883 | 0.0015435
| 0.85 | 0.0005039 | 0.0017667 | 0.0019861 | 0.0019591 | 0.0018895 | 0.0018014 | 0.0017274 | 0.0016727 | 0.0015941 | 0.0015498 | 0.0015058 |  | 0.85 | 0.0005039 | 0.0017667 | 0.0019861 | 0.0019591 | 0.0018895 | 0.0018014 | 0.0017274 | 0.0016727 | 0.0015941 | 0.0015498 | 0.0015058
| 0.9 | 0.0004779 | 0.0017696 | 0.0019648 | 0.0019248 | 0.0018457 | 0.0017687 | 0.0016981 | 0.0016282 | 0.0015716 | 0.0015156 | 0.0014686 |  | 0.9 | 0.0004779 | 0.0017696 | 0.0019648 | 0.0019248 | 0.0018457 | 0.0017687 | 0.0016981 | 0.0016282 | 0.0015716 | 0.0015156 | 0.0014686
| 0.95 | 0.00046368 | 0.001778 | 0.0019449 | 0.0019057 | 0.0018158 | 0.0017327 | 0.0016551 | 0.0015884 | 0.0015379 | 0.0014852 | 0.0014318 |  | 0.95 | 0.00046368 | 0.001778 | 0.0019449 | 0.0019057 | 0.0018158 | 0.0017327 | 0.0016551 | 0.0015884 | 0.0015379 | 0.0014852 | 0.0014318
| 1 | 0.00042599 | 0.0017713 | 0.0019247 | 0.0018758 | 0.0017778 | 0.0016906 | 0.0016229 | 0.001558 | 0.0015019 | 0.0014511 | 0.0014062 |  | 1 | 0.00042599 | 0.0017713 | 0.0019247 | 0.0018758 | 0.0017778 | 0.0016906 | 0.0016229 | 0.001558 | 0.0015019 | 0.0014511 | 0.0014062
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | [12 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 0 to 1
| 0.05 | 1.4332 | 1.6302 | 1.7873 | 1.9175 | 2.0252 | 2.1148 | 2.1927 | 2.2462 | 2.2994 | 2.3448 | 2.3831 |  | 0.05 | 1.4332 | 1.6302 | 1.7873 | 1.9175 | 2.0252 | 2.1148 | 2.1927 | 2.2462 | 2.2994 | 2.3448 | 2.3831
| 0.1 | 1.448 | 1.9044 | 2.2436 | 2.5044 | 2.709 | 2.8708 | 3.0073 | 3.0975 | 3.1829 | 3.265 | 3.3082 |  | 0.1 | 1.448 | 1.9044 | 2.2436 | 2.5044 | 2.709 | 2.8708 | 3.0073 | 3.0975 | 3.1829 | 3.265 | 3.3082
| 0.15 | 1.3967 | 2.1059 | 2.6167 | 2.9814 | 3.2791 | 3.5115 | 3.6782 | 3.7897 | 3.9006 | 3.9847 | 4.0517 |  | 0.15 | 1.3967 | 2.1059 | 2.6167 | 2.9814 | 3.2791 | 3.5115 | 3.6782 | 3.7897 | 3.9006 | 3.9847 | 4.0517
| 0.2 | 1.3504 | 2.2883 | 2.9287 | 3.4014 | 3.7398 | 4.0278 | 4.2063 | 4.3899 | 4.5149 | 4.612 | 4.6858 |  | 0.2 | 1.3504 | 2.2883 | 2.9287 | 3.4014 | 3.7398 | 4.0278 | 4.2063 | 4.3899 | 4.5149 | 4.612 | 4.6858
| 0.25 | 1.3039 | 2.4557 | 3.2243 | 3.7867 | 4.2004 | 4.5064 | 4.7343 | 4.9137 | 5.0564 | 5.1633 | 5.2856 |  | 0.25 | 1.3039 | 2.4557 | 3.2243 | 3.7867 | 4.2004 | 4.5064 | 4.7343 | 4.9137 | 5.0564 | 5.1633 | 5.2856
| 0.3 | 1.2666 | 2.6104 | 3.5357 | 4.1372 | 4.5965 | 4.9399 | 5.1865 | 5.3869 | 5.4441 | 5.647 | 5.7315 |  | 0.3 | 1.2666 | 2.6104 | 3.5357 | 4.1372 | 4.5965 | 4.9399 | 5.1865 | 5.3869 | 5.4441 | 5.647 | 5.7315
| 0.35 | 1.2445 | 2.8021 | 3.8645 | 4.4615 | 4.9607 | 5.3214 | 5.5884 | 5.8201 | 5.98 | 6.0939 | 6.1952 |  | 0.35 | 1.2445 | 2.8021 | 3.8645 | 4.4615 | 4.9607 | 5.3214 | 5.5884 | 5.8201 | 5.98 | 6.0939 | 6.1952
| 0.4 | 1.2194 | 2.927 | 3.968 | 4.7963 | 5.2966 | 5.6923 | 5.9857 | 6.2139 | 6.377 | 6.5173 | 6.6238 |  | 0.4 | 1.2194 | 2.927 | 3.968 | 4.7963 | 5.2966 | 5.6923 | 5.9857 | 6.2139 | 6.377 | 6.5173 | 6.6238
| 0.45 | 1.1996 | 3.0787 | 4.1359 | 5.0367 | 5.6093 | 6.0298 | 6.3375 | 6.5889 | 6.7685 | 6.9056 | 7.0098 |  | 0.45 | 1.1996 | 3.0787 | 4.1359 | 5.0367 | 5.6093 | 6.0298 | 6.3375 | 6.5889 | 6.7685 | 6.9056 | 7.0098
| 0.5 | 1.1795 | 3.2011 | 4.4439 | 5.2755 | 5.8871 | 6.3493 | 6.6814 | 6.9371 | 7.1251 | 7.2779 | 7.393 |  | 0.5 | 1.1795 | 3.2011 | 4.4439 | 5.2755 | 5.8871 | 6.3493 | 6.6814 | 6.9371 | 7.1251 | 7.2779 | 7.393
| 0.55 | 1.1732 | 3.3682 | 4.6613 | 5.4744 | 6.1802 | 6.6491 | 7.0042 | 7.2712 | 7.4764 | 7.6236 | 7.7463 |  | 0.55 | 1.1732 | 3.3682 | 4.6613 | 5.4744 | 6.1802 | 6.6491 | 7.0042 | 7.2712 | 7.4764 | 7.6236 | 7.7463
| 0.6 | 1.1594 | 3.4877 | 4.856 | 5.7905 | 6.4364 | 6.9375 | 7.3065 | 7.5863 | 7.8009 | 7.9674 | 8.0881 |  | 0.6 | 1.1594 | 3.4877 | 4.856 | 5.7905 | 6.4364 | 6.9375 | 7.3065 | 7.5863 | 7.8009 | 7.9674 | 8.0881
| 0.65 | 1.1475 | 3.6072 | 5.0499 | 6.0095 | 6.6986 | 7.2109 | 7.5932 | 7.8828 | 8.1164 | 8.2833 | 8.4177 |  | 0.65 | 1.1475 | 3.6072 | 5.0499 | 6.0095 | 6.6986 | 7.2109 | 7.5932 | 7.8828 | 8.1164 | 8.2833 | 8.4177
| 0.7 | 1.1441 | 3.6572 | 5.2274 | 6.2271 | 6.9466 | 7.4778 | 7.8777 | 8.1793 | 8.4247 | 8.597 | 8.7251 |  | 0.7 | 1.1441 | 3.6572 | 5.2274 | 6.2271 | 6.9466 | 7.4778 | 7.8777 | 8.1793 | 8.4247 | 8.597 | 8.7251
| 0.75 | 1.1349 | 3.8509 | 5.3933 | 6.4374 | 7.1761 | 7.731 | 8.1496 | 8.4612 | 8.7157 | 8.8938 | 9.0305 |  | 0.75 | 1.1349 | 3.8509 | 5.3933 | 6.4374 | 7.1761 | 7.731 | 8.1496 | 8.4612 | 8.7157 | 8.8938 | 9.0305
| 0.8 | 1.1259 | 3.9688 | 5.5786 | 6.6287 | 7.4066 | 7.9799 | 8.4076 | 8.7345 | 8.9857 | 9.18 | 9.3316 |  | 0.8 | 1.1259 | 3.9688 | 5.5786 | 6.6287 | 7.4066 | 7.9799 | 8.4076 | 8.7345 | 8.9857 | 9.18 | 9.3316
| 0.85 | 1.1258 | 4.0905 | 5.7406 | 6.8317 | 7.6234 | 8.2141 | 8.6583 | 9.0024 | 9.2584 | 9.4634 | 9.6178 |  | 0.85 | 1.1258 | 4.0905 | 5.7406 | 6.8317 | 7.6234 | 8.2141 | 8.6583 | 9.0024 | 9.2584 | 9.4634 | 9.6178
| 0.9 | 1.1186 | 4.2005 | 5.8902 | 7.0147 | 7.8384 | 8.4476 | 8.909 | 9.2627 | 9.5249 | 9.7334 | 9.8899 |  | 0.9 | 1.1186 | 4.2005 | 5.8902 | 7.0147 | 7.8384 | 8.4476 | 8.909 | 9.2627 | 9.5249 | 9.7334 | 9.8899
| 0.95 | 1.111 | 4.2812 | 6.0443 | 7.1966 | 8.0385 | 8.6698 | 9.1516 | 9.5101 | 9.7848 | 9.9987 | 10.1671 |  | 0.95 | 1.111 | 4.2812 | 6.0443 | 7.1966 | 8.0385 | 8.6698 | 9.1516 | 9.5101 | 9.7848 | 9.9987 | 10.1671
| 1 | 1.1055 | 4.4105 | 6.1909 | 7.3787 | 8.2356 | 8.8923 | 9.384 | 9.7508 | 10.0399 | 10.257 | 10.4291 |  | 1 | 1.1055 | 4.4105 | 6.1909 | 7.3787 | 8.2356 | 8.8923 | 9.384 | 9.7508 | 10.0399 | 10.257 | 10.4291
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0028631 | 0.0044895 | 0.0071654 | 0.0095546 | 0.011494 | 0.014053 | 0.014042 | 0.016006 | 0.018254 | 0.019194 | 0.021049 |  | 0.05 | 0.0028631 | 0.0044895 | 0.0071654 | 0.0095546 | 0.011494 | 0.014053 | 0.014042 | 0.016006 | 0.018254 | 0.019194 | 0.021049
| 0.1 | 0.0078716 | 0.012915 | 0.017927 | 0.022702 | 0.025513 | 0.029139 | 0.029061 | 0.034888 | 0.035522 | 0.042832 | 0.044057 |  | 0.1 | 0.0078716 | 0.012915 | 0.017927 | 0.022702 | 0.025513 | 0.029139 | 0.029061 | 0.034888 | 0.035522 | 0.042832 | 0.044057
| 0.15 | 0.0043909 | 0.016493 | 0.025215 | 0.030257 | 0.039494 | 0.04037 | 0.044113 | 0.047662 | 0.053761 | 0.056079 | 0.058403 |  | 0.15 | 0.0043909 | 0.016493 | 0.025215 | 0.030257 | 0.039494 | 0.04037 | 0.044113 | 0.047662 | 0.053761 | 0.056079 | 0.058403
| 0.2 | 0.0026229 | 0.01958 | 0.031389 | 0.039194 | 0.050924 | 0.052439 | 0.055794 | 0.060436 | 0.065165 | 0.067949 | 0.068772 |  | 0.2 | 0.0026229 | 0.01958 | 0.031389 | 0.039194 | 0.050924 | 0.052439 | 0.055794 | 0.060436 | 0.065165 | 0.067949 | 0.068772
| 0.25 | -0.00068726 | 0.022997 | 0.037563 | 0.052217 | 0.062355 | 0.064024 | 0.067475 | 0.07321 | 0.07657 | 0.07982 | 0.087815 |  | 0.25 | -0.00068726 | 0.022997 | 0.037563 | 0.052217 | 0.062355 | 0.064024 | 0.067475 | 0.07321 | 0.07657 | 0.07982 | 0.087815
| 0.3 | -0.0042262 | 0.02514 | 0.043737 | 0.060543 | 0.073785 | 0.07561 | 0.079156 | 0.085983 | 0.087975 | 0.095 | 0.097507 |  | 0.3 | -0.0042262 | 0.02514 | 0.043737 | 0.060543 | 0.073785 | 0.07561 | 0.079156 | 0.085983 | 0.087975 | 0.095 | 0.097507
| 0.35 | -0.0065501 | 0.027767 | 0.04991 | 0.068869 | 0.085215 | 0.087195 | 0.090837 | 0.098757 | 0.099379 | 0.10301 | 0.11196 |  | 0.35 | -0.0065501 | 0.027767 | 0.04991 | 0.068869 | 0.085215 | 0.087195 | 0.090837 | 0.098757 | 0.099379 | 0.10301 | 0.11196
| 0.4 | -0.0090186 | 0.03113 | 0.056084 | 0.077195 | 0.094265 | 0.09878 | 0.10252 | 0.11019 | 0.11078 | 0.11586 | 0.11808 |  | 0.4 | -0.0090186 | 0.03113 | 0.056084 | 0.077195 | 0.094265 | 0.09878 | 0.10252 | 0.11019 | 0.11078 | 0.11586 | 0.11808
| 0.45 | -0.011253 | 0.034493 | 0.062258 | 0.08552 | 0.099951 | 0.10854 | 0.11184 | 0.11702 | 0.11892 | 0.12303 | 0.12388 |  | 0.45 | -0.011253 | 0.034493 | 0.062258 | 0.08552 | 0.099951 | 0.10854 | 0.11184 | 0.11702 | 0.11892 | 0.12303 | 0.12388
| 0.5 | -0.011269 | 0.037855 | 0.069043 | 0.093846 | 0.10725 | 0.11511 | 0.12027 | 0.12472 | 0.12667 | 0.131 | 0.13316 |  | 0.5 | -0.011269 | 0.037855 | 0.069043 | 0.093846 | 0.10725 | 0.11511 | 0.12027 | 0.12472 | 0.12667 | 0.131 | 0.13316
| 0.55 | -0.014043 | 0.041218 | 0.075828 | 0.10023 | 0.11309 | 0.1211 | 0.12611 | 0.13133 | 0.13452 | 0.13701 | 0.14402 |  | 0.55 | -0.014043 | 0.041218 | 0.075828 | 0.10023 | 0.11309 | 0.1211 | 0.12611 | 0.13133 | 0.13452 | 0.13701 | 0.14402
| 0.6 | -0.015065 | 0.044581 | 0.082613 | 0.10496 | 0.11834 | 0.1271 | 0.13331 | 0.13695 | 0.14324 | 0.14552 | 0.14868 |  | 0.6 | -0.015065 | 0.044581 | 0.082613 | 0.10496 | 0.11834 | 0.1271 | 0.13331 | 0.13695 | 0.14324 | 0.14552 | 0.14868
| 0.65 | -0.014658 | 0.047944 | 0.089399 | 0.10957 | 0.12359 | 0.13403 | 0.13917 | 0.14313 | 0.15024 | 0.15314 | 0.15654 |  | 0.65 | -0.014658 | 0.047944 | 0.089399 | 0.10957 | 0.12359 | 0.13403 | 0.13917 | 0.14313 | 0.15024 | 0.15314 | 0.15654
| 0.7 | -0.015353 | 0.047989 | 0.094637 | 0.11659 | 0.12884 | 0.13914 | 0.14626 | 0.15052 | 0.15627 | 0.16065 | 0.1635 |  | 0.7 | -0.015353 | 0.047989 | 0.094637 | 0.11659 | 0.12884 | 0.13914 | 0.14626 | 0.15052 | 0.15627 | 0.16065 | 0.1635
| 0.75 | -0.018331 | 0.054977 | 0.10009 | 0.11919 | 0.13409 | 0.14374 | 0.15154 | 0.15628 | 0.16122 | 0.16643 | 0.16973 |  | 0.75 | -0.018331 | 0.054977 | 0.10009 | 0.11919 | 0.13409 | 0.14374 | 0.15154 | 0.15628 | 0.16122 | 0.16643 | 0.16973
| 0.8 | -0.017702 | 0.060018 | 0.10066 | 0.1227 | 0.13934 | 0.14912 | 0.15629 | 0.16131 | 0.16705 | 0.17089 | 0.17589 |  | 0.8 | -0.017702 | 0.060018 | 0.10066 | 0.1227 | 0.13934 | 0.14912 | 0.15629 | 0.16131 | 0.16705 | 0.17089 | 0.17589
| 0.85 | -0.017681 | 0.062248 | 0.10331 | 0.12785 | 0.14286 | 0.15456 | 0.16223 | 0.16951 | 0.1733 | 0.17813 | 0.18281 |  | 0.85 | -0.017681 | 0.062248 | 0.10331 | 0.12785 | 0.14286 | 0.15456 | 0.16223 | 0.16951 | 0.1733 | 0.17813 | 0.18281
| 0.9 | -0.018461 | 0.063757 | 0.10856 | 0.13137 | 0.14614 | 0.15909 | 0.16858 | 0.17347 | 0.17863 | 0.18333 | 0.18729 |  | 0.9 | -0.018461 | 0.063757 | 0.10856 | 0.13137 | 0.14614 | 0.15909 | 0.16858 | 0.17347 | 0.17863 | 0.18333 | 0.18729
| 0.95 | -0.018625 | 0.068737 | 0.10743 | 0.1349 | 0.15065 | 0.1619 | 0.17231 | 0.1796 | 0.18684 | 0.19158 | 0.19274 |  | 0.95 | -0.018625 | 0.068737 | 0.10743 | 0.1349 | 0.15065 | 0.1619 | 0.17231 | 0.1796 | 0.18684 | 0.19158 | 0.19274
| 1 | -0.019752 | 0.073718 | 0.11634 | 0.13712 | 0.15426 | 0.16787 | 0.17637 | 0.18505 | 0.19053 | 0.19465 | 0.19962 |  | 1 | -0.019752 | 0.073718 | 0.11634 | 0.13712 | 0.15426 | 0.16787 | 0.17637 | 0.18505 | 0.19053 | 0.19465 | 0.19962
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.001435 | -0.0035249 | -0.0050363 | -0.006189 | -0.0070237 | -0.0076683 | -0.0083587 | -0.0087523 | -0.0090917 | -0.0092115 | -0.0094223 |  | 0.05 | -0.001435 | -0.0035249 | -0.0050363 | -0.006189 | -0.0070237 | -0.0076683 | -0.0083587 | -0.0087523 | -0.0090917 | -0.0092115 | -0.0094223
| 0.1 | -8.4615e-05 | -0.0044703 | -0.0073308 | -0.0093827 | -0.010847 | -0.011686 | -0.013042 | -0.013 | -0.014075 | -0.014454 | -0.014458 |  | 0.1 | -8.4615e-05 | -0.0044703 | -0.0073308 | -0.0093827 | -0.010847 | -0.011686 | -0.013042 | -0.013 | -0.014075 | -0.014454 | -0.014458
| 0.15 | 0.00053958 | -0.0054237 | -0.0095808 | -0.012316 | -0.013575 | -0.014146 | -0.01586 | -0.017606 | -0.016188 | -0.017779 | -0.018161 |  | 0.15 | 0.00053958 | -0.0054237 | -0.0095808 | -0.012316 | -0.013575 | -0.014146 | -0.01586 | -0.017606 | -0.016188 | -0.017779 | -0.018161
| 0.2 | 0.00094464 | -0.006517 | -0.012009 | -0.013821 | -0.016541 | -0.016606 | -0.018678 | -0.019965 | -0.019118 | -0.019839 | -0.021736 |  | 0.2 | 0.00094464 | -0.006517 | -0.012009 | -0.013821 | -0.016541 | -0.016606 | -0.018678 | -0.019965 | -0.019118 | -0.019839 | -0.021736
| 0.25 | 0.00065823 | -0.0075648 | -0.012859 | -0.015326 | -0.018235 | -0.019066 | -0.020679 | -0.022323 | -0.022863 | -0.0219 | -0.023432 |  | 0.25 | 0.00065823 | -0.0075648 | -0.012859 | -0.015326 | -0.018235 | -0.019066 | -0.020679 | -0.022323 | -0.022863 | -0.0219 | -0.023432
| 0.3 | 0.00069724 | -0.0090191 | -0.01371 | -0.017677 | -0.018751 | -0.021237 | -0.022126 | -0.023128 | -0.023865 | -0.02418 | -0.025128 |  | 0.3 | 0.00069724 | -0.0090191 | -0.01371 | -0.017677 | -0.018751 | -0.021237 | -0.022126 | -0.023128 | -0.023865 | -0.02418 | -0.025128
| 0.35 | 0.00034797 | -0.0090663 | -0.01456 | -0.018511 | -0.021241 | -0.022487 | -0.023791 | -0.024675 | -0.025528 | -0.026417 | -0.026824 |  | 0.35 | 0.00034797 | -0.0090663 | -0.01456 | -0.018511 | -0.021241 | -0.022487 | -0.023791 | -0.024675 | -0.025528 | -0.026417 | -0.026824
| 0.4 | 0.00046628 | -0.010581 | -0.015411 | -0.019687 | -0.022025 | -0.02379 | -0.025456 | -0.026357 | -0.027001 | -0.028027 | -0.028522 |  | 0.4 | 0.00046628 | -0.010581 | -0.015411 | -0.019687 | -0.022025 | -0.02379 | -0.025456 | -0.026357 | -0.027001 | -0.028027 | -0.028522
| 0.45 | 0.00038893 | -0.011241 | -0.016261 | -0.021335 | -0.023541 | -0.025124 | -0.026898 | -0.027826 | -0.028965 | -0.029638 | -0.029837 |  | 0.45 | 0.00038893 | -0.011241 | -0.016261 | -0.021335 | -0.023541 | -0.025124 | -0.026898 | -0.027826 | -0.028965 | -0.029638 | -0.029837
| 0.5 | 7.1138e-05 | -0.01182 | -0.017112 | -0.022096 | -0.024531 | -0.026351 | -0.028214 | -0.0291 | -0.030502 | -0.031093 | -0.031608 |  | 0.5 | 7.1138e-05 | -0.01182 | -0.017112 | -0.022096 | -0.024531 | -0.026351 | -0.028214 | -0.0291 | -0.030502 | -0.031093 | -0.031608
| 0.55 | 3.4691e-06 | -0.012556 | -0.017962 | -0.023059 | -0.025775 | -0.027507 | -0.029712 | -0.030682 | -0.031874 | -0.032585 | -0.033293 |  | 0.55 | 3.4691e-06 | -0.012556 | -0.017962 | -0.023059 | -0.025775 | -0.027507 | -0.029712 | -0.030682 | -0.031874 | -0.032585 | -0.033293
| 0.6 | 0.00022568 | -0.013439 | -0.018813 | -0.024218 | -0.026712 | -0.028799 | -0.030669 | -0.031875 | -0.033338 | -0.033622 | -0.034774 |  | 0.6 | 0.00022568 | -0.013439 | -0.018813 | -0.024218 | -0.026712 | -0.028799 | -0.030669 | -0.031875 | -0.033338 | -0.033622 | -0.034774
| 0.65 | -8.7082e-05 | -0.014322 | -0.019663 | -0.024789 | -0.027856 | -0.029908 | -0.032165 | -0.033354 | -0.034529 | -0.035537 | -0.036099 |  | 0.65 | -8.7082e-05 | -0.014322 | -0.019663 | -0.024789 | -0.027856 | -0.029908 | -0.032165 | -0.033354 | -0.034529 | -0.035537 | -0.036099
| 0.7 | -0.00013008 | -0.014102 | -0.020514 | -0.025734 | -0.028584 | -0.030905 | -0.033315 | -0.034511 | -0.036011 | -0.036807 | -0.037377 |  | 0.7 | -0.00013008 | -0.014102 | -0.020514 | -0.025734 | -0.028584 | -0.030905 | -0.033315 | -0.034511 | -0.036011 | -0.036807 | -0.037377
| 0.75 | -0.00014363 | -0.015161 | -0.021364 | -0.026204 | -0.029519 | -0.032377 | -0.034446 | -0.036148 | -0.037009 | -0.038418 | -0.039032 |  | 0.75 | -0.00014363 | -0.015161 | -0.021364 | -0.026204 | -0.029519 | -0.032377 | -0.034446 | -0.036148 | -0.037009 | -0.038418 | -0.039032
| 0.8 | -0.00022051 | -0.016059 | -0.022215 | -0.02728 | -0.030564 | -0.033394 | -0.035601 | -0.037126 | -0.038275 | -0.039292 | -0.039905 |  | 0.8 | -0.00022051 | -0.016059 | -0.022215 | -0.02728 | -0.030564 | -0.033394 | -0.035601 | -0.037126 | -0.038275 | -0.039292 | -0.039905
| 0.85 | -0.00020386 | -0.016177 | -0.023065 | -0.027855 | -0.031482 | -0.034449 | -0.036478 | -0.038131 | -0.039748 | -0.04049 | -0.041197 |  | 0.85 | -0.00020386 | -0.016177 | -0.023065 | -0.027855 | -0.031482 | -0.034449 | -0.036478 | -0.038131 | -0.039748 | -0.04049 | -0.041197
| 0.9 | -0.0002619 | -0.017788 | -0.023938 | -0.028533 | -0.032809 | -0.035465 | -0.037328 | -0.039411 | -0.040782 | -0.041707 | -0.042516 |  | 0.9 | -0.0002619 | -0.017788 | -0.023938 | -0.028533 | -0.032809 | -0.035465 | -0.037328 | -0.039411 | -0.040782 | -0.041707 | -0.042516
| 0.95 | -0.00044485 | -0.017952 | -0.024016 | -0.02907 | -0.033299 | -0.036297 | -0.038706 | -0.040657 | -0.041916 | -0.04304 | -0.043672 |  | 0.95 | -0.00044485 | -0.017952 | -0.024016 | -0.02907 | -0.033299 | -0.036297 | -0.038706 | -0.040657 | -0.041916 | -0.04304 | -0.043672
| 1 | -0.00023002 | -0.018189 | -0.024788 | -0.029926 | -0.034356 | -0.037492 | -0.039635 | -0.04158 | -0.043138 | -0.043988 | -0.044827 |  | 1 | -0.00023002 | -0.018189 | -0.024788 | -0.029926 | -0.034356 | -0.037492 | -0.039635 | -0.04158 | -0.043138 | -0.043988 | -0.044827
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS5_LS< (hidden)
If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0236 | 1.0379 | 1.049 | 1.0569 | 1.0619 | 1.0643 | 1.0646 | 1.0632 | 1.0605 | 1.0567 | 1.052
| 0.1 | 1.0338 | 1.0676 | 1.0939 | 1.1108 | 1.12 | 1.1233 | 1.1225 | 1.1186 | 1.1125 | 1.1049 | 1.0961
| 0.15 | 1.0333 | 1.0708 | 1.1104 | 1.1337 | 1.1453 | 1.1489 | 1.1472 | 1.1418 | 1.134 | 1.1245 | 1.1138
| 0.2 | 1.0217 | 1.0728 | 1.1165 | 1.1446 | 1.158 | 1.162 | 1.1599 | 1.1539 | 1.1452 | 1.1348 | 1.1232
| 0.25 | 1.0045 | 1.0707 | 1.1183 | 1.1503 | 1.1651 | 1.1696 | 1.1675 | 1.1613 | 1.1523 | 1.1415 | 1.1295
| 0.3 | 0.98547 | 1.0665 | 1.1199 | 1.1532 | 1.1694 | 1.1746 | 1.1728 | 1.1667 | 1.1576 | 1.1467 | 1.1344
| 0.35 | 0.96623 | 1.0616 | 1.1213 | 1.1548 | 1.1724 | 1.1784 | 1.1771 | 1.1711 | 1.1621 | 1.1509 | 1.1385
| 0.4 | 0.9477 | 1.0565 | 1.1217 | 1.1557 | 1.1748 | 1.1816 | 1.1808 | 1.1749 | 1.1658 | 1.1545 | 1.1418
| 0.45 | 0.93031 | 1.0516 | 1.1215 | 1.1569 | 1.1769 | 1.1845 | 1.184 | 1.1781 | 1.1689 | 1.1574 | 1.1445
| 0.5 | 0.91419 | 1.0471 | 1.1208 | 1.1578 | 1.1789 | 1.1871 | 1.1867 | 1.1809 | 1.1715 | 1.1599 | 1.1468
| 0.55 | 0.89938 | 1.0428 | 1.1198 | 1.1584 | 1.1807 | 1.1894 | 1.1891 | 1.1832 | 1.1737 | 1.1619 | 1.1486
| 0.6 | 0.88582 | 1.039 | 1.1188 | 1.1588 | 1.1824 | 1.1914 | 1.1911 | 1.1851 | 1.1755 | 1.1636 | 1.1502
| 0.65 | 0.87342 | 1.0355 | 1.1176 | 1.1593 | 1.1839 | 1.1931 | 1.1929 | 1.1868 | 1.1771 | 1.1651 | 1.1516
| 0.7 | 0.86208 | 1.0322 | 1.1165 | 1.1601 | 1.1853 | 1.1946 | 1.1943 | 1.1882 | 1.1784 | 1.1664 | 1.1528
| 0.75 | 0.85171 | 1.0292 | 1.1154 | 1.1608 | 1.1865 | 1.1959 | 1.1956 | 1.1895 | 1.1797 | 1.1675 | 1.1539
| 0.8 | 0.84221 | 1.0265 | 1.1144 | 1.1616 | 1.1875 | 1.197 | 1.1968 | 1.1906 | 1.1808 | 1.1686 | 1.1549
| 0.85 | 0.83348 | 1.0239 | 1.1135 | 1.1622 | 1.1885 | 1.198 | 1.1978 | 1.1916 | 1.1818 | 1.1695 | 1.1558
| 0.9 | 0.82546 | 1.0215 | 1.1126 | 1.1628 | 1.1893 | 1.1989 | 1.1987 | 1.1926 | 1.1827 | 1.1704 | 1.1567
| 0.95 | 0.81806 | 1.0193 | 1.1119 | 1.1634 | 1.19 | 1.1997 | 1.1996 | 1.1935 | 1.1835 | 1.1712 | 1.1574
| 1 | 0.81122 | 1.0172 | 1.1113 | 1.1638 | 1.1906 | 1.2004 | 1.2004 | 1.1943 | 1.1843 | 1.172 | 1.1581
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| 0.05 | 1.338 | 1.3118 | 1.2858 | 1.2602 | 1.2352 | 1.2112 | 1.1882 | 1.1669 | 1.1456 | 1.1255 | 1.1063
| 0.1 | 1.1924 | 1.1532 | 1.1169 | 1.0832 | 1.0517 | 1.0224 | 0.99528 | 0.96949 | 0.94558 | 0.923 | 0.90196
| 0.15 | 1.1048 | 1.0529 | 1.0104 | 0.97298 | 0.93888 | 0.90788 | 0.87955 | 0.85268 | 0.82854 | 0.80572 | 0.78492
| 0.2 | 1.0472 | 0.98183 | 0.93542 | 0.89572 | 0.8605 | 0.82805 | 0.79926 | 0.77245 | 0.74801 | 0.72562 | 0.70504
| 0.25 | 1.0076 | 0.92854 | 0.87857 | 0.8373 | 0.80072 | 0.76729 | 0.73821 | 0.7114 | 0.68751 | 0.66566 | 0.64611
| 0.3 | 0.97887 | 0.88594 | 0.83321 | 0.7902 | 0.7521 | 0.71863 | 0.68902 | 0.66284 | 0.63939 | 0.61835 | 0.59916
| 0.35 | 0.9564 | 0.85093 | 0.79566 | 0.75056 | 0.71144 | 0.67781 | 0.64859 | 0.62317 | 0.5999 | 0.57983 | 0.5616
| 0.4 | 0.93943 | 0.82139 | 0.76346 | 0.71633 | 0.67685 | 0.64318 | 0.61464 | 0.58927 | 0.56721 | 0.5475 | 0.52993
| 0.45 | 0.92576 | 0.7956 | 0.73514 | 0.68625 | 0.64668 | 0.61328 | 0.58523 | 0.56086 | 0.53943 | 0.52013 | 0.50326
| 0.5 | 0.91472 | 0.77324 | 0.70967 | 0.65987 | 0.61991 | 0.58729 | 0.55974 | 0.53575 | 0.51515 | 0.49643 | 0.48024
| 0.55 | 0.90466 | 0.75317 | 0.68649 | 0.6363 | 0.59656 | 0.56404 | 0.53743 | 0.51388 | 0.49395 | 0.4758 | 0.46001
| 0.6 | 0.89687 | 0.73525 | 0.66564 | 0.61484 | 0.57537 | 0.54365 | 0.51734 | 0.49458 | 0.47506 | 0.45783 | 0.44209
| 0.65 | 0.89021 | 0.71849 | 0.64676 | 0.59544 | 0.55615 | 0.52499 | 0.4992 | 0.47723 | 0.45825 | 0.44131 | 0.42642
| 0.7 | 0.88391 | 0.70327 | 0.62927 | 0.57768 | 0.53897 | 0.50853 | 0.4832 | 0.46163 | 0.44314 | 0.42664 | 0.41199
| 0.75 | 0.87877 | 0.68916 | 0.61321 | 0.56139 | 0.52339 | 0.49323 | 0.46858 | 0.44741 | 0.42946 | 0.4133 | 0.3991
| 0.8 | 0.87436 | 0.67587 | 0.59782 | 0.54638 | 0.50898 | 0.47939 | 0.45497 | 0.43458 | 0.41683 | 0.40115 | 0.38752
| 0.85 | 0.86986 | 0.66328 | 0.58421 | 0.53274 | 0.49555 | 0.46643 | 0.44255 | 0.42276 | 0.40527 | 0.39036 | 0.37696
| 0.9 | 0.86658 | 0.65157 | 0.57124 | 0.51975 | 0.48325 | 0.45472 | 0.43149 | 0.41192 | 0.39472 | 0.38006 | 0.36693
| 0.95 | 0.86334 | 0.64046 | 0.55894 | 0.50783 | 0.47162 | 0.44361 | 0.42097 | 0.40165 | 0.38495 | 0.37054 | 0.3579
| 1 | 0.86054 | 0.62995 | 0.54761 | 0.49684 | 0.46078 | 0.43355 | 0.41119 | 0.39213 | 0.37592 | 0.36177 | 0.34928
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0069409 | 0.0077604 | 0.0084833 | 0.0091355 | 0.0096876 | 0.010177 | 0.010732 | 0.011063 | 0.011382 | 0.011607 | 0.011825
| 0.1 | 0.0078005 | 0.00903 | 0.0098351 | 0.010484 | 0.010956 | 0.011318 | 0.011744 | 0.011957 | 0.012022 | 0.012137 | 0.012221
| 0.15 | 0.0072742 | 0.0090248 | 0.0099973 | 0.010706 | 0.011249 | 0.011639 | 0.01199 | 0.012124 | 0.012088 | 0.012098 | 0.012051
| 0.2 | 0.0061592 | 0.0087911 | 0.010065 | 0.01092 | 0.011523 | 0.011861 | 0.012041 | 0.012011 | 0.01192 | 0.011892 | 0.011752
| 0.25 | 0.0052603 | 0.0085994 | 0.010169 | 0.01117 | 0.01168 | 0.011887 | 0.011909 | 0.01175 | 0.011653 | 0.011521 | 0.011314
| 0.3 | 0.0044711 | 0.0084851 | 0.010309 | 0.011338 | 0.011672 | 0.011702 | 0.011659 | 0.011452 | 0.011214 | 0.011068 | 0.010802
| 0.35 | 0.0038917 | 0.0084003 | 0.010524 | 0.011392 | 0.011563 | 0.011453 | 0.01133 | 0.011075 | 0.010883 | 0.010611 | 0.010362
| 0.4 | 0.0033594 | 0.0083857 | 0.010667 | 0.011337 | 0.011373 | 0.011213 | 0.011053 | 0.010705 | 0.010481 | 0.01021 | 0.0099171
| 0.45 | 0.0028737 | 0.0085365 | 0.010698 | 0.011237 | 0.011192 | 0.010942 | 0.010639 | 0.010351 | 0.010042 | 0.0097356 | 0.0095192
| 0.5 | 0.0023812 | 0.0086256 | 0.010679 | 0.011107 | 0.01094 | 0.010611 | 0.010324 | 0.009994 | 0.0097229 | 0.0094796 | 0.0091613
| 0.55 | 0.002199 | 0.008745 | 0.010683 | 0.010922 | 0.010711 | 0.010377 | 0.010005 | 0.0097525 | 0.0093481 | 0.0091312 | 0.0088646
| 0.6 | 0.0019184 | 0.0087903 | 0.010641 | 0.010785 | 0.01046 | 0.010106 | 0.0097017 | 0.009409 | 0.0090802 | 0.0088523 | 0.0085505
| 0.65 | 0.0015446 | 0.0089405 | 0.010583 | 0.010555 | 0.010183 | 0.0098152 | 0.0094284 | 0.0091245 | 0.0088093 | 0.0085942 | 0.0083332
| 0.7 | 0.0013403 | 0.0090279 | 0.010497 | 0.01033 | 0.0099984 | 0.0095564 | 0.0092173 | 0.0088788 | 0.0086346 | 0.0083014 | 0.0080956
| 0.75 | 0.0012773 | 0.0091103 | 0.010317 | 0.010147 | 0.0097544 | 0.0093123 | 0.0089626 | 0.0086487 | 0.0083724 | 0.0081356 | 0.0078886
| 0.8 | 0.0010022 | 0.0091201 | 0.010247 | 0.0099688 | 0.0095564 | 0.0091164 | 0.0087362 | 0.0083856 | 0.0081458 | 0.0078588 | 0.007668
| 0.85 | 0.00083829 | 0.0091217 | 0.010214 | 0.0098095 | 0.0093625 | 0.0088793 | 0.0085379 | 0.0082266 | 0.0079659 | 0.0076894 | 0.0075047
| 0.9 | 0.00069909 | 0.009227 | 0.010062 | 0.0096429 | 0.0091194 | 0.008728 | 0.0083773 | 0.0080059 | 0.0077586 | 0.0075085 | 0.0072957
| 0.95 | 0.00062337 | 0.0092012 | 0.0098914 | 0.0094825 | 0.0089387 | 0.008523 | 0.0081774 | 0.0078521 | 0.0076054 | 0.0073763 | 0.0071737
| 1 | 0.00051999 | 0.0092405 | 0.0098139 | 0.0092723 | 0.0087843 | 0.0083511 | 0.0079918 | 0.0076929 | 0.0074608 | 0.007194 | 0.006999
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0015898 | 0.0017159 | 0.0018428 | 0.001954 | 0.0020553 | 0.0021462 | 0.0022389 | 0.0023103 | 0.0023644 | 0.0024085 | 0.0024517
| 0.1 | 0.0018446 | 0.0020661 | 0.0022032 | 0.0022835 | 0.0023536 | 0.0024059 | 0.0024584 | 0.0024813 | 0.0024999 | 0.0025139 | 0.0025096
| 0.15 | 0.0017326 | 0.0020918 | 0.0022388 | 0.002316 | 0.0023541 | 0.0023864 | 0.0024175 | 0.0024311 | 0.0024291 | 0.0024194 | 0.0024115
| 0.2 | 0.0015367 | 0.0020553 | 0.0021962 | 0.0022674 | 0.0023106 | 0.0023407 | 0.0023732 | 0.0023736 | 0.0023593 | 0.0023348 | 0.0023159
| 0.25 | 0.0013772 | 0.0020032 | 0.0021433 | 0.0022316 | 0.0022927 | 0.00231 | 0.0023347 | 0.0023115 | 0.0022856 | 0.0022692 | 0.002235
| 0.3 | 0.0012322 | 0.0019565 | 0.002108 | 0.0022077 | 0.0022781 | 0.0022792 | 0.0022797 | 0.0022412 | 0.0022142 | 0.0021809 | 0.002137
| 0.35 | 0.0011218 | 0.0019083 | 0.0020827 | 0.0022057 | 0.0022476 | 0.0022461 | 0.0022261 | 0.0021892 | 0.0021454 | 0.0021001 | 0.0020627
| 0.4 | 0.0009907 | 0.0018706 | 0.0020734 | 0.0021973 | 0.0022155 | 0.0022057 | 0.002169 | 0.0021179 | 0.0020798 | 0.0020357 | 0.001985
| 0.45 | 0.00090036 | 0.0018411 | 0.0020665 | 0.0021679 | 0.0021841 | 0.0021528 | 0.0021122 | 0.0020607 | 0.0020116 | 0.0019526 | 0.0019076
| 0.5 | 0.00083946 | 0.0018084 | 0.0020636 | 0.0021482 | 0.0021503 | 0.0021064 | 0.0020594 | 0.0020038 | 0.0019483 | 0.0018934 | 0.0018475
| 0.55 | 0.00077059 | 0.0017846 | 0.0020682 | 0.0021301 | 0.002111 | 0.002065 | 0.0020038 | 0.0019447 | 0.0018875 | 0.0018331 | 0.0017866
| 0.6 | 0.00069364 | 0.0017837 | 0.0020468 | 0.0020999 | 0.0020753 | 0.0020106 | 0.0019562 | 0.0018967 | 0.0018322 | 0.0017818 | 0.0017299
| 0.65 | 0.00066017 | 0.0017732 | 0.0020375 | 0.0020734 | 0.0020261 | 0.0019691 | 0.0019012 | 0.0018345 | 0.0017861 | 0.0017242 | 0.001671
| 0.7 | 0.00061588 | 0.001769 | 0.0020276 | 0.0020457 | 0.0019991 | 0.0019282 | 0.00186 | 0.0017953 | 0.0017323 | 0.0016787 | 0.0016269
| 0.75 | 0.00057388 | 0.0017623 | 0.0020114 | 0.0020161 | 0.0019544 | 0.0018858 | 0.0018122 | 0.0017498 | 0.0016923 | 0.0016278 | 0.0015774
| 0.8 | 0.00053996 | 0.0017689 | 0.001996 | 0.001987 | 0.0019226 | 0.0018433 | 0.0017702 | 0.0017062 | 0.00164 | 0.0015883 | 0.0015435
| 0.85 | 0.0005039 | 0.0017667 | 0.0019861 | 0.0019591 | 0.0018895 | 0.0018014 | 0.0017274 | 0.0016727 | 0.0015941 | 0.0015498 | 0.0015058
| 0.9 | 0.0004779 | 0.0017696 | 0.0019648 | 0.0019248 | 0.0018457 | 0.0017687 | 0.0016981 | 0.0016282 | 0.0015716 | 0.0015156 | 0.0014686
| 0.95 | 0.00046368 | 0.001778 | 0.0019449 | 0.0019057 | 0.0018158 | 0.0017327 | 0.0016551 | 0.0015884 | 0.0015379 | 0.0014852 | 0.0014318
| 1 | 0.00042599 | 0.0017713 | 0.0019247 | 0.0018758 | 0.0017778 | 0.0016906 | 0.0016229 | 0.001558 | 0.0015019 | 0.0014511 | 0.0014062
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.4332 | 1.6302 | 1.7873 | 1.9175 | 2.0252 | 2.1148 | 2.1927 | 2.2462 | 2.2994 | 2.3448 | 2.3831
| 0.1 | 1.448 | 1.9044 | 2.2436 | 2.5044 | 2.709 | 2.8708 | 3.0073 | 3.0975 | 3.1829 | 3.265 | 3.3082
| 0.15 | 1.3967 | 2.1059 | 2.6167 | 2.9814 | 3.2791 | 3.5115 | 3.6782 | 3.7897 | 3.9006 | 3.9847 | 4.0517
| 0.2 | 1.3504 | 2.2883 | 2.9287 | 3.4014 | 3.7398 | 4.0278 | 4.2063 | 4.3899 | 4.5149 | 4.612 | 4.6858
| 0.25 | 1.3039 | 2.4557 | 3.2243 | 3.7867 | 4.2004 | 4.5064 | 4.7343 | 4.9137 | 5.0564 | 5.1633 | 5.2856
| 0.3 | 1.2666 | 2.6104 | 3.5357 | 4.1372 | 4.5965 | 4.9399 | 5.1865 | 5.3869 | 5.4441 | 5.647 | 5.7315
| 0.35 | 1.2445 | 2.8021 | 3.8645 | 4.4615 | 4.9607 | 5.3214 | 5.5884 | 5.8201 | 5.98 | 6.0939 | 6.1952
| 0.4 | 1.2194 | 2.927 | 3.968 | 4.7963 | 5.2966 | 5.6923 | 5.9857 | 6.2139 | 6.377 | 6.5173 | 6.6238
| 0.45 | 1.1996 | 3.0787 | 4.1359 | 5.0367 | 5.6093 | 6.0298 | 6.3375 | 6.5889 | 6.7685 | 6.9056 | 7.0098
| 0.5 | 1.1795 | 3.2011 | 4.4439 | 5.2755 | 5.8871 | 6.3493 | 6.6814 | 6.9371 | 7.1251 | 7.2779 | 7.393
| 0.55 | 1.1732 | 3.3682 | 4.6613 | 5.4744 | 6.1802 | 6.6491 | 7.0042 | 7.2712 | 7.4764 | 7.6236 | 7.7463
| 0.6 | 1.1594 | 3.4877 | 4.856 | 5.7905 | 6.4364 | 6.9375 | 7.3065 | 7.5863 | 7.8009 | 7.9674 | 8.0881
| 0.65 | 1.1475 | 3.6072 | 5.0499 | 6.0095 | 6.6986 | 7.2109 | 7.5932 | 7.8828 | 8.1164 | 8.2833 | 8.4177
| 0.7 | 1.1441 | 3.6572 | 5.2274 | 6.2271 | 6.9466 | 7.4778 | 7.8777 | 8.1793 | 8.4247 | 8.597 | 8.7251
| 0.75 | 1.1349 | 3.8509 | 5.3933 | 6.4374 | 7.1761 | 7.731 | 8.1496 | 8.4612 | 8.7157 | 8.8938 | 9.0305
| 0.8 | 1.1259 | 3.9688 | 5.5786 | 6.6287 | 7.4066 | 7.9799 | 8.4076 | 8.7345 | 8.9857 | 9.18 | 9.3316
| 0.85 | 1.1258 | 4.0905 | 5.7406 | 6.8317 | 7.6234 | 8.2141 | 8.6583 | 9.0024 | 9.2584 | 9.4634 | 9.6178
| 0.9 | 1.1186 | 4.2005 | 5.8902 | 7.0147 | 7.8384 | 8.4476 | 8.909 | 9.2627 | 9.5249 | 9.7334 | 9.8899
| 0.95 | 1.111 | 4.2812 | 6.0443 | 7.1966 | 8.0385 | 8.6698 | 9.1516 | 9.5101 | 9.7848 | 9.9987 | 10.1671
| 1 | 1.1055 | 4.4105 | 6.1909 | 7.3787 | 8.2356 | 8.8923 | 9.384 | 9.7508 | 10.0399 | 10.257 | 10.4291
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0028631 | 0.0044895 | 0.0071654 | 0.0095546 | 0.011494 | 0.014053 | 0.014042 | 0.016006 | 0.018254 | 0.019194 | 0.021049
| 0.1 | 0.0078716 | 0.012915 | 0.017927 | 0.022702 | 0.025513 | 0.029139 | 0.029061 | 0.034888 | 0.035522 | 0.042832 | 0.044057
| 0.15 | 0.0043909 | 0.016493 | 0.025215 | 0.030257 | 0.039494 | 0.04037 | 0.044113 | 0.047662 | 0.053761 | 0.056079 | 0.058403
| 0.2 | 0.0026229 | 0.01958 | 0.031389 | 0.039194 | 0.050924 | 0.052439 | 0.055794 | 0.060436 | 0.065165 | 0.067949 | 0.068772
| 0.25 | -0.00068726 | 0.022997 | 0.037563 | 0.052217 | 0.062355 | 0.064024 | 0.067475 | 0.07321 | 0.07657 | 0.07982 | 0.087815
| 0.3 | -0.0042262 | 0.02514 | 0.043737 | 0.060543 | 0.073785 | 0.07561 | 0.079156 | 0.085983 | 0.087975 | 0.095 | 0.097507
| 0.35 | -0.0065501 | 0.027767 | 0.04991 | 0.068869 | 0.085215 | 0.087195 | 0.090837 | 0.098757 | 0.099379 | 0.10301 | 0.11196
| 0.4 | -0.0090186 | 0.03113 | 0.056084 | 0.077195 | 0.094265 | 0.09878 | 0.10252 | 0.11019 | 0.11078 | 0.11586 | 0.11808
| 0.45 | -0.011253 | 0.034493 | 0.062258 | 0.08552 | 0.099951 | 0.10854 | 0.11184 | 0.11702 | 0.11892 | 0.12303 | 0.12388
| 0.5 | -0.011269 | 0.037855 | 0.069043 | 0.093846 | 0.10725 | 0.11511 | 0.12027 | 0.12472 | 0.12667 | 0.131 | 0.13316
| 0.55 | -0.014043 | 0.041218 | 0.075828 | 0.10023 | 0.11309 | 0.1211 | 0.12611 | 0.13133 | 0.13452 | 0.13701 | 0.14402
| 0.6 | -0.015065 | 0.044581 | 0.082613 | 0.10496 | 0.11834 | 0.1271 | 0.13331 | 0.13695 | 0.14324 | 0.14552 | 0.14868
| 0.65 | -0.014658 | 0.047944 | 0.089399 | 0.10957 | 0.12359 | 0.13403 | 0.13917 | 0.14313 | 0.15024 | 0.15314 | 0.15654
| 0.7 | -0.015353 | 0.047989 | 0.094637 | 0.11659 | 0.12884 | 0.13914 | 0.14626 | 0.15052 | 0.15627 | 0.16065 | 0.1635
| 0.75 | -0.018331 | 0.054977 | 0.10009 | 0.11919 | 0.13409 | 0.14374 | 0.15154 | 0.15628 | 0.16122 | 0.16643 | 0.16973
| 0.8 | -0.017702 | 0.060018 | 0.10066 | 0.1227 | 0.13934 | 0.14912 | 0.15629 | 0.16131 | 0.16705 | 0.17089 | 0.17589
| 0.85 | -0.017681 | 0.062248 | 0.10331 | 0.12785 | 0.14286 | 0.15456 | 0.16223 | 0.16951 | 0.1733 | 0.17813 | 0.18281
| 0.9 | -0.018461 | 0.063757 | 0.10856 | 0.13137 | 0.14614 | 0.15909 | 0.16858 | 0.17347 | 0.17863 | 0.18333 | 0.18729
| 0.95 | -0.018625 | 0.068737 | 0.10743 | 0.1349 | 0.15065 | 0.1619 | 0.17231 | 0.1796 | 0.18684 | 0.19158 | 0.19274
| 1 | -0.019752 | 0.073718 | 0.11634 | 0.13712 | 0.15426 | 0.16787 | 0.17637 | 0.18505 | 0.19053 | 0.19465 | 0.19962
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.001435 | -0.0035249 | -0.0050363 | -0.006189 | -0.0070237 | -0.0076683 | -0.0083587 | -0.0087523 | -0.0090917 | -0.0092115 | -0.0094223
| 0.1 | -8.4615e-05 | -0.0044703 | -0.0073308 | -0.0093827 | -0.010847 | -0.011686 | -0.013042 | -0.013 | -0.014075 | -0.014454 | -0.014458
| 0.15 | 0.00053958 | -0.0054237 | -0.0095808 | -0.012316 | -0.013575 | -0.014146 | -0.01586 | -0.017606 | -0.016188 | -0.017779 | -0.018161
| 0.2 | 0.00094464 | -0.006517 | -0.012009 | -0.013821 | -0.016541 | -0.016606 | -0.018678 | -0.019965 | -0.019118 | -0.019839 | -0.021736
| 0.25 | 0.00065823 | -0.0075648 | -0.012859 | -0.015326 | -0.018235 | -0.019066 | -0.020679 | -0.022323 | -0.022863 | -0.0219 | -0.023432
| 0.3 | 0.00069724 | -0.0090191 | -0.01371 | -0.017677 | -0.018751 | -0.021237 | -0.022126 | -0.023128 | -0.023865 | -0.02418 | -0.025128
| 0.35 | 0.00034797 | -0.0090663 | -0.01456 | -0.018511 | -0.021241 | -0.022487 | -0.023791 | -0.024675 | -0.025528 | -0.026417 | -0.026824
| 0.4 | 0.00046628 | -0.010581 | -0.015411 | -0.019687 | -0.022025 | -0.02379 | -0.025456 | -0.026357 | -0.027001 | -0.028027 | -0.028522
| 0.45 | 0.00038893 | -0.011241 | -0.016261 | -0.021335 | -0.023541 | -0.025124 | -0.026898 | -0.027826 | -0.028965 | -0.029638 | -0.029837
| 0.5 | 7.1138e-05 | -0.01182 | -0.017112 | -0.022096 | -0.024531 | -0.026351 | -0.028214 | -0.0291 | -0.030502 | -0.031093 | -0.031608
| 0.55 | 3.4691e-06 | -0.012556 | -0.017962 | -0.023059 | -0.025775 | -0.027507 | -0.029712 | -0.030682 | -0.031874 | -0.032585 | -0.033293
| 0.6 | 0.00022568 | -0.013439 | -0.018813 | -0.024218 | -0.026712 | -0.028799 | -0.030669 | -0.031875 | -0.033338 | -0.033622 | -0.034774
| 0.65 | -8.7082e-05 | -0.014322 | -0.019663 | -0.024789 | -0.027856 | -0.029908 | -0.032165 | -0.033354 | -0.034529 | -0.035537 | -0.036099
| 0.7 | -0.00013008 | -0.014102 | -0.020514 | -0.025734 | -0.028584 | -0.030905 | -0.033315 | -0.034511 | -0.036011 | -0.036807 | -0.037377
| 0.75 | -0.00014363 | -0.015161 | -0.021364 | -0.026204 | -0.029519 | -0.032377 | -0.034446 | -0.036148 | -0.037009 | -0.038418 | -0.039032
| 0.8 | -0.00022051 | -0.016059 | -0.022215 | -0.02728 | -0.030564 | -0.033394 | -0.035601 | -0.037126 | -0.038275 | -0.039292 | -0.039905
| 0.85 | -0.00020386 | -0.016177 | -0.023065 | -0.027855 | -0.031482 | -0.034449 | -0.036478 | -0.038131 | -0.039748 | -0.04049 | -0.041197
| 0.9 | -0.0002619 | -0.017788 | -0.023938 | -0.028533 | -0.032809 | -0.035465 | -0.037328 | -0.039411 | -0.040782 | -0.041707 | -0.042516
| 0.95 | -0.00044485 | -0.017952 | -0.024016 | -0.02907 | -0.033299 | -0.036297 | -0.038706 | -0.040657 | -0.041916 | -0.04304 | -0.043672
| 1 | -0.00023002 | -0.018189 | -0.024788 | -0.029926 | -0.034356 | -0.037492 | -0.039635 | -0.04158 | -0.043138 | -0.043988 | -0.044827
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-23.83) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-117.04))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-23.83) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-117.04))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS6_LS>= (hidden)
If Iload/Isc x 5.6569 ≥1 | [12 empty] | If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 |  | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0114 | 1.0181 | 1.0228 | 1.0258 | 1.0272 | 1.0273 | 1.0263 | 1.0244 | 1.0217 | 1.0184 | 1.0146 |  | 0.05 | 1.0114 | 1.0181 | 1.0228 | 1.0258 | 1.0272 | 1.0273 | 1.0263 | 1.0244 | 1.0217 | 1.0184 | 1.0146
| 0.1 | 1.0331 | 1.0533 | 1.0694 | 1.0797 | 1.0853 | 1.0872 | 1.0862 | 1.0831 | 1.0784 | 1.0724 | 1.0654 |  | 0.1 | 1.0331 | 1.0533 | 1.0694 | 1.0797 | 1.0853 | 1.0872 | 1.0862 | 1.0831 | 1.0784 | 1.0724 | 1.0654
| 0.15 | 1.0441 | 1.07 | 1.094 | 1.1092 | 1.1169 | 1.1189 | 1.1168 | 1.1121 | 1.106 | 1.0983 | 1.0896 |  | 0.15 | 1.0441 | 1.07 | 1.094 | 1.1092 | 1.1169 | 1.1189 | 1.1168 | 1.1121 | 1.106 | 1.0983 | 1.0896
| 0.2 | 1.0452 | 1.0765 | 1.1093 | 1.1288 | 1.1381 | 1.1401 | 1.1372 | 1.1309 | 1.1223 | 1.1131 | 1.1033 |  | 0.2 | 1.0452 | 1.0765 | 1.1093 | 1.1288 | 1.1381 | 1.1401 | 1.1372 | 1.1309 | 1.1223 | 1.1131 | 1.1033
| 0.25 | 1.0393 | 1.0803 | 1.1174 | 1.1404 | 1.1508 | 1.1529 | 1.1495 | 1.1425 | 1.1342 | 1.1254 | 1.1154 |  | 0.25 | 1.0393 | 1.0803 | 1.1174 | 1.1404 | 1.1508 | 1.1529 | 1.1495 | 1.1425 | 1.1342 | 1.1254 | 1.1154
| 0.3 | 1.0292 | 1.0806 | 1.1215 | 1.1474 | 1.1588 | 1.161 | 1.1574 | 1.1517 | 1.1439 | 1.1342 | 1.1234 |  | 0.3 | 1.0292 | 1.0806 | 1.1215 | 1.1474 | 1.1588 | 1.161 | 1.1574 | 1.1517 | 1.1439 | 1.1342 | 1.1234
| 0.35 | 1.0167 | 1.0787 | 1.1233 | 1.1516 | 1.164 | 1.1665 | 1.1647 | 1.159 | 1.1507 | 1.1404 | 1.129 |  | 0.35 | 1.0167 | 1.0787 | 1.1233 | 1.1516 | 1.164 | 1.1665 | 1.1647 | 1.159 | 1.1507 | 1.1404 | 1.129
| 0.4 | 1.003 | 1.0755 | 1.1253 | 1.1542 | 1.1679 | 1.1723 | 1.1704 | 1.1644 | 1.1556 | 1.145 | 1.1331 |  | 0.4 | 1.003 | 1.0755 | 1.1253 | 1.1542 | 1.1679 | 1.1723 | 1.1704 | 1.1644 | 1.1556 | 1.145 | 1.1331
| 0.45 | 0.98887 | 1.0716 | 1.1266 | 1.1573 | 1.172 | 1.1766 | 1.1746 | 1.1684 | 1.1594 | 1.1485 | 1.1364 |  | 0.45 | 0.98887 | 1.0716 | 1.1266 | 1.1573 | 1.172 | 1.1766 | 1.1746 | 1.1684 | 1.1594 | 1.1485 | 1.1364
| 0.5 | 0.97472 | 1.0675 | 1.1272 | 1.1597 | 1.1751 | 1.1799 | 1.1779 | 1.1716 | 1.1624 | 1.1514 | 1.139 |  | 0.5 | 0.97472 | 1.0675 | 1.1272 | 1.1597 | 1.1751 | 1.1799 | 1.1779 | 1.1716 | 1.1624 | 1.1514 | 1.139
| 0.55 | 0.96089 | 1.0633 | 1.1272 | 1.1613 | 1.1774 | 1.1824 | 1.1806 | 1.1743 | 1.165 | 1.1538 | 1.1413 |  | 0.55 | 0.96089 | 1.0633 | 1.1272 | 1.1613 | 1.1774 | 1.1824 | 1.1806 | 1.1743 | 1.165 | 1.1538 | 1.1413
| 0.6 | 0.94756 | 1.0592 | 1.1268 | 1.1624 | 1.1791 | 1.1845 | 1.1828 | 1.1765 | 1.1672 | 1.156 | 1.1434 |  | 0.6 | 0.94756 | 1.0592 | 1.1268 | 1.1624 | 1.1791 | 1.1845 | 1.1828 | 1.1765 | 1.1672 | 1.156 | 1.1434
| 0.65 | 0.93484 | 1.0552 | 1.1262 | 1.1631 | 1.1805 | 1.1862 | 1.1847 | 1.1785 | 1.1692 | 1.1579 | 1.1453 |  | 0.65 | 0.93484 | 1.0552 | 1.1262 | 1.1631 | 1.1805 | 1.1862 | 1.1847 | 1.1785 | 1.1692 | 1.1579 | 1.1453
| 0.7 | 0.92278 | 1.0515 | 1.1254 | 1.1636 | 1.1816 | 1.1878 | 1.1865 | 1.1804 | 1.1711 | 1.1597 | 1.147 |  | 0.7 | 0.92278 | 1.0515 | 1.1254 | 1.1636 | 1.1816 | 1.1878 | 1.1865 | 1.1804 | 1.1711 | 1.1597 | 1.147
| 0.75 | 0.91139 | 1.0479 | 1.1245 | 1.1639 | 1.1826 | 1.1891 | 1.1881 | 1.182 | 1.1728 | 1.1614 | 1.1485 |  | 0.75 | 0.91139 | 1.0479 | 1.1245 | 1.1639 | 1.1826 | 1.1891 | 1.1881 | 1.182 | 1.1728 | 1.1614 | 1.1485
| 0.8 | 0.90067 | 1.0445 | 1.1236 | 1.164 | 1.1835 | 1.1904 | 1.1896 | 1.1836 | 1.1744 | 1.1629 | 1.1499 |  | 0.8 | 0.90067 | 1.0445 | 1.1236 | 1.164 | 1.1835 | 1.1904 | 1.1896 | 1.1836 | 1.1744 | 1.1629 | 1.1499
| 0.85 | 0.89059 | 1.0414 | 1.1226 | 1.1642 | 1.1843 | 1.1916 | 1.191 | 1.1851 | 1.1758 | 1.1643 | 1.1512 |  | 0.85 | 0.89059 | 1.0414 | 1.1226 | 1.1642 | 1.1843 | 1.1916 | 1.191 | 1.1851 | 1.1758 | 1.1643 | 1.1512
| 0.9 | 0.88112 | 1.0385 | 1.1216 | 1.1642 | 1.185 | 1.1928 | 1.1923 | 1.1865 | 1.1772 | 1.1655 | 1.1524 |  | 0.9 | 0.88112 | 1.0385 | 1.1216 | 1.1642 | 1.185 | 1.1928 | 1.1923 | 1.1865 | 1.1772 | 1.1655 | 1.1524
| 0.95 | 0.87223 | 1.0357 | 1.1206 | 1.1643 | 1.1858 | 1.1939 | 1.1936 | 1.1878 | 1.1784 | 1.1667 | 1.1534 |  | 0.95 | 0.87223 | 1.0357 | 1.1206 | 1.1643 | 1.1858 | 1.1939 | 1.1936 | 1.1878 | 1.1784 | 1.1667 | 1.1534
| 1 | 0.86389 | 1.0331 | 1.1197 | 1.1643 | 1.1865 | 1.195 | 1.1947 | 1.1889 | 1.1795 | 1.1677 | 1.1544 |  | 1 | 0.86389 | 1.0331 | 1.1197 | 1.1643 | 1.1865 | 1.195 | 1.1947 | 1.1889 | 1.1795 | 1.1677 | 1.1544
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 |  | 0 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| 0.05 | 1.3163 | 1.2977 | 1.2788 | 1.2601 | 1.2418 | 1.2237 | 1.2067 | 1.1894 | 1.1727 | 1.1565 | 1.1408 |  | 0.05 | 1.3163 | 1.2977 | 1.2788 | 1.2601 | 1.2418 | 1.2237 | 1.2067 | 1.1894 | 1.1727 | 1.1565 | 1.1408
| 0.1 | 1.1812 | 1.1552 | 1.1292 | 1.1033 | 1.0781 | 1.0538 | 1.0312 | 1.0091 | 0.9882 | 0.96841 | 0.94953 |  | 0.1 | 1.1812 | 1.1552 | 1.1292 | 1.1033 | 1.0781 | 1.0538 | 1.0312 | 1.0091 | 0.9882 | 0.96841 | 0.94953
| 0.15 | 1.0931 | 1.0616 | 1.0306 | 1.0007 | 0.97221 | 0.94527 | 0.92048 | 0.89666 | 0.87462 | 0.85403 | 0.83442 |  | 0.15 | 1.0931 | 1.0616 | 1.0306 | 1.0007 | 0.97221 | 0.94527 | 0.92048 | 0.89666 | 0.87462 | 0.85403 | 0.83442
| 0.2 | 1.0303 | 0.99357 | 0.95859 | 0.92578 | 0.89555 | 0.86774 | 0.84201 | 0.81753 | 0.79538 | 0.77452 | 0.7552 |  | 0.2 | 1.0303 | 0.99357 | 0.95859 | 0.92578 | 0.89555 | 0.86774 | 0.84201 | 0.81753 | 0.79538 | 0.77452 | 0.7552
| 0.25 | 0.98449 | 0.94076 | 0.90288 | 0.8684 | 0.83724 | 0.8085 | 0.78246 | 0.75802 | 0.73561 | 0.71502 | 0.69628 |  | 0.25 | 0.98449 | 0.94076 | 0.90288 | 0.8684 | 0.83724 | 0.8085 | 0.78246 | 0.75802 | 0.73561 | 0.71502 | 0.69628
| 0.3 | 0.94981 | 0.89863 | 0.85817 | 0.82264 | 0.79048 | 0.76134 | 0.73508 | 0.71071 | 0.6885 | 0.66806 | 0.64947 |  | 0.3 | 0.94981 | 0.89863 | 0.85817 | 0.82264 | 0.79048 | 0.76134 | 0.73508 | 0.71071 | 0.6885 | 0.66806 | 0.64947
| 0.35 | 0.92277 | 0.86403 | 0.82084 | 0.78451 | 0.75206 | 0.72225 | 0.69575 | 0.67142 | 0.64957 | 0.62949 | 0.61113 |  | 0.35 | 0.92277 | 0.86403 | 0.82084 | 0.78451 | 0.75206 | 0.72225 | 0.69575 | 0.67142 | 0.64957 | 0.62949 | 0.61113
| 0.4 | 0.90054 | 0.83449 | 0.78939 | 0.75231 | 0.7192 | 0.68896 | 0.66251 | 0.63816 | 0.61662 | 0.59708 | 0.57905 |  | 0.4 | 0.90054 | 0.83449 | 0.78939 | 0.75231 | 0.7192 | 0.68896 | 0.66251 | 0.63816 | 0.61662 | 0.59708 | 0.57905
| 0.45 | 0.88292 | 0.80906 | 0.7624 | 0.72408 | 0.69023 | 0.66029 | 0.63352 | 0.60949 | 0.58831 | 0.56893 | 0.55118 |  | 0.45 | 0.88292 | 0.80906 | 0.7624 | 0.72408 | 0.69023 | 0.66029 | 0.63352 | 0.60949 | 0.58831 | 0.56893 | 0.55118
| 0.5 | 0.86818 | 0.78632 | 0.7385 | 0.69899 | 0.66488 | 0.63434 | 0.60777 | 0.58445 | 0.56334 | 0.54442 | 0.52758 |  | 0.5 | 0.86818 | 0.78632 | 0.7385 | 0.69899 | 0.66488 | 0.63434 | 0.60777 | 0.58445 | 0.56334 | 0.54442 | 0.52758
| 0.55 | 0.85605 | 0.76654 | 0.71736 | 0.67672 | 0.64194 | 0.61171 | 0.58522 | 0.56187 | 0.5412 | 0.52287 | 0.5062 |  | 0.55 | 0.85605 | 0.76654 | 0.71736 | 0.67672 | 0.64194 | 0.61171 | 0.58522 | 0.56187 | 0.5412 | 0.52287 | 0.5062
| 0.6 | 0.84499 | 0.74873 | 0.69808 | 0.65655 | 0.62123 | 0.59096 | 0.56487 | 0.54165 | 0.52172 | 0.50363 | 0.48722 |  | 0.6 | 0.84499 | 0.74873 | 0.69808 | 0.65655 | 0.62123 | 0.59096 | 0.56487 | 0.54165 | 0.52172 | 0.50363 | 0.48722
| 0.65 | 0.83611 | 0.73284 | 0.6803 | 0.63797 | 0.60236 | 0.57235 | 0.5464 | 0.52389 | 0.50408 | 0.48628 | 0.47042 |  | 0.65 | 0.83611 | 0.73284 | 0.6803 | 0.63797 | 0.60236 | 0.57235 | 0.5464 | 0.52389 | 0.50408 | 0.48628 | 0.47042
| 0.7 | 0.82829 | 0.71805 | 0.66376 | 0.62098 | 0.5853 | 0.55534 | 0.52992 | 0.50774 | 0.48792 | 0.47063 | 0.45545 |  | 0.7 | 0.82829 | 0.71805 | 0.66376 | 0.62098 | 0.5853 | 0.55534 | 0.52992 | 0.50774 | 0.48792 | 0.47063 | 0.45545
| 0.75 | 0.82146 | 0.70428 | 0.64895 | 0.6052 | 0.5695 | 0.53952 | 0.51426 | 0.49255 | 0.4732 | 0.45644 | 0.4413 |  | 0.75 | 0.82146 | 0.70428 | 0.64895 | 0.6052 | 0.5695 | 0.53952 | 0.51426 | 0.49255 | 0.4732 | 0.45644 | 0.4413
| 0.8 | 0.81492 | 0.69181 | 0.63505 | 0.59044 | 0.55457 | 0.52532 | 0.50035 | 0.47878 | 0.46007 | 0.44364 | 0.42871 |  | 0.8 | 0.81492 | 0.69181 | 0.63505 | 0.59044 | 0.55457 | 0.52532 | 0.50035 | 0.47878 | 0.46007 | 0.44364 | 0.42871
| 0.85 | 0.80951 | 0.68024 | 0.62171 | 0.5769 | 0.54093 | 0.51179 | 0.4873 | 0.46621 | 0.44772 | 0.43155 | 0.41708 |  | 0.85 | 0.80951 | 0.68024 | 0.62171 | 0.5769 | 0.54093 | 0.51179 | 0.4873 | 0.46621 | 0.44772 | 0.43155 | 0.41708
| 0.9 | 0.8048 | 0.66943 | 0.60949 | 0.56396 | 0.52859 | 0.49954 | 0.47526 | 0.45445 | 0.43641 | 0.42044 | 0.40604 |  | 0.9 | 0.8048 | 0.66943 | 0.60949 | 0.56396 | 0.52859 | 0.49954 | 0.47526 | 0.45445 | 0.43641 | 0.42044 | 0.40604
| 0.95 | 0.8005 | 0.659 | 0.59766 | 0.55194 | 0.51663 | 0.48811 | 0.46392 | 0.44366 | 0.42583 | 0.41039 | 0.39624 |  | 0.95 | 0.8005 | 0.659 | 0.59766 | 0.55194 | 0.51663 | 0.48811 | 0.46392 | 0.44366 | 0.42583 | 0.41039 | 0.39624
| 1 | 0.79612 | 0.64947 | 0.58669 | 0.54087 | 0.50552 | 0.47698 | 0.45362 | 0.43359 | 0.41605 | 0.40061 | 0.387 |  | 1 | 0.79612 | 0.64947 | 0.58669 | 0.54087 | 0.50552 | 0.47698 | 0.45362 | 0.43359 | 0.41605 | 0.40061 | 0.387
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0037694 | -0.0023591 | -0.0010448 | 0.00019142 | 0.0013267 | 0.0023733 | 0.0033013 | 0.0041339 | 0.0048942 | 0.0055883 | 0.0061953 |  | 0.05 | -0.0037694 | -0.0023591 | -0.0010448 | 0.00019142 | 0.0013267 | 0.0023733 | 0.0033013 | 0.0041339 | 0.0048942 | 0.0055883 | 0.0061953
| 0.1 | -0.0017279 | 0.00024194 | 0.0019301 | 0.0033684 | 0.0045309 | 0.0055545 | 0.0063843 | 0.0070557 | 0.007633 | 0.0081363 | 0.0085427 |  | 0.1 | -0.0017279 | 0.00024194 | 0.0019301 | 0.0033684 | 0.0045309 | 0.0055545 | 0.0063843 | 0.0070557 | 0.007633 | 0.0081363 | 0.0085427
| 0.15 | -0.0013232 | 0.0014271 | 0.0033883 | 0.0048562 | 0.0059663 | 0.0068918 | 0.0075551 | 0.0080677 | 0.008544 | 0.0089408 | 0.0091547 |  | 0.15 | -0.0013232 | 0.0014271 | 0.0033883 | 0.0048562 | 0.0059663 | 0.0068918 | 0.0075551 | 0.0080677 | 0.008544 | 0.0089408 | 0.0091547
| 0.2 | -0.0018611 | 0.0020082 | 0.0041231 | 0.0055317 | 0.0066389 | 0.0074717 | 0.008074 | 0.0084963 | 0.0088659 | 0.0091414 | 0.0093216 |  | 0.2 | -0.0018611 | 0.0020082 | 0.0041231 | 0.0055317 | 0.0066389 | 0.0074717 | 0.008074 | 0.0084963 | 0.0088659 | 0.0091414 | 0.0093216
| 0.25 | -0.002429 | 0.0021935 | 0.0045512 | 0.0060222 | 0.0070537 | 0.0078753 | 0.0083696 | 0.0088914 | 0.0091167 | 0.0093714 | 0.009459 |  | 0.25 | -0.002429 | 0.0021935 | 0.0045512 | 0.0060222 | 0.0070537 | 0.0078753 | 0.0083696 | 0.0088914 | 0.0091167 | 0.0093714 | 0.009459
| 0.3 | -0.0031336 | 0.0024584 | 0.0047105 | 0.0063562 | 0.0074502 | 0.0082125 | 0.0087798 | 0.0090279 | 0.0093021 | 0.0094699 | 0.0094547 |  | 0.3 | -0.0031336 | 0.0024584 | 0.0047105 | 0.0063562 | 0.0074502 | 0.0082125 | 0.0087798 | 0.0090279 | 0.0093021 | 0.0094699 | 0.0094547
| 0.35 | -0.0039985 | 0.0025555 | 0.0050451 | 0.0067138 | 0.007857 | 0.0085881 | 0.0090043 | 0.0091986 | 0.0093668 | 0.009484 | 0.0094036 |  | 0.35 | -0.0039985 | 0.0025555 | 0.0050451 | 0.0067138 | 0.007857 | 0.0085881 | 0.0090043 | 0.0091986 | 0.0093668 | 0.009484 | 0.0094036
| 0.4 | -0.004661 | 0.0026586 | 0.0053463 | 0.007043 | 0.0081944 | 0.0088271 | 0.009182 | 0.0093152 | 0.0093534 | 0.0093927 | 0.0093163 |  | 0.4 | -0.004661 | 0.0026586 | 0.0053463 | 0.007043 | 0.0081944 | 0.0088271 | 0.009182 | 0.0093152 | 0.0093534 | 0.0093927 | 0.0093163
| 0.45 | -0.0050866 | 0.00269 | 0.0056474 | 0.0073455 | 0.0084651 | 0.0089971 | 0.0092309 | 0.0093706 | 0.0094035 | 0.0093185 | 0.0092331 |  | 0.45 | -0.0050866 | 0.00269 | 0.0056474 | 0.0073455 | 0.0084651 | 0.0089971 | 0.0092309 | 0.0093706 | 0.0094035 | 0.0093185 | 0.0092331
| 0.5 | -0.0055925 | 0.0028097 | 0.0059281 | 0.0077004 | 0.0086279 | 0.0091084 | 0.0092929 | 0.0093703 | 0.0092 | 0.0091614 | 0.0090523 |  | 0.5 | -0.0055925 | 0.0028097 | 0.0059281 | 0.0077004 | 0.0086279 | 0.0091084 | 0.0092929 | 0.0093703 | 0.0092 | 0.0091614 | 0.0090523
| 0.55 | -0.0061852 | 0.0029995 | 0.0061232 | 0.0079993 | 0.0088219 | 0.0092473 | 0.0092908 | 0.009206 | 0.0091238 | 0.0089644 | 0.0088725 |  | 0.55 | -0.0061852 | 0.0029995 | 0.0061232 | 0.0079993 | 0.0088219 | 0.0092473 | 0.0092908 | 0.009206 | 0.0091238 | 0.0089644 | 0.0088725
| 0.6 | -0.0065539 | 0.003065 | 0.0064031 | 0.0082 | 0.0088665 | 0.0091774 | 0.0092423 | 0.0090886 | 0.0090029 | 0.0088871 | 0.0086334 |  | 0.6 | -0.0065539 | 0.003065 | 0.0064031 | 0.0082 | 0.0088665 | 0.0091774 | 0.0092423 | 0.0090886 | 0.0090029 | 0.0088871 | 0.0086334
| 0.65 | -0.0067694 | 0.0031483 | 0.0066917 | 0.0083508 | 0.0089314 | 0.0091984 | 0.0091237 | 0.0090927 | 0.0088739 | 0.0086813 | 0.008442 |  | 0.65 | -0.0067694 | 0.0031483 | 0.0066917 | 0.0083508 | 0.0089314 | 0.0091984 | 0.0091237 | 0.0090927 | 0.0088739 | 0.0086813 | 0.008442
| 0.7 | -0.0071957 | 0.0032909 | 0.0069597 | 0.0084229 | 0.0090026 | 0.009115 | 0.0090145 | 0.0089086 | 0.0086363 | 0.0085375 | 0.008303 |  | 0.7 | -0.0071957 | 0.0032909 | 0.0069597 | 0.0084229 | 0.0090026 | 0.009115 | 0.0090145 | 0.0089086 | 0.0086363 | 0.0085375 | 0.008303
| 0.75 | -0.0074499 | 0.0034566 | 0.0071718 | 0.00853 | 0.0089509 | 0.0090219 | 0.0089227 | 0.0087542 | 0.0084804 | 0.0082978 | 0.0081167 |  | 0.75 | -0.0074499 | 0.0034566 | 0.0071718 | 0.00853 | 0.0089509 | 0.0090219 | 0.0089227 | 0.0087542 | 0.0084804 | 0.0082978 | 0.0081167
| 0.8 | -0.0077177 | 0.0036726 | 0.0073618 | 0.0086283 | 0.008954 | 0.0089591 | 0.0087949 | 0.0085532 | 0.0084159 | 0.0081233 | 0.0079164 |  | 0.8 | -0.0077177 | 0.0036726 | 0.0073618 | 0.0086283 | 0.008954 | 0.0089591 | 0.0087949 | 0.0085532 | 0.0084159 | 0.0081233 | 0.0079164
| 0.85 | -0.0079204 | 0.0038198 | 0.0074967 | 0.008721 | 0.0089335 | 0.0088603 | 0.0086862 | 0.008389 | 0.0081988 | 0.0080319 | 0.0077538 |  | 0.85 | -0.0079204 | 0.0038198 | 0.0074967 | 0.008721 | 0.0089335 | 0.0088603 | 0.0086862 | 0.008389 | 0.0081988 | 0.0080319 | 0.0077538
| 0.9 | -0.0081054 | 0.003931 | 0.0076026 | 0.008675 | 0.0088773 | 0.008777 | 0.0085071 | 0.0082856 | 0.0080686 | 0.0078187 | 0.0076578 |  | 0.9 | -0.0081054 | 0.003931 | 0.0076026 | 0.008675 | 0.0088773 | 0.008777 | 0.0085071 | 0.0082856 | 0.0080686 | 0.0078187 | 0.0076578
| 0.95 | -0.0082425 | 0.0041216 | 0.0077754 | 0.008721 | 0.0087869 | 0.0086182 | 0.0083803 | 0.0080617 | 0.0079087 | 0.0076527 | 0.0074534 |  | 0.95 | -0.0082425 | 0.0041216 | 0.0077754 | 0.008721 | 0.0087869 | 0.0086182 | 0.0083803 | 0.0080617 | 0.0079087 | 0.0076527 | 0.0074534
| 1 | -0.0084072 | 0.0043186 | 0.0077694 | 0.0086941 | 0.0087264 | 0.0084649 | 0.0082817 | 0.0079599 | 0.0077343 | 0.0074498 | 0.007259 |  | 1 | -0.0084072 | 0.0043186 | 0.0077694 | 0.0086941 | 0.0087264 | 0.0084649 | 0.0082817 | 0.0079599 | 0.0077343 | 0.0074498 | 0.007259
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0014737 | 0.0015333 | 0.0015977 | 0.0016652 | 0.0017046 | 0.0017665 | 0.0018137 | 0.0018669 | 0.0019341 | 0.0019705 | 0.0020054 |  | 0.05 | 0.0014737 | 0.0015333 | 0.0015977 | 0.0016652 | 0.0017046 | 0.0017665 | 0.0018137 | 0.0018669 | 0.0019341 | 0.0019705 | 0.0020054
| 0.1 | 0.0017291 | 0.0018023 | 0.0018728 | 0.0019334 | 0.0019846 | 0.0020115 | 0.0020494 | 0.0020868 | 0.0021075 | 0.0021233 | 0.0021335 |  | 0.1 | 0.0017291 | 0.0018023 | 0.0018728 | 0.0019334 | 0.0019846 | 0.0020115 | 0.0020494 | 0.0020868 | 0.0021075 | 0.0021233 | 0.0021335
| 0.15 | 0.0017507 | 0.001864 | 0.0019442 | 0.0019903 | 0.0020284 | 0.0020417 | 0.0020654 | 0.0020783 | 0.0020798 | 0.002086 | 0.002077 |  | 0.15 | 0.0017507 | 0.001864 | 0.0019442 | 0.0019903 | 0.0020284 | 0.0020417 | 0.0020654 | 0.0020783 | 0.0020798 | 0.002086 | 0.002077
| 0.2 | 0.001693 | 0.0018541 | 0.0019345 | 0.0019789 | 0.0019962 | 0.0020083 | 0.0020237 | 0.0020153 | 0.0020161 | 0.0020001 | 0.001988 |  | 0.2 | 0.001693 | 0.0018541 | 0.0019345 | 0.0019789 | 0.0019962 | 0.0020083 | 0.0020237 | 0.0020153 | 0.0020161 | 0.0020001 | 0.001988
| 0.25 | 0.001578 | 0.0018145 | 0.0019017 | 0.0019297 | 0.0019505 | 0.0019529 | 0.0019637 | 0.0019505 | 0.0019429 | 0.0019212 | 0.0019042 |  | 0.25 | 0.001578 | 0.0018145 | 0.0019017 | 0.0019297 | 0.0019505 | 0.0019529 | 0.0019637 | 0.0019505 | 0.0019429 | 0.0019212 | 0.0019042
| 0.3 | 0.0014676 | 0.0017732 | 0.0018627 | 0.0018906 | 0.0018923 | 0.001904 | 0.0019019 | 0.0018977 | 0.0018808 | 0.0018641 | 0.0018465 |  | 0.3 | 0.0014676 | 0.0017732 | 0.0018627 | 0.0018906 | 0.0018923 | 0.001904 | 0.0019019 | 0.0018977 | 0.0018808 | 0.0018641 | 0.0018465
| 0.35 | 0.0013817 | 0.0017302 | 0.0018084 | 0.0018413 | 0.0018656 | 0.0018648 | 0.0018607 | 0.0018507 | 0.0018261 | 0.0018044 | 0.0017908 |  | 0.35 | 0.0013817 | 0.0017302 | 0.0018084 | 0.0018413 | 0.0018656 | 0.0018648 | 0.0018607 | 0.0018507 | 0.0018261 | 0.0018044 | 0.0017908
| 0.4 | 0.0012882 | 0.0016918 | 0.0017698 | 0.0018087 | 0.0018326 | 0.0018398 | 0.001834 | 0.0018074 | 0.001785 | 0.0017617 | 0.0017233 |  | 0.4 | 0.0012882 | 0.0016918 | 0.0017698 | 0.0018087 | 0.0018326 | 0.0018398 | 0.001834 | 0.0018074 | 0.001785 | 0.0017617 | 0.0017233
| 0.45 | 0.001192 | 0.0016621 | 0.001731 | 0.0017906 | 0.0018073 | 0.0018051 | 0.0017913 | 0.0017717 | 0.0017374 | 0.001705 | 0.0016767 |  | 0.45 | 0.001192 | 0.0016621 | 0.001731 | 0.0017906 | 0.0018073 | 0.0018051 | 0.0017913 | 0.0017717 | 0.0017374 | 0.001705 | 0.0016767
| 0.5 | 0.001121 | 0.0016302 | 0.0017053 | 0.0017552 | 0.0017842 | 0.0017749 | 0.0017602 | 0.0017318 | 0.0016865 | 0.0016633 | 0.001629 |  | 0.5 | 0.001121 | 0.0016302 | 0.0017053 | 0.0017552 | 0.0017842 | 0.0017749 | 0.0017602 | 0.0017318 | 0.0016865 | 0.0016633 | 0.001629
| 0.55 | 0.0010677 | 0.0015915 | 0.0016959 | 0.0017446 | 0.0017555 | 0.0017506 | 0.0017307 | 0.0016837 | 0.001652 | 0.0016181 | 0.0015863 |  | 0.55 | 0.0010677 | 0.0015915 | 0.0016959 | 0.0017446 | 0.0017555 | 0.0017506 | 0.0017307 | 0.0016837 | 0.001652 | 0.0016181 | 0.0015863
| 0.6 | 0.0010127 | 0.0015608 | 0.0016712 | 0.0017316 | 0.0017411 | 0.0017211 | 0.0016901 | 0.0016468 | 0.001616 | 0.0015729 | 0.0015484 |  | 0.6 | 0.0010127 | 0.0015608 | 0.0016712 | 0.0017316 | 0.0017411 | 0.0017211 | 0.0016901 | 0.0016468 | 0.001616 | 0.0015729 | 0.0015484
| 0.65 | 0.00094744 | 0.0015441 | 0.0016581 | 0.0017153 | 0.001711 | 0.0016871 | 0.0016623 | 0.0016141 | 0.0015837 | 0.0015425 | 0.0014964 |  | 0.65 | 0.00094744 | 0.0015441 | 0.0016581 | 0.0017153 | 0.001711 | 0.0016871 | 0.0016623 | 0.0016141 | 0.0015837 | 0.0015425 | 0.0014964
| 0.7 | 0.00091863 | 0.0015216 | 0.0016428 | 0.001701 | 0.0016897 | 0.001656 | 0.0016287 | 0.0015754 | 0.0015416 | 0.0015029 | 0.0014723 |  | 0.7 | 0.00091863 | 0.0015216 | 0.0016428 | 0.001701 | 0.0016897 | 0.001656 | 0.0016287 | 0.0015754 | 0.0015416 | 0.0015029 | 0.0014723
| 0.75 | 0.00087765 | 0.0015031 | 0.0016307 | 0.0016895 | 0.0016773 | 0.0016398 | 0.0015919 | 0.0015514 | 0.0015153 | 0.0014715 | 0.0014312 |  | 0.75 | 0.00087765 | 0.0015031 | 0.0016307 | 0.0016895 | 0.0016773 | 0.0016398 | 0.0015919 | 0.0015514 | 0.0015153 | 0.0014715 | 0.0014312
| 0.8 | 0.0008427 | 0.0014777 | 0.0016289 | 0.0016624 | 0.0016412 | 0.0016082 | 0.0015679 | 0.0015206 | 0.0014726 | 0.0014399 | 0.0013886 |  | 0.8 | 0.0008427 | 0.0014777 | 0.0016289 | 0.0016624 | 0.0016412 | 0.0016082 | 0.0015679 | 0.0015206 | 0.0014726 | 0.0014399 | 0.0013886
| 0.85 | 0.00081939 | 0.0014705 | 0.0016159 | 0.0016509 | 0.0016276 | 0.001582 | 0.0015372 | 0.0014944 | 0.0014467 | 0.0014041 | 0.0013651 |  | 0.85 | 0.00081939 | 0.0014705 | 0.0016159 | 0.0016509 | 0.0016276 | 0.001582 | 0.0015372 | 0.0014944 | 0.0014467 | 0.0014041 | 0.0013651
| 0.9 | 0.00077725 | 0.0014571 | 0.0016131 | 0.0016326 | 0.0015949 | 0.0015535 | 0.0015102 | 0.0014641 | 0.001417 | 0.0013749 | 0.0013383 |  | 0.9 | 0.00077725 | 0.0014571 | 0.0016131 | 0.0016326 | 0.0015949 | 0.0015535 | 0.0015102 | 0.0014641 | 0.001417 | 0.0013749 | 0.0013383
| 0.95 | 0.00075172 | 0.0014453 | 0.0016018 | 0.0016116 | 0.0015772 | 0.0015269 | 0.00148 | 0.001435 | 0.001391 | 0.0013494 | 0.0013017 |  | 0.95 | 0.00075172 | 0.0014453 | 0.0016018 | 0.0016116 | 0.0015772 | 0.0015269 | 0.00148 | 0.001435 | 0.001391 | 0.0013494 | 0.0013017
| 1 | 0.00072291 | 0.0014374 | 0.0015932 | 0.0015903 | 0.0015615 | 0.0015048 | 0.0014664 | 0.0014019 | 0.0013656 | 0.0013252 | 0.0012808 |  | 1 | 0.00072291 | 0.0014374 | 0.0015932 | 0.0015903 | 0.0015615 | 0.0015048 | 0.0014664 | 0.0014019 | 0.0013656 | 0.0013252 | 0.0012808
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | [12 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 0 to 1
| 0.05 | 1.4903 | 1.6209 | 1.7319 | 1.8253 | 1.9071 | 1.9733 | 2.0245 | 2.0718 | 2.1158 | 2.1528 | 2.1847 |  | 0.05 | 1.4903 | 1.6209 | 1.7319 | 1.8253 | 1.9071 | 1.9733 | 2.0245 | 2.0718 | 2.1158 | 2.1528 | 2.1847
| 0.1 | 1.601 | 1.9268 | 2.1814 | 2.3864 | 2.5454 | 2.6756 | 2.785 | 2.8708 | 2.9435 | 2.9922 | 3.0506 |  | 0.1 | 1.601 | 1.9268 | 2.1814 | 2.3864 | 2.5454 | 2.6756 | 2.785 | 2.8708 | 2.9435 | 2.9922 | 3.0506
| 0.15 | 1.5883 | 2.127 | 2.5244 | 2.8419 | 3.0813 | 3.247 | 3.4052 | 3.5182 | 3.5959 | 3.6722 | 3.7526 |  | 0.15 | 1.5883 | 2.127 | 2.5244 | 2.8419 | 3.0813 | 3.247 | 3.4052 | 3.5182 | 3.5959 | 3.6722 | 3.7526
| 0.2 | 1.5509 | 2.2899 | 2.8185 | 3.2084 | 3.5091 | 3.7994 | 3.9143 | 4.1015 | 4.1984 | 4.2278 | 4.3039 |  | 0.2 | 1.5509 | 2.2899 | 2.8185 | 3.2084 | 3.5091 | 3.7994 | 3.9143 | 4.1015 | 4.1984 | 4.2278 | 4.3039
| 0.25 | 1.5031 | 2.4406 | 3.0819 | 3.5558 | 3.9126 | 4.1244 | 4.3728 | 4.554 | 4.6527 | 4.7834 | 4.8398 |  | 0.25 | 1.5031 | 2.4406 | 3.0819 | 3.5558 | 3.9126 | 4.1244 | 4.3728 | 4.554 | 4.6527 | 4.7834 | 4.8398
| 0.3 | 1.4564 | 2.6163 | 3.2951 | 3.8767 | 4.2869 | 4.5471 | 4.7356 | 5.0009 | 5.1303 | 5.2368 | 5.3211 |  | 0.3 | 1.4564 | 2.6163 | 3.2951 | 3.8767 | 4.2869 | 4.5471 | 4.7356 | 5.0009 | 5.1303 | 5.2368 | 5.3211
| 0.35 | 1.4148 | 2.7048 | 3.5676 | 4.1444 | 4.6355 | 4.9679 | 5.2773 | 5.4052 | 5.5824 | 5.6716 | 5.7817 |  | 0.35 | 1.4148 | 2.7048 | 3.5676 | 4.1444 | 4.6355 | 4.9679 | 5.2773 | 5.4052 | 5.5824 | 5.6716 | 5.7817
| 0.4 | 1.3846 | 2.9013 | 3.7884 | 4.4642 | 4.9639 | 5.2406 | 5.6038 | 5.8095 | 5.9767 | 6.1 | 6.1954 |  | 0.4 | 1.3846 | 2.9013 | 3.7884 | 4.4642 | 4.9639 | 5.2406 | 5.6038 | 5.8095 | 5.9767 | 6.1 | 6.1954
| 0.45 | 1.3535 | 2.9492 | 4.0013 | 4.7416 | 5.2685 | 5.665 | 5.949 | 6.1726 | 6.3462 | 6.4746 | 6.5742 |  | 0.45 | 1.3535 | 2.9492 | 4.0013 | 4.7416 | 5.2685 | 5.665 | 5.949 | 6.1726 | 6.3462 | 6.4746 | 6.5742
| 0.5 | 1.3265 | 3.0577 | 4.2049 | 4.9955 | 5.5591 | 5.9734 | 6.2798 | 6.5164 | 6.6911 | 6.836 | 6.937 |  | 0.5 | 1.3265 | 3.0577 | 4.2049 | 4.9955 | 5.5591 | 5.9734 | 6.2798 | 6.5164 | 6.6911 | 6.836 | 6.937
| 0.55 | 1.3036 | 3.168 | 4.4022 | 5.2392 | 5.8222 | 6.2711 | 6.5853 | 6.8424 | 7.0252 | 7.1705 | 7.2792 |  | 0.55 | 1.3036 | 3.168 | 4.4022 | 5.2392 | 5.8222 | 6.2711 | 6.5853 | 6.8424 | 7.0252 | 7.1705 | 7.2792
| 0.6 | 1.2903 | 3.2465 | 4.5766 | 5.4717 | 6.0886 | 6.55 | 6.8871 | 7.142 | 7.3432 | 7.4899 | 7.6026 |  | 0.6 | 1.2903 | 3.2465 | 4.5766 | 5.4717 | 6.0886 | 6.55 | 6.8871 | 7.142 | 7.3432 | 7.4899 | 7.6026
| 0.65 | 1.2735 | 3.3893 | 4.8079 | 5.6921 | 6.336 | 6.8193 | 7.1632 | 7.4368 | 7.6428 | 7.7946 | 7.9131 |  | 0.65 | 1.2735 | 3.3893 | 4.8079 | 5.6921 | 6.336 | 6.8193 | 7.1632 | 7.4368 | 7.6428 | 7.7946 | 7.9131
| 0.7 | 1.2571 | 3.5069 | 4.9246 | 5.8963 | 6.5699 | 7.0744 | 7.4372 | 7.7187 | 7.932 | 8.0913 | 8.215 |  | 0.7 | 1.2571 | 3.5069 | 4.9246 | 5.8963 | 6.5699 | 7.0744 | 7.4372 | 7.7187 | 7.932 | 8.0913 | 8.215
| 0.75 | 1.2425 | 3.6372 | 5.1168 | 6.1075 | 6.8118 | 7.317 | 7.6895 | 7.9803 | 8.2051 | 8.3755 | 8.5055 |  | 0.75 | 1.2425 | 3.6372 | 5.1168 | 6.1075 | 6.8118 | 7.317 | 7.6895 | 7.9803 | 8.2051 | 8.3755 | 8.5055
| 0.8 | 1.2378 | 3.7201 | 5.2787 | 6.3021 | 7.0275 | 7.5559 | 7.9489 | 8.2426 | 8.4789 | 8.6553 | 8.7806 |  | 0.8 | 1.2378 | 3.7201 | 5.2787 | 6.3021 | 7.0275 | 7.5559 | 7.9489 | 8.2426 | 8.4789 | 8.6553 | 8.7806
| 0.85 | 1.2257 | 3.8332 | 5.4343 | 6.5011 | 7.2367 | 7.781 | 8.1872 | 8.498 | 8.7298 | 8.9187 | 9.0533 |  | 0.85 | 1.2257 | 3.8332 | 5.4343 | 6.5011 | 7.2367 | 7.781 | 8.1872 | 8.498 | 8.7298 | 8.9187 | 9.0533
| 0.9 | 1.2149 | 3.9333 | 5.5896 | 6.6766 | 7.446 | 8.0045 | 8.4211 | 8.7408 | 8.9841 | 9.1654 | 9.3075 |  | 0.9 | 1.2149 | 3.9333 | 5.5896 | 6.6766 | 7.446 | 8.0045 | 8.4211 | 8.7408 | 8.9841 | 9.1654 | 9.3075
| 0.95 | 1.2061 | 4.0561 | 5.749 | 6.8507 | 7.6432 | 8.2222 | 8.6482 | 8.9781 | 9.2276 | 9.4215 | 9.5575 |  | 0.95 | 1.2061 | 4.0561 | 5.749 | 6.8507 | 7.6432 | 8.2222 | 8.6482 | 8.9781 | 9.2276 | 9.4215 | 9.5575
| 1 | 1.2059 | 4.1427 | 5.8845 | 7.0314 | 7.8339 | 8.4238 | 8.8713 | 9.213 | 9.4668 | 9.6605 | 9.8052 |  | 1 | 1.2059 | 4.1427 | 5.8845 | 7.0314 | 7.8339 | 8.4238 | 8.8713 | 9.213 | 9.4668 | 9.6605 | 9.8052
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.023371 | -0.019987 | -0.015913 | -0.013444 | -0.010041 | -0.0067524 | -0.0046334 | -0.0020859 | 0.00050047 | 0.003071 | 0.0050557 |  | 0.05 | -0.023371 | -0.019987 | -0.015913 | -0.013444 | -0.010041 | -0.0067524 | -0.0046334 | -0.0020859 | 0.00050047 | 0.003071 | 0.0050557
| 0.1 | -0.021021 | -0.014847 | -0.0091611 | -0.003508 | 0.0010274 | 0.0081778 | 0.0088793 | 0.011324 | 0.012526 | 0.016956 | 0.021502 |  | 0.1 | -0.021021 | -0.014847 | -0.0091611 | -0.003508 | 0.0010274 | 0.0081778 | 0.0088793 | 0.011324 | 0.012526 | 0.016956 | 0.021502
| 0.15 | -0.021084 | -0.010282 | -0.0016696 | 0.0065332 | 0.010876 | 0.018656 | 0.021474 | 0.024733 | 0.024551 | 0.025329 | 0.033935 |  | 0.15 | -0.021084 | -0.010282 | -0.0016696 | 0.0065332 | 0.010876 | 0.018656 | 0.021474 | 0.024733 | 0.024551 | 0.025329 | 0.033935
| 0.2 | -0.022132 | -0.0060352 | 0.0058219 | 0.014939 | 0.022991 | 0.029943 | 0.03407 | 0.037438 | 0.036576 | 0.042537 | 0.046368 |  | 0.2 | -0.022132 | -0.0060352 | 0.0058219 | 0.014939 | 0.022991 | 0.029943 | 0.03407 | 0.037438 | 0.036576 | 0.042537 | 0.046368
| 0.25 | -0.027205 | -0.0060377 | 0.011325 | 0.023044 | 0.032502 | 0.036726 | 0.046665 | 0.050142 | 0.049187 | 0.053788 | 0.061933 |  | 0.25 | -0.027205 | -0.0060377 | 0.011325 | 0.023044 | 0.032502 | 0.036726 | 0.046665 | 0.050142 | 0.049187 | 0.053788 | 0.061933
| 0.3 | -0.031357 | -0.0017135 | 0.018354 | 0.029028 | 0.042736 | 0.051761 | 0.057741 | 0.062847 | 0.064771 | 0.070831 | 0.081578 |  | 0.3 | -0.031357 | -0.0017135 | 0.018354 | 0.029028 | 0.042736 | 0.051761 | 0.057741 | 0.062847 | 0.064771 | 0.070831 | 0.081578
| 0.35 | -0.033005 | 0.00031274 | 0.023285 | 0.038453 | 0.05297 | 0.061272 | 0.068437 | 0.074981 | 0.080355 | 0.08417 | 0.092117 |  | 0.35 | -0.033005 | 0.00031274 | 0.023285 | 0.038453 | 0.05297 | 0.061272 | 0.068437 | 0.074981 | 0.080355 | 0.08417 | 0.092117
| 0.4 | -0.035808 | -0.0051778 | 0.028216 | 0.047879 | 0.062707 | 0.073911 | 0.079133 | 0.087244 | 0.089337 | 0.09751 | 0.10105 |  | 0.4 | -0.035808 | -0.0051778 | 0.028216 | 0.047879 | 0.062707 | 0.073911 | 0.079133 | 0.087244 | 0.089337 | 0.09751 | 0.10105
| 0.45 | -0.039937 | 0.0009599 | 0.034179 | 0.057304 | 0.071162 | 0.08634 | 0.092485 | 0.098308 | 0.10148 | 0.10851 | 0.11031 |  | 0.45 | -0.039937 | 0.0009599 | 0.034179 | 0.057304 | 0.071162 | 0.08634 | 0.092485 | 0.098308 | 0.10148 | 0.10851 | 0.11031
| 0.5 | -0.042294 | 0.0050034 | 0.040475 | 0.068948 | 0.079391 | 0.092428 | 0.10198 | 0.1087 | 0.11488 | 0.11731 | 0.11982 |  | 0.5 | -0.042294 | 0.0050034 | 0.040475 | 0.068948 | 0.079391 | 0.092428 | 0.10198 | 0.1087 | 0.11488 | 0.11731 | 0.11982
| 0.55 | -0.042467 | 0.0046088 | 0.046772 | 0.074296 | 0.090437 | 0.10386 | 0.11133 | 0.11658 | 0.12368 | 0.12474 | 0.12933 |  | 0.55 | -0.042467 | 0.0046088 | 0.046772 | 0.074296 | 0.090437 | 0.10386 | 0.11133 | 0.11658 | 0.12368 | 0.12474 | 0.12933
| 0.6 | -0.043606 | 0.0079407 | 0.053069 | 0.079094 | 0.098212 | 0.11103 | 0.11972 | 0.12639 | 0.13136 | 0.13456 | 0.13541 |  | 0.6 | -0.043606 | 0.0079407 | 0.053069 | 0.079094 | 0.098212 | 0.11103 | 0.11972 | 0.12639 | 0.13136 | 0.13456 | 0.13541
| 0.65 | -0.047123 | 0.0086024 | 0.059365 | 0.087773 | 0.1068 | 0.11903 | 0.12733 | 0.13517 | 0.13924 | 0.14053 | 0.14326 |  | 0.65 | -0.047123 | 0.0086024 | 0.059365 | 0.087773 | 0.1068 | 0.11903 | 0.12733 | 0.13517 | 0.13924 | 0.14053 | 0.14326
| 0.7 | -0.046108 | 0.013738 | 0.065662 | 0.095989 | 0.11575 | 0.12782 | 0.13494 | 0.13936 | 0.14529 | 0.15089 | 0.15071 |  | 0.7 | -0.046108 | 0.013738 | 0.065662 | 0.095989 | 0.11575 | 0.12782 | 0.13494 | 0.13936 | 0.14529 | 0.15089 | 0.15071
| 0.75 | -0.046866 | 0.014868 | 0.071959 | 0.10227 | 0.12253 | 0.13318 | 0.14144 | 0.1455 | 0.15161 | 0.15476 | 0.15683 |  | 0.75 | -0.046866 | 0.014868 | 0.071959 | 0.10227 | 0.12253 | 0.13318 | 0.14144 | 0.1455 | 0.15161 | 0.15476 | 0.15683
| 0.8 | -0.048439 | 0.018825 | 0.076606 | 0.11174 | 0.12858 | 0.13891 | 0.14835 | 0.15437 | 0.15799 | 0.16245 | 0.16487 |  | 0.8 | -0.048439 | 0.018825 | 0.076606 | 0.11174 | 0.12858 | 0.13891 | 0.14835 | 0.15437 | 0.15799 | 0.16245 | 0.16487
| 0.85 | -0.048778 | 0.016005 | 0.085915 | 0.11769 | 0.13714 | 0.14582 | 0.15394 | 0.15893 | 0.16346 | 0.16675 | 0.16828 |  | 0.85 | -0.048778 | 0.016005 | 0.085915 | 0.11769 | 0.13714 | 0.14582 | 0.15394 | 0.15893 | 0.16346 | 0.16675 | 0.16828
| 0.9 | -0.049446 | 0.023868 | 0.090116 | 0.12134 | 0.1435 | 0.152 | 0.16002 | 0.16694 | 0.16927 | 0.17203 | 0.1755 |  | 0.9 | -0.049446 | 0.023868 | 0.090116 | 0.12134 | 0.1435 | 0.152 | 0.16002 | 0.16694 | 0.16927 | 0.17203 | 0.1755
| 0.95 | -0.049744 | 0.031731 | 0.092986 | 0.12474 | 0.14523 | 0.1564 | 0.16412 | 0.16877 | 0.17655 | 0.17759 | 0.17996 |  | 0.95 | -0.049744 | 0.031731 | 0.092986 | 0.12474 | 0.14523 | 0.1564 | 0.16412 | 0.16877 | 0.17655 | 0.17759 | 0.17996
| 1 | -0.050552 | 0.03424 | 0.098726 | 0.13044 | 0.1498 | 0.16063 | 0.17044 | 0.17529 | 0.18087 | 0.1833 | 0.18402 |  | 1 | -0.050552 | 0.03424 | 0.098726 | 0.13044 | 0.1498 | 0.16063 | 0.17044 | 0.17529 | 0.18087 | 0.1833 | 0.18402
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0018549 | -0.0030959 | -0.0041023 | -0.0049054 | -0.0052577 | -0.0057591 | -0.0061612 | -0.0064896 | -0.0069228 | -0.0071505 | -0.0073457 |  | 0.05 | -0.0018549 | -0.0030959 | -0.0041023 | -0.0049054 | -0.0052577 | -0.0057591 | -0.0061612 | -0.0064896 | -0.0069228 | -0.0071505 | -0.0073457
| 0.1 | -0.00064836 | -0.0036325 | -0.0056861 | -0.0072769 | -0.008587 | -0.0092827 | -0.0098762 | -0.010462 | -0.010684 | -0.011197 | -0.01109 |  | 0.1 | -0.00064836 | -0.0036325 | -0.0056861 | -0.0072769 | -0.008587 | -0.0092827 | -0.0098762 | -0.010462 | -0.010684 | -0.011197 | -0.01109
| 0.15 | 0.00038427 | -0.0041459 | -0.0069051 | -0.0086441 | -0.010348 | -0.011446 | -0.01228 | -0.012477 | -0.013889 | -0.013661 | -0.013483 |  | 0.15 | 0.00038427 | -0.0041459 | -0.0069051 | -0.0086441 | -0.010348 | -0.011446 | -0.01228 | -0.012477 | -0.013889 | -0.013661 | -0.013483
| 0.2 | 0.00083302 | -0.0047245 | -0.0083531 | -0.009259 | -0.012108 | -0.013279 | -0.014229 | -0.014493 | -0.015627 | -0.016125 | -0.015875 |  | 0.2 | 0.00083302 | -0.0047245 | -0.0083531 | -0.009259 | -0.012108 | -0.013279 | -0.014229 | -0.014493 | -0.015627 | -0.016125 | -0.015875
| 0.25 | 0.0013773 | -0.0053032 | -0.0087943 | -0.010936 | -0.014213 | -0.014795 | -0.016177 | -0.016508 | -0.017365 | -0.017366 | -0.018268 |  | 0.25 | 0.0013773 | -0.0053032 | -0.0087943 | -0.010936 | -0.014213 | -0.014795 | -0.016177 | -0.016508 | -0.017365 | -0.017366 | -0.018268
| 0.3 | 0.0014568 | -0.0060074 | -0.01041 | -0.012614 | -0.016766 | -0.017731 | -0.017916 | -0.018524 | -0.018872 | -0.019583 | -0.019877 |  | 0.3 | 0.0014568 | -0.0060074 | -0.01041 | -0.012614 | -0.016766 | -0.017731 | -0.017916 | -0.018524 | -0.018872 | -0.019583 | -0.019877
| 0.35 | 0.0014275 | -0.0067116 | -0.012139 | -0.014699 | -0.017808 | -0.019283 | -0.019607 | -0.02054 | -0.020736 | -0.021349 | -0.021646 |  | 0.35 | 0.0014275 | -0.0067116 | -0.012139 | -0.014699 | -0.017808 | -0.019283 | -0.019607 | -0.02054 | -0.020736 | -0.021349 | -0.021646
| 0.4 | 0.0013575 | -0.007085 | -0.012758 | -0.01615 | -0.018849 | -0.020103 | -0.020814 | -0.021757 | -0.022126 | -0.023115 | -0.02307 |  | 0.4 | 0.0013575 | -0.007085 | -0.012758 | -0.01615 | -0.018849 | -0.020103 | -0.020814 | -0.021757 | -0.022126 | -0.023115 | -0.02307
| 0.45 | 0.0015749 | -0.0074584 | -0.01378 | -0.017602 | -0.01989 | -0.020923 | -0.022024 | -0.022933 | -0.023406 | -0.02431 | -0.02448 |  | 0.45 | 0.0015749 | -0.0074584 | -0.01378 | -0.017602 | -0.01989 | -0.020923 | -0.022024 | -0.022933 | -0.023406 | -0.02431 | -0.02448
| 0.5 | 0.001489 | -0.0083044 | -0.013601 | -0.01858 | -0.020673 | -0.022367 | -0.023119 | -0.024374 | -0.024952 | -0.025118 | -0.025443 |  | 0.5 | 0.001489 | -0.0083044 | -0.013601 | -0.01858 | -0.020673 | -0.022367 | -0.023119 | -0.024374 | -0.024952 | -0.025118 | -0.025443
| 0.55 | 0.0012229 | -0.0091504 | -0.015434 | -0.019251 | -0.021627 | -0.023019 | -0.024345 | -0.025075 | -0.026026 | -0.026316 | -0.026993 |  | 0.55 | 0.0012229 | -0.0091504 | -0.015434 | -0.019251 | -0.021627 | -0.023019 | -0.024345 | -0.025075 | -0.026026 | -0.026316 | -0.026993
| 0.6 | 0.0012188 | -0.0099964 | -0.015804 | -0.019921 | -0.022341 | -0.023965 | -0.025177 | -0.026155 | -0.02727 | -0.02771 | -0.027784 |  | 0.6 | 0.0012188 | -0.0099964 | -0.015804 | -0.019921 | -0.022341 | -0.023965 | -0.025177 | -0.026155 | -0.02727 | -0.02771 | -0.027784
| 0.65 | 0.0013029 | -0.011399 | -0.016174 | -0.02047 | -0.023222 | -0.024897 | -0.02605 | -0.02697 | -0.027894 | -0.028443 | -0.02911 |  | 0.65 | 0.0013029 | -0.011399 | -0.016174 | -0.02047 | -0.023222 | -0.024897 | -0.02605 | -0.02697 | -0.027894 | -0.028443 | -0.02911
| 0.7 | 0.0010954 | -0.011326 | -0.017694 | -0.021 | -0.024145 | -0.025841 | -0.02636 | -0.028025 | -0.028926 | -0.029472 | -0.029909 |  | 0.7 | 0.0010954 | -0.011326 | -0.017694 | -0.021 | -0.024145 | -0.025841 | -0.02636 | -0.028025 | -0.028926 | -0.029472 | -0.029909
| 0.75 | 0.0011325 | -0.011873 | -0.0182 | -0.022092 | -0.024733 | -0.026375 | -0.02794 | -0.028779 | -0.029687 | -0.030413 | -0.031065 |  | 0.75 | 0.0011325 | -0.011873 | -0.0182 | -0.022092 | -0.024733 | -0.026375 | -0.02794 | -0.028779 | -0.029687 | -0.030413 | -0.031065
| 0.8 | 0.00099249 | -0.01242 | -0.018909 | -0.022787 | -0.025435 | -0.027234 | -0.02872 | -0.029689 | -0.030782 | -0.03144 | -0.032057 |  | 0.8 | 0.00099249 | -0.01242 | -0.018909 | -0.022787 | -0.025435 | -0.027234 | -0.02872 | -0.029689 | -0.030782 | -0.03144 | -0.032057
| 0.85 | 0.00073147 | -0.012704 | -0.019272 | -0.023128 | -0.025989 | -0.028062 | -0.029567 | -0.03079 | -0.031574 | -0.032538 | -0.033055 |  | 0.85 | 0.00073147 | -0.012704 | -0.019272 | -0.023128 | -0.025989 | -0.028062 | -0.029567 | -0.03079 | -0.031574 | -0.032538 | -0.033055
| 0.9 | 0.00096609 | -0.013019 | -0.019773 | -0.023834 | -0.026667 | -0.028865 | -0.030447 | -0.031626 | -0.032527 | -0.033367 | -0.033965 |  | 0.9 | 0.00096609 | -0.013019 | -0.019773 | -0.023834 | -0.026667 | -0.028865 | -0.030447 | -0.031626 | -0.032527 | -0.033367 | -0.033965
| 0.95 | 0.00094492 | -0.013754 | -0.020376 | -0.024165 | -0.027294 | -0.029626 | -0.031275 | -0.032478 | -0.033428 | -0.034286 | -0.035108 |  | 0.95 | 0.00094492 | -0.013754 | -0.020376 | -0.024165 | -0.027294 | -0.029626 | -0.031275 | -0.032478 | -0.033428 | -0.034286 | -0.035108
| 1 | 0.00084441 | -0.01449 | -0.020633 | -0.024785 | -0.027779 | -0.030271 | -0.031689 | -0.033524 | -0.034459 | -0.03472 | -0.035658 |  | 1 | 0.00084441 | -0.01449 | -0.020633 | -0.024785 | -0.027779 | -0.030271 | -0.031689 | -0.033524 | -0.034459 | -0.03472 | -0.035658
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS6_LS< (hidden)
If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0114 | 1.0181 | 1.0228 | 1.0258 | 1.0272 | 1.0273 | 1.0263 | 1.0244 | 1.0217 | 1.0184 | 1.0146
| 0.1 | 1.0331 | 1.0533 | 1.0694 | 1.0797 | 1.0853 | 1.0872 | 1.0862 | 1.0831 | 1.0784 | 1.0724 | 1.0654
| 0.15 | 1.0441 | 1.07 | 1.094 | 1.1092 | 1.1169 | 1.1189 | 1.1168 | 1.1121 | 1.106 | 1.0983 | 1.0896
| 0.2 | 1.0452 | 1.0765 | 1.1093 | 1.1288 | 1.1381 | 1.1401 | 1.1372 | 1.1309 | 1.1223 | 1.1131 | 1.1033
| 0.25 | 1.0393 | 1.0803 | 1.1174 | 1.1404 | 1.1508 | 1.1529 | 1.1495 | 1.1425 | 1.1342 | 1.1254 | 1.1154
| 0.3 | 1.0292 | 1.0806 | 1.1215 | 1.1474 | 1.1588 | 1.161 | 1.1574 | 1.1517 | 1.1439 | 1.1342 | 1.1234
| 0.35 | 1.0167 | 1.0787 | 1.1233 | 1.1516 | 1.164 | 1.1665 | 1.1647 | 1.159 | 1.1507 | 1.1404 | 1.129
| 0.4 | 1.003 | 1.0755 | 1.1253 | 1.1542 | 1.1679 | 1.1723 | 1.1704 | 1.1644 | 1.1556 | 1.145 | 1.1331
| 0.45 | 0.98887 | 1.0716 | 1.1266 | 1.1573 | 1.172 | 1.1766 | 1.1746 | 1.1684 | 1.1594 | 1.1485 | 1.1364
| 0.5 | 0.97472 | 1.0675 | 1.1272 | 1.1597 | 1.1751 | 1.1799 | 1.1779 | 1.1716 | 1.1624 | 1.1514 | 1.139
| 0.55 | 0.96089 | 1.0633 | 1.1272 | 1.1613 | 1.1774 | 1.1824 | 1.1806 | 1.1743 | 1.165 | 1.1538 | 1.1413
| 0.6 | 0.94756 | 1.0592 | 1.1268 | 1.1624 | 1.1791 | 1.1845 | 1.1828 | 1.1765 | 1.1672 | 1.156 | 1.1434
| 0.65 | 0.93484 | 1.0552 | 1.1262 | 1.1631 | 1.1805 | 1.1862 | 1.1847 | 1.1785 | 1.1692 | 1.1579 | 1.1453
| 0.7 | 0.92278 | 1.0515 | 1.1254 | 1.1636 | 1.1816 | 1.1878 | 1.1865 | 1.1804 | 1.1711 | 1.1597 | 1.147
| 0.75 | 0.91139 | 1.0479 | 1.1245 | 1.1639 | 1.1826 | 1.1891 | 1.1881 | 1.182 | 1.1728 | 1.1614 | 1.1485
| 0.8 | 0.90067 | 1.0445 | 1.1236 | 1.164 | 1.1835 | 1.1904 | 1.1896 | 1.1836 | 1.1744 | 1.1629 | 1.1499
| 0.85 | 0.89059 | 1.0414 | 1.1226 | 1.1642 | 1.1843 | 1.1916 | 1.191 | 1.1851 | 1.1758 | 1.1643 | 1.1512
| 0.9 | 0.88112 | 1.0385 | 1.1216 | 1.1642 | 1.185 | 1.1928 | 1.1923 | 1.1865 | 1.1772 | 1.1655 | 1.1524
| 0.95 | 0.87223 | 1.0357 | 1.1206 | 1.1643 | 1.1858 | 1.1939 | 1.1936 | 1.1878 | 1.1784 | 1.1667 | 1.1534
| 1 | 0.86389 | 1.0331 | 1.1197 | 1.1643 | 1.1865 | 1.195 | 1.1947 | 1.1889 | 1.1795 | 1.1677 | 1.1544
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| 0.05 | 1.3163 | 1.2977 | 1.2788 | 1.2601 | 1.2418 | 1.2237 | 1.2067 | 1.1894 | 1.1727 | 1.1565 | 1.1408
| 0.1 | 1.1812 | 1.1552 | 1.1292 | 1.1033 | 1.0781 | 1.0538 | 1.0312 | 1.0091 | 0.9882 | 0.96841 | 0.94953
| 0.15 | 1.0931 | 1.0616 | 1.0306 | 1.0007 | 0.97221 | 0.94527 | 0.92048 | 0.89666 | 0.87462 | 0.85403 | 0.83442
| 0.2 | 1.0303 | 0.99357 | 0.95859 | 0.92578 | 0.89555 | 0.86774 | 0.84201 | 0.81753 | 0.79538 | 0.77452 | 0.7552
| 0.25 | 0.98449 | 0.94076 | 0.90288 | 0.8684 | 0.83724 | 0.8085 | 0.78246 | 0.75802 | 0.73561 | 0.71502 | 0.69628
| 0.3 | 0.94981 | 0.89863 | 0.85817 | 0.82264 | 0.79048 | 0.76134 | 0.73508 | 0.71071 | 0.6885 | 0.66806 | 0.64947
| 0.35 | 0.92277 | 0.86403 | 0.82084 | 0.78451 | 0.75206 | 0.72225 | 0.69575 | 0.67142 | 0.64957 | 0.62949 | 0.61113
| 0.4 | 0.90054 | 0.83449 | 0.78939 | 0.75231 | 0.7192 | 0.68896 | 0.66251 | 0.63816 | 0.61662 | 0.59708 | 0.57905
| 0.45 | 0.88292 | 0.80906 | 0.7624 | 0.72408 | 0.69023 | 0.66029 | 0.63352 | 0.60949 | 0.58831 | 0.56893 | 0.55118
| 0.5 | 0.86818 | 0.78632 | 0.7385 | 0.69899 | 0.66488 | 0.63434 | 0.60777 | 0.58445 | 0.56334 | 0.54442 | 0.52758
| 0.55 | 0.85605 | 0.76654 | 0.71736 | 0.67672 | 0.64194 | 0.61171 | 0.58522 | 0.56187 | 0.5412 | 0.52287 | 0.5062
| 0.6 | 0.84499 | 0.74873 | 0.69808 | 0.65655 | 0.62123 | 0.59096 | 0.56487 | 0.54165 | 0.52172 | 0.50363 | 0.48722
| 0.65 | 0.83611 | 0.73284 | 0.6803 | 0.63797 | 0.60236 | 0.57235 | 0.5464 | 0.52389 | 0.50408 | 0.48628 | 0.47042
| 0.7 | 0.82829 | 0.71805 | 0.66376 | 0.62098 | 0.5853 | 0.55534 | 0.52992 | 0.50774 | 0.48792 | 0.47063 | 0.45545
| 0.75 | 0.82146 | 0.70428 | 0.64895 | 0.6052 | 0.5695 | 0.53952 | 0.51426 | 0.49255 | 0.4732 | 0.45644 | 0.4413
| 0.8 | 0.81492 | 0.69181 | 0.63505 | 0.59044 | 0.55457 | 0.52532 | 0.50035 | 0.47878 | 0.46007 | 0.44364 | 0.42871
| 0.85 | 0.80951 | 0.68024 | 0.62171 | 0.5769 | 0.54093 | 0.51179 | 0.4873 | 0.46621 | 0.44772 | 0.43155 | 0.41708
| 0.9 | 0.8048 | 0.66943 | 0.60949 | 0.56396 | 0.52859 | 0.49954 | 0.47526 | 0.45445 | 0.43641 | 0.42044 | 0.40604
| 0.95 | 0.8005 | 0.659 | 0.59766 | 0.55194 | 0.51663 | 0.48811 | 0.46392 | 0.44366 | 0.42583 | 0.41039 | 0.39624
| 1 | 0.79612 | 0.64947 | 0.58669 | 0.54087 | 0.50552 | 0.47698 | 0.45362 | 0.43359 | 0.41605 | 0.40061 | 0.387
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0037694 | -0.0023591 | -0.0010448 | 0.00019142 | 0.0013267 | 0.0023733 | 0.0033013 | 0.0041339 | 0.0048942 | 0.0055883 | 0.0061953
| 0.1 | -0.0017279 | 0.00024194 | 0.0019301 | 0.0033684 | 0.0045309 | 0.0055545 | 0.0063843 | 0.0070557 | 0.007633 | 0.0081363 | 0.0085427
| 0.15 | -0.0013232 | 0.0014271 | 0.0033883 | 0.0048562 | 0.0059663 | 0.0068918 | 0.0075551 | 0.0080677 | 0.008544 | 0.0089408 | 0.0091547
| 0.2 | -0.0018611 | 0.0020082 | 0.0041231 | 0.0055317 | 0.0066389 | 0.0074717 | 0.008074 | 0.0084963 | 0.0088659 | 0.0091414 | 0.0093216
| 0.25 | -0.002429 | 0.0021935 | 0.0045512 | 0.0060222 | 0.0070537 | 0.0078753 | 0.0083696 | 0.0088914 | 0.0091167 | 0.0093714 | 0.009459
| 0.3 | -0.0031336 | 0.0024584 | 0.0047105 | 0.0063562 | 0.0074502 | 0.0082125 | 0.0087798 | 0.0090279 | 0.0093021 | 0.0094699 | 0.0094547
| 0.35 | -0.0039985 | 0.0025555 | 0.0050451 | 0.0067138 | 0.007857 | 0.0085881 | 0.0090043 | 0.0091986 | 0.0093668 | 0.009484 | 0.0094036
| 0.4 | -0.004661 | 0.0026586 | 0.0053463 | 0.007043 | 0.0081944 | 0.0088271 | 0.009182 | 0.0093152 | 0.0093534 | 0.0093927 | 0.0093163
| 0.45 | -0.0050866 | 0.00269 | 0.0056474 | 0.0073455 | 0.0084651 | 0.0089971 | 0.0092309 | 0.0093706 | 0.0094035 | 0.0093185 | 0.0092331
| 0.5 | -0.0055925 | 0.0028097 | 0.0059281 | 0.0077004 | 0.0086279 | 0.0091084 | 0.0092929 | 0.0093703 | 0.0092 | 0.0091614 | 0.0090523
| 0.55 | -0.0061852 | 0.0029995 | 0.0061232 | 0.0079993 | 0.0088219 | 0.0092473 | 0.0092908 | 0.009206 | 0.0091238 | 0.0089644 | 0.0088725
| 0.6 | -0.0065539 | 0.003065 | 0.0064031 | 0.0082 | 0.0088665 | 0.0091774 | 0.0092423 | 0.0090886 | 0.0090029 | 0.0088871 | 0.0086334
| 0.65 | -0.0067694 | 0.0031483 | 0.0066917 | 0.0083508 | 0.0089314 | 0.0091984 | 0.0091237 | 0.0090927 | 0.0088739 | 0.0086813 | 0.008442
| 0.7 | -0.0071957 | 0.0032909 | 0.0069597 | 0.0084229 | 0.0090026 | 0.009115 | 0.0090145 | 0.0089086 | 0.0086363 | 0.0085375 | 0.008303
| 0.75 | -0.0074499 | 0.0034566 | 0.0071718 | 0.00853 | 0.0089509 | 0.0090219 | 0.0089227 | 0.0087542 | 0.0084804 | 0.0082978 | 0.0081167
| 0.8 | -0.0077177 | 0.0036726 | 0.0073618 | 0.0086283 | 0.008954 | 0.0089591 | 0.0087949 | 0.0085532 | 0.0084159 | 0.0081233 | 0.0079164
| 0.85 | -0.0079204 | 0.0038198 | 0.0074967 | 0.008721 | 0.0089335 | 0.0088603 | 0.0086862 | 0.008389 | 0.0081988 | 0.0080319 | 0.0077538
| 0.9 | -0.0081054 | 0.003931 | 0.0076026 | 0.008675 | 0.0088773 | 0.008777 | 0.0085071 | 0.0082856 | 0.0080686 | 0.0078187 | 0.0076578
| 0.95 | -0.0082425 | 0.0041216 | 0.0077754 | 0.008721 | 0.0087869 | 0.0086182 | 0.0083803 | 0.0080617 | 0.0079087 | 0.0076527 | 0.0074534
| 1 | -0.0084072 | 0.0043186 | 0.0077694 | 0.0086941 | 0.0087264 | 0.0084649 | 0.0082817 | 0.0079599 | 0.0077343 | 0.0074498 | 0.007259
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0014737 | 0.0015333 | 0.0015977 | 0.0016652 | 0.0017046 | 0.0017665 | 0.0018137 | 0.0018669 | 0.0019341 | 0.0019705 | 0.0020054
| 0.1 | 0.0017291 | 0.0018023 | 0.0018728 | 0.0019334 | 0.0019846 | 0.0020115 | 0.0020494 | 0.0020868 | 0.0021075 | 0.0021233 | 0.0021335
| 0.15 | 0.0017507 | 0.001864 | 0.0019442 | 0.0019903 | 0.0020284 | 0.0020417 | 0.0020654 | 0.0020783 | 0.0020798 | 0.002086 | 0.002077
| 0.2 | 0.001693 | 0.0018541 | 0.0019345 | 0.0019789 | 0.0019962 | 0.0020083 | 0.0020237 | 0.0020153 | 0.0020161 | 0.0020001 | 0.001988
| 0.25 | 0.001578 | 0.0018145 | 0.0019017 | 0.0019297 | 0.0019505 | 0.0019529 | 0.0019637 | 0.0019505 | 0.0019429 | 0.0019212 | 0.0019042
| 0.3 | 0.0014676 | 0.0017732 | 0.0018627 | 0.0018906 | 0.0018923 | 0.001904 | 0.0019019 | 0.0018977 | 0.0018808 | 0.0018641 | 0.0018465
| 0.35 | 0.0013817 | 0.0017302 | 0.0018084 | 0.0018413 | 0.0018656 | 0.0018648 | 0.0018607 | 0.0018507 | 0.0018261 | 0.0018044 | 0.0017908
| 0.4 | 0.0012882 | 0.0016918 | 0.0017698 | 0.0018087 | 0.0018326 | 0.0018398 | 0.001834 | 0.0018074 | 0.001785 | 0.0017617 | 0.0017233
| 0.45 | 0.001192 | 0.0016621 | 0.001731 | 0.0017906 | 0.0018073 | 0.0018051 | 0.0017913 | 0.0017717 | 0.0017374 | 0.001705 | 0.0016767
| 0.5 | 0.001121 | 0.0016302 | 0.0017053 | 0.0017552 | 0.0017842 | 0.0017749 | 0.0017602 | 0.0017318 | 0.0016865 | 0.0016633 | 0.001629
| 0.55 | 0.0010677 | 0.0015915 | 0.0016959 | 0.0017446 | 0.0017555 | 0.0017506 | 0.0017307 | 0.0016837 | 0.001652 | 0.0016181 | 0.0015863
| 0.6 | 0.0010127 | 0.0015608 | 0.0016712 | 0.0017316 | 0.0017411 | 0.0017211 | 0.0016901 | 0.0016468 | 0.001616 | 0.0015729 | 0.0015484
| 0.65 | 0.00094744 | 0.0015441 | 0.0016581 | 0.0017153 | 0.001711 | 0.0016871 | 0.0016623 | 0.0016141 | 0.0015837 | 0.0015425 | 0.0014964
| 0.7 | 0.00091863 | 0.0015216 | 0.0016428 | 0.001701 | 0.0016897 | 0.001656 | 0.0016287 | 0.0015754 | 0.0015416 | 0.0015029 | 0.0014723
| 0.75 | 0.00087765 | 0.0015031 | 0.0016307 | 0.0016895 | 0.0016773 | 0.0016398 | 0.0015919 | 0.0015514 | 0.0015153 | 0.0014715 | 0.0014312
| 0.8 | 0.0008427 | 0.0014777 | 0.0016289 | 0.0016624 | 0.0016412 | 0.0016082 | 0.0015679 | 0.0015206 | 0.0014726 | 0.0014399 | 0.0013886
| 0.85 | 0.00081939 | 0.0014705 | 0.0016159 | 0.0016509 | 0.0016276 | 0.001582 | 0.0015372 | 0.0014944 | 0.0014467 | 0.0014041 | 0.0013651
| 0.9 | 0.00077725 | 0.0014571 | 0.0016131 | 0.0016326 | 0.0015949 | 0.0015535 | 0.0015102 | 0.0014641 | 0.001417 | 0.0013749 | 0.0013383
| 0.95 | 0.00075172 | 0.0014453 | 0.0016018 | 0.0016116 | 0.0015772 | 0.0015269 | 0.00148 | 0.001435 | 0.001391 | 0.0013494 | 0.0013017
| 1 | 0.00072291 | 0.0014374 | 0.0015932 | 0.0015903 | 0.0015615 | 0.0015048 | 0.0014664 | 0.0014019 | 0.0013656 | 0.0013252 | 0.0012808
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.4903 | 1.6209 | 1.7319 | 1.8253 | 1.9071 | 1.9733 | 2.0245 | 2.0718 | 2.1158 | 2.1528 | 2.1847
| 0.1 | 1.601 | 1.9268 | 2.1814 | 2.3864 | 2.5454 | 2.6756 | 2.785 | 2.8708 | 2.9435 | 2.9922 | 3.0506
| 0.15 | 1.5883 | 2.127 | 2.5244 | 2.8419 | 3.0813 | 3.247 | 3.4052 | 3.5182 | 3.5959 | 3.6722 | 3.7526
| 0.2 | 1.5509 | 2.2899 | 2.8185 | 3.2084 | 3.5091 | 3.7994 | 3.9143 | 4.1015 | 4.1984 | 4.2278 | 4.3039
| 0.25 | 1.5031 | 2.4406 | 3.0819 | 3.5558 | 3.9126 | 4.1244 | 4.3728 | 4.554 | 4.6527 | 4.7834 | 4.8398
| 0.3 | 1.4564 | 2.6163 | 3.2951 | 3.8767 | 4.2869 | 4.5471 | 4.7356 | 5.0009 | 5.1303 | 5.2368 | 5.3211
| 0.35 | 1.4148 | 2.7048 | 3.5676 | 4.1444 | 4.6355 | 4.9679 | 5.2773 | 5.4052 | 5.5824 | 5.6716 | 5.7817
| 0.4 | 1.3846 | 2.9013 | 3.7884 | 4.4642 | 4.9639 | 5.2406 | 5.6038 | 5.8095 | 5.9767 | 6.1 | 6.1954
| 0.45 | 1.3535 | 2.9492 | 4.0013 | 4.7416 | 5.2685 | 5.665 | 5.949 | 6.1726 | 6.3462 | 6.4746 | 6.5742
| 0.5 | 1.3265 | 3.0577 | 4.2049 | 4.9955 | 5.5591 | 5.9734 | 6.2798 | 6.5164 | 6.6911 | 6.836 | 6.937
| 0.55 | 1.3036 | 3.168 | 4.4022 | 5.2392 | 5.8222 | 6.2711 | 6.5853 | 6.8424 | 7.0252 | 7.1705 | 7.2792
| 0.6 | 1.2903 | 3.2465 | 4.5766 | 5.4717 | 6.0886 | 6.55 | 6.8871 | 7.142 | 7.3432 | 7.4899 | 7.6026
| 0.65 | 1.2735 | 3.3893 | 4.8079 | 5.6921 | 6.336 | 6.8193 | 7.1632 | 7.4368 | 7.6428 | 7.7946 | 7.9131
| 0.7 | 1.2571 | 3.5069 | 4.9246 | 5.8963 | 6.5699 | 7.0744 | 7.4372 | 7.7187 | 7.932 | 8.0913 | 8.215
| 0.75 | 1.2425 | 3.6372 | 5.1168 | 6.1075 | 6.8118 | 7.317 | 7.6895 | 7.9803 | 8.2051 | 8.3755 | 8.5055
| 0.8 | 1.2378 | 3.7201 | 5.2787 | 6.3021 | 7.0275 | 7.5559 | 7.9489 | 8.2426 | 8.4789 | 8.6553 | 8.7806
| 0.85 | 1.2257 | 3.8332 | 5.4343 | 6.5011 | 7.2367 | 7.781 | 8.1872 | 8.498 | 8.7298 | 8.9187 | 9.0533
| 0.9 | 1.2149 | 3.9333 | 5.5896 | 6.6766 | 7.446 | 8.0045 | 8.4211 | 8.7408 | 8.9841 | 9.1654 | 9.3075
| 0.95 | 1.2061 | 4.0561 | 5.749 | 6.8507 | 7.6432 | 8.2222 | 8.6482 | 8.9781 | 9.2276 | 9.4215 | 9.5575
| 1 | 1.2059 | 4.1427 | 5.8845 | 7.0314 | 7.8339 | 8.4238 | 8.8713 | 9.213 | 9.4668 | 9.6605 | 9.8052
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.023371 | -0.019987 | -0.015913 | -0.013444 | -0.010041 | -0.0067524 | -0.0046334 | -0.0020859 | 0.00050047 | 0.003071 | 0.0050557
| 0.1 | -0.021021 | -0.014847 | -0.0091611 | -0.003508 | 0.0010274 | 0.0081778 | 0.0088793 | 0.011324 | 0.012526 | 0.016956 | 0.021502
| 0.15 | -0.021084 | -0.010282 | -0.0016696 | 0.0065332 | 0.010876 | 0.018656 | 0.021474 | 0.024733 | 0.024551 | 0.025329 | 0.033935
| 0.2 | -0.022132 | -0.0060352 | 0.0058219 | 0.014939 | 0.022991 | 0.029943 | 0.03407 | 0.037438 | 0.036576 | 0.042537 | 0.046368
| 0.25 | -0.027205 | -0.0060377 | 0.011325 | 0.023044 | 0.032502 | 0.036726 | 0.046665 | 0.050142 | 0.049187 | 0.053788 | 0.061933
| 0.3 | -0.031357 | -0.0017135 | 0.018354 | 0.029028 | 0.042736 | 0.051761 | 0.057741 | 0.062847 | 0.064771 | 0.070831 | 0.081578
| 0.35 | -0.033005 | 0.00031274 | 0.023285 | 0.038453 | 0.05297 | 0.061272 | 0.068437 | 0.074981 | 0.080355 | 0.08417 | 0.092117
| 0.4 | -0.035808 | -0.0051778 | 0.028216 | 0.047879 | 0.062707 | 0.073911 | 0.079133 | 0.087244 | 0.089337 | 0.09751 | 0.10105
| 0.45 | -0.039937 | 0.0009599 | 0.034179 | 0.057304 | 0.071162 | 0.08634 | 0.092485 | 0.098308 | 0.10148 | 0.10851 | 0.11031
| 0.5 | -0.042294 | 0.0050034 | 0.040475 | 0.068948 | 0.079391 | 0.092428 | 0.10198 | 0.1087 | 0.11488 | 0.11731 | 0.11982
| 0.55 | -0.042467 | 0.0046088 | 0.046772 | 0.074296 | 0.090437 | 0.10386 | 0.11133 | 0.11658 | 0.12368 | 0.12474 | 0.12933
| 0.6 | -0.043606 | 0.0079407 | 0.053069 | 0.079094 | 0.098212 | 0.11103 | 0.11972 | 0.12639 | 0.13136 | 0.13456 | 0.13541
| 0.65 | -0.047123 | 0.0086024 | 0.059365 | 0.087773 | 0.1068 | 0.11903 | 0.12733 | 0.13517 | 0.13924 | 0.14053 | 0.14326
| 0.7 | -0.046108 | 0.013738 | 0.065662 | 0.095989 | 0.11575 | 0.12782 | 0.13494 | 0.13936 | 0.14529 | 0.15089 | 0.15071
| 0.75 | -0.046866 | 0.014868 | 0.071959 | 0.10227 | 0.12253 | 0.13318 | 0.14144 | 0.1455 | 0.15161 | 0.15476 | 0.15683
| 0.8 | -0.048439 | 0.018825 | 0.076606 | 0.11174 | 0.12858 | 0.13891 | 0.14835 | 0.15437 | 0.15799 | 0.16245 | 0.16487
| 0.85 | -0.048778 | 0.016005 | 0.085915 | 0.11769 | 0.13714 | 0.14582 | 0.15394 | 0.15893 | 0.16346 | 0.16675 | 0.16828
| 0.9 | -0.049446 | 0.023868 | 0.090116 | 0.12134 | 0.1435 | 0.152 | 0.16002 | 0.16694 | 0.16927 | 0.17203 | 0.1755
| 0.95 | -0.049744 | 0.031731 | 0.092986 | 0.12474 | 0.14523 | 0.1564 | 0.16412 | 0.16877 | 0.17655 | 0.17759 | 0.17996
| 1 | -0.050552 | 0.03424 | 0.098726 | 0.13044 | 0.1498 | 0.16063 | 0.17044 | 0.17529 | 0.18087 | 0.1833 | 0.18402
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0018549 | -0.0030959 | -0.0041023 | -0.0049054 | -0.0052577 | -0.0057591 | -0.0061612 | -0.0064896 | -0.0069228 | -0.0071505 | -0.0073457
| 0.1 | -0.00064836 | -0.0036325 | -0.0056861 | -0.0072769 | -0.008587 | -0.0092827 | -0.0098762 | -0.010462 | -0.010684 | -0.011197 | -0.01109
| 0.15 | 0.00038427 | -0.0041459 | -0.0069051 | -0.0086441 | -0.010348 | -0.011446 | -0.01228 | -0.012477 | -0.013889 | -0.013661 | -0.013483
| 0.2 | 0.00083302 | -0.0047245 | -0.0083531 | -0.009259 | -0.012108 | -0.013279 | -0.014229 | -0.014493 | -0.015627 | -0.016125 | -0.015875
| 0.25 | 0.0013773 | -0.0053032 | -0.0087943 | -0.010936 | -0.014213 | -0.014795 | -0.016177 | -0.016508 | -0.017365 | -0.017366 | -0.018268
| 0.3 | 0.0014568 | -0.0060074 | -0.01041 | -0.012614 | -0.016766 | -0.017731 | -0.017916 | -0.018524 | -0.018872 | -0.019583 | -0.019877
| 0.35 | 0.0014275 | -0.0067116 | -0.012139 | -0.014699 | -0.017808 | -0.019283 | -0.019607 | -0.02054 | -0.020736 | -0.021349 | -0.021646
| 0.4 | 0.0013575 | -0.007085 | -0.012758 | -0.01615 | -0.018849 | -0.020103 | -0.020814 | -0.021757 | -0.022126 | -0.023115 | -0.02307
| 0.45 | 0.0015749 | -0.0074584 | -0.01378 | -0.017602 | -0.01989 | -0.020923 | -0.022024 | -0.022933 | -0.023406 | -0.02431 | -0.02448
| 0.5 | 0.001489 | -0.0083044 | -0.013601 | -0.01858 | -0.020673 | -0.022367 | -0.023119 | -0.024374 | -0.024952 | -0.025118 | -0.025443
| 0.55 | 0.0012229 | -0.0091504 | -0.015434 | -0.019251 | -0.021627 | -0.023019 | -0.024345 | -0.025075 | -0.026026 | -0.026316 | -0.026993
| 0.6 | 0.0012188 | -0.0099964 | -0.015804 | -0.019921 | -0.022341 | -0.023965 | -0.025177 | -0.026155 | -0.02727 | -0.02771 | -0.027784
| 0.65 | 0.0013029 | -0.011399 | -0.016174 | -0.02047 | -0.023222 | -0.024897 | -0.02605 | -0.02697 | -0.027894 | -0.028443 | -0.02911
| 0.7 | 0.0010954 | -0.011326 | -0.017694 | -0.021 | -0.024145 | -0.025841 | -0.02636 | -0.028025 | -0.028926 | -0.029472 | -0.029909
| 0.75 | 0.0011325 | -0.011873 | -0.0182 | -0.022092 | -0.024733 | -0.026375 | -0.02794 | -0.028779 | -0.029687 | -0.030413 | -0.031065
| 0.8 | 0.00099249 | -0.01242 | -0.018909 | -0.022787 | -0.025435 | -0.027234 | -0.02872 | -0.029689 | -0.030782 | -0.03144 | -0.032057
| 0.85 | 0.00073147 | -0.012704 | -0.019272 | -0.023128 | -0.025989 | -0.028062 | -0.029567 | -0.03079 | -0.031574 | -0.032538 | -0.033055
| 0.9 | 0.00096609 | -0.013019 | -0.019773 | -0.023834 | -0.026667 | -0.028865 | -0.030447 | -0.031626 | -0.032527 | -0.033367 | -0.033965
| 0.95 | 0.00094492 | -0.013754 | -0.020376 | -0.024165 | -0.027294 | -0.029626 | -0.031275 | -0.032478 | -0.033428 | -0.034286 | -0.035108
| 1 | 0.00084441 | -0.01449 | -0.020633 | -0.024785 | -0.027779 | -0.030271 | -0.031689 | -0.033524 | -0.034459 | -0.03472 | -0.035658
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-25.25) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-139.76))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-25.25) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-139.76))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS7_LS< (hidden)
If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 1.0121 | 1.0241 | 1.0331 | 1.0396 | 1.044 | 1.0465 | 1.0474 | 1.0468 | 1.0451 | 1.0411 | 1.0378
| 0.1 | 1.0313 | 1.0544 | 1.0738 | 1.0876 | 1.0954 | 1.0988 | 1.0987 | 1.0961 | 1.0916 | 1.0852 | 1.0784
| 0.15 | 1.0285 | 1.0661 | 1.0944 | 1.1125 | 1.1223 | 1.1262 | 1.1256 | 1.122 | 1.1161 | 1.1083 | 1.0997
| 0.2 | 1.0186 | 1.0675 | 1.1054 | 1.128 | 1.1397 | 1.1437 | 1.1426 | 1.1379 | 1.1308 | 1.1219 | 1.112
| 0.25 | 1.0036 | 1.0645 | 1.1108 | 1.1372 | 1.1502 | 1.1545 | 1.1531 | 1.1479 | 1.14 | 1.1303 | 1.1196
| 0.3 | 0.98584 | 1.0596 | 1.1133 | 1.1428 | 1.157 | 1.1617 | 1.1601 | 1.1546 | 1.1463 | 1.1362 | 1.125
| 0.35 | 0.96739 | 1.0541 | 1.1142 | 1.1463 | 1.1616 | 1.1666 | 1.1652 | 1.1596 | 1.1511 | 1.1408 | 1.1294
| 0.4 | 0.94923 | 1.0487 | 1.1142 | 1.1485 | 1.1648 | 1.1704 | 1.1692 | 1.1636 | 1.1551 | 1.1447 | 1.133
| 0.45 | 0.93186 | 1.0435 | 1.1136 | 1.1499 | 1.1673 | 1.1734 | 1.1725 | 1.1671 | 1.1586 | 1.148 | 1.1361
| 0.5 | 0.91555 | 1.0387 | 1.1127 | 1.1508 | 1.1692 | 1.176 | 1.1755 | 1.1701 | 1.1616 | 1.1509 | 1.1389
| 0.55 | 0.90037 | 1.0343 | 1.1117 | 1.1515 | 1.171 | 1.1784 | 1.1781 | 1.1729 | 1.1643 | 1.1534 | 1.1412
| 0.6 | 0.88633 | 1.0302 | 1.1105 | 1.152 | 1.1726 | 1.1806 | 1.1806 | 1.1753 | 1.1666 | 1.1557 | 1.1433
| 0.65 | 0.8734 | 1.0266 | 1.1094 | 1.1525 | 1.1741 | 1.1826 | 1.1827 | 1.1775 | 1.1687 | 1.1576 | 1.145
| 0.7 | 0.86149 | 1.0232 | 1.1083 | 1.153 | 1.1756 | 1.1845 | 1.1847 | 1.1794 | 1.1705 | 1.1593 | 1.1466
| 0.75 | 0.85053 | 1.0201 | 1.1073 | 1.1536 | 1.177 | 1.1862 | 1.1865 | 1.1811 | 1.1721 | 1.1607 | 1.1479
| 0.8 | 0.84044 | 1.0172 | 1.1064 | 1.1541 | 1.1783 | 1.1877 | 1.188 | 1.1826 | 1.1735 | 1.162 | 1.1491
| 0.85 | 0.83114 | 1.0146 | 1.1055 | 1.1547 | 1.1795 | 1.1891 | 1.1894 | 1.1839 | 1.1747 | 1.1632 | 1.1501
| 0.9 | 0.82255 | 1.0122 | 1.1049 | 1.1554 | 1.1806 | 1.1904 | 1.1907 | 1.1851 | 1.1758 | 1.1642 | 1.1511
| 0.95 | 0.81461 | 1.0099 | 1.1043 | 1.156 | 1.1816 | 1.1915 | 1.1918 | 1.1862 | 1.1769 | 1.1652 | 1.152
| 1 | 0.80726 | 1.0078 | 1.1038 | 1.1566 | 1.1826 | 1.1925 | 1.1928 | 1.1872 | 1.1778 | 1.166 | 1.1528
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| 0.05 | 1.5278 | 1.4974 | 1.4711 | 1.4452 | 1.4198 | 1.3951 | 1.3713 | 1.3492 | 1.327 | 1.3119 | 1.2915
| 0.1 | 1.372 | 1.3313 | 1.2943 | 1.2595 | 1.2261 | 1.1951 | 1.1662 | 1.1388 | 1.1128 | 1.0914 | 1.0683
| 0.15 | 1.2732 | 1.222 | 1.1787 | 1.1392 | 1.1029 | 1.0693 | 1.0385 | 1.0095 | 0.98255 | 0.95943 | 0.936
| 0.2 | 1.2062 | 1.1437 | 1.0956 | 1.0535 | 1.0149 | 0.97994 | 0.94837 | 0.91866 | 0.89175 | 0.86819 | 0.84511
| 0.25 | 1.1578 | 1.0839 | 1.0317 | 0.98748 | 0.94789 | 0.91194 | 0.87944 | 0.84961 | 0.82282 | 0.79942 | 0.77653
| 0.3 | 1.1225 | 1.0353 | 0.98046 | 0.93448 | 0.8934 | 0.85662 | 0.82409 | 0.79452 | 0.76776 | 0.74461 | 0.72297
| 0.35 | 1.0954 | 0.99573 | 0.93796 | 0.88995 | 0.84761 | 0.81046 | 0.77804 | 0.74848 | 0.72246 | 0.69998 | 0.67863
| 0.4 | 1.074 | 0.96206 | 0.90112 | 0.85161 | 0.80837 | 0.7708 | 0.73863 | 0.70985 | 0.68432 | 0.66215 | 0.64183
| 0.45 | 1.0559 | 0.93289 | 0.8694 | 0.81792 | 0.77392 | 0.73668 | 0.70464 | 0.67623 | 0.65136 | 0.63017 | 0.60992
| 0.5 | 1.0418 | 0.90729 | 0.84085 | 0.78755 | 0.74354 | 0.70628 | 0.67478 | 0.64717 | 0.62294 | 0.60192 | 0.58264
| 0.55 | 1.0299 | 0.88416 | 0.81511 | 0.76058 | 0.71637 | 0.67957 | 0.64866 | 0.62156 | 0.59783 | 0.57751 | 0.55859
| 0.6 | 1.0199 | 0.86367 | 0.7917 | 0.7361 | 0.69198 | 0.65557 | 0.62511 | 0.59883 | 0.5756 | 0.55555 | 0.53747
| 0.65 | 1.0105 | 0.84486 | 0.77035 | 0.71405 | 0.67005 | 0.63403 | 0.60418 | 0.5781 | 0.55572 | 0.53599 | 0.51843
| 0.7 | 1.0031 | 0.82769 | 0.75029 | 0.69359 | 0.64979 | 0.61442 | 0.58469 | 0.55938 | 0.53777 | 0.51868 | 0.5015
| 0.75 | 0.99662 | 0.81151 | 0.73175 | 0.67495 | 0.63134 | 0.59643 | 0.56768 | 0.5426 | 0.5213 | 0.50278 | 0.48602
| 0.8 | 0.99088 | 0.79642 | 0.71479 | 0.65741 | 0.61422 | 0.57999 | 0.5514 | 0.52742 | 0.50638 | 0.48811 | 0.47195
| 0.85 | 0.98508 | 0.78252 | 0.69896 | 0.64163 | 0.59841 | 0.56472 | 0.53699 | 0.51315 | 0.49274 | 0.47502 | 0.45883
| 0.9 | 0.98053 | 0.76912 | 0.68418 | 0.62654 | 0.58404 | 0.55057 | 0.52331 | 0.50022 | 0.47984 | 0.4626 | 0.44694
| 0.95 | 0.97654 | 0.75676 | 0.66988 | 0.61248 | 0.57031 | 0.53776 | 0.51082 | 0.48807 | 0.46826 | 0.45128 | 0.43592
| 1 | 0.97287 | 0.74495 | 0.65661 | 0.59926 | 0.55803 | 0.52562 | 0.49901 | 0.47675 | 0.45753 | 0.44053 | 0.42561
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0027122 | -0.00073244 | 0.00089025 | 0.002398 | 0.0037395 | 0.0048885 | 0.0056514 | 0.0064972 | 0.0074678 | 0.008047 | 0.0086098
| 0.1 | -0.00013552 | 0.0028741 | 0.0049102 | 0.0064696 | 0.0076174 | 0.0085232 | 0.0091444 | 0.0099098 | 0.010401 | 0.010823 | 0.011144
| 0.15 | -0.00012752 | 0.0041723 | 0.0063241 | 0.0076711 | 0.0087304 | 0.0094152 | 0.0099896 | 0.010555 | 0.010926 | 0.011208 | 0.01146
| 0.2 | -0.0011078 | 0.0046225 | 0.0067872 | 0.0080219 | 0.009014 | 0.0097936 | 0.010417 | 0.010854 | 0.011177 | 0.011367 | 0.011556
| 0.25 | -0.0019085 | 0.0047474 | 0.0068641 | 0.0082698 | 0.0093396 | 0.010179 | 0.010766 | 0.011156 | 0.011389 | 0.0115 | 0.011555
| 0.3 | -0.0028964 | 0.0048697 | 0.0068312 | 0.0085759 | 0.0098314 | 0.010601 | 0.011033 | 0.011295 | 0.011421 | 0.011417 | 0.011437
| 0.35 | -0.0037646 | 0.0048345 | 0.0070819 | 0.0089914 | 0.0102 | 0.010852 | 0.011197 | 0.011349 | 0.011364 | 0.011374 | 0.011279
| 0.4 | -0.0046612 | 0.004833 | 0.007457 | 0.0093637 | 0.010469 | 0.01105 | 0.011231 | 0.011318 | 0.011247 | 0.01114 | 0.01102
| 0.45 | -0.0053407 | 0.0048164 | 0.007779 | 0.0096494 | 0.010689 | 0.011146 | 0.011205 | 0.011209 | 0.011041 | 0.010874 | 0.010768
| 0.5 | -0.0056984 | 0.0047809 | 0.0081029 | 0.0099151 | 0.010781 | 0.011108 | 0.011075 | 0.011032 | 0.010921 | 0.010602 | 0.010453
| 0.55 | -0.0062064 | 0.0048012 | 0.0084172 | 0.010175 | 0.010859 | 0.010962 | 0.010981 | 0.010828 | 0.010625 | 0.010392 | 0.010216
| 0.6 | -0.0067427 | 0.0049165 | 0.0085995 | 0.010242 | 0.010885 | 0.010945 | 0.010857 | 0.01063 | 0.010407 | 0.010134 | 0.0099468
| 0.65 | -0.0071206 | 0.005107 | 0.0088816 | 0.01041 | 0.010813 | 0.010819 | 0.010683 | 0.010475 | 0.010169 | 0.0099134 | 0.0096815
| 0.7 | -0.0074494 | 0.0052172 | 0.0090916 | 0.010445 | 0.010717 | 0.010704 | 0.010504 | 0.010232 | 0.0099738 | 0.0097018 | 0.00944
| 0.75 | -0.0075628 | 0.0053608 | 0.009247 | 0.01048 | 0.010692 | 0.010588 | 0.010291 | 0.0099886 | 0.0096587 | 0.0094253 | 0.0092021
| 0.8 | -0.0079048 | 0.0055481 | 0.0093878 | 0.010383 | 0.010538 | 0.010382 | 0.010149 | 0.0098764 | 0.0095023 | 0.0091654 | 0.0089237
| 0.85 | -0.008162 | 0.0057555 | 0.0095186 | 0.010372 | 0.010508 | 0.010253 | 0.0099406 | 0.0096187 | 0.0092749 | 0.0090482 | 0.008791
| 0.9 | -0.0083437 | 0.0059877 | 0.009547 | 0.010401 | 0.010356 | 0.01007 | 0.0097221 | 0.0093788 | 0.0091145 | 0.0088002 | 0.0085412
| 0.95 | -0.0083803 | 0.0061117 | 0.009611 | 0.010322 | 0.010235 | 0.009967 | 0.0096005 | 0.0092562 | 0.0088916 | 0.0086434 | 0.0083843
| 1 | -0.0086689 | 0.0063409 | 0.0097141 | 0.010247 | 0.010106 | 0.0097295 | 0.0094422 | 0.0091039 | 0.008748 | 0.0085202 | 0.0082335
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0010945 | 0.0012237 | 0.0013339 | 0.0014365 | 0.0015241 | 0.0016088 | 0.001704 | 0.0017611 | 0.0018136 | 0.0018514 | 0.0018776
| 0.1 | 0.0012976 | 0.0015464 | 0.0016938 | 0.0017913 | 0.0018686 | 0.0019174 | 0.0019778 | 0.0020155 | 0.0020289 | 0.0020444 | 0.0020722
| 0.15 | 0.0012802 | 0.0016449 | 0.0018024 | 0.0018869 | 0.0019276 | 0.0019678 | 0.002004 | 0.0020105 | 0.0020253 | 0.0020317 | 0.0020334
| 0.2 | 0.0011562 | 0.0016767 | 0.0018055 | 0.0018785 | 0.0019173 | 0.0019484 | 0.0019837 | 0.0019897 | 0.0019901 | 0.0019865 | 0.0019842
| 0.25 | 0.00099848 | 0.0016692 | 0.001805 | 0.0018517 | 0.0019057 | 0.0019381 | 0.0019664 | 0.0019553 | 0.0019555 | 0.0019426 | 0.0019241
| 0.3 | 0.00088154 | 0.001626 | 0.0017652 | 0.0018436 | 0.001902 | 0.0019286 | 0.0019432 | 0.0019237 | 0.0019156 | 0.0018891 | 0.0018684
| 0.35 | 0.00079208 | 0.0016026 | 0.0017416 | 0.0018489 | 0.0019011 | 0.0019108 | 0.0019118 | 0.0018941 | 0.0018645 | 0.0018341 | 0.0018062
| 0.4 | 0.00070346 | 0.0015721 | 0.0017194 | 0.0018426 | 0.0018789 | 0.0018769 | 0.0018647 | 0.0018449 | 0.0018127 | 0.0017815 | 0.0017536
| 0.45 | 0.00063203 | 0.0015515 | 0.0017145 | 0.0018292 | 0.0018626 | 0.0018505 | 0.0018223 | 0.0018001 | 0.0017592 | 0.0017228 | 0.0016915
| 0.5 | 0.00054664 | 0.0015292 | 0.0017146 | 0.0018268 | 0.0018406 | 0.0018207 | 0.001791 | 0.0017482 | 0.0017023 | 0.0016751 | 0.0016275
| 0.55 | 0.00051702 | 0.001508 | 0.0017229 | 0.0018014 | 0.0018174 | 0.0017845 | 0.0017492 | 0.0017112 | 0.0016659 | 0.0016216 | 0.0015872
| 0.6 | 0.00046545 | 0.0014843 | 0.0017191 | 0.0017908 | 0.0017928 | 0.001751 | 0.0017135 | 0.0016685 | 0.0016165 | 0.0015816 | 0.0015406
| 0.65 | 0.00042737 | 0.0014747 | 0.0017165 | 0.0017698 | 0.0017632 | 0.0017215 | 0.0016745 | 0.0016255 | 0.0015784 | 0.0015312 | 0.0014902
| 0.7 | 0.00039113 | 0.001473 | 0.0017068 | 0.0017488 | 0.0017353 | 0.001686 | 0.001633 | 0.0015779 | 0.0015315 | 0.0014876 | 0.001447
| 0.75 | 0.00036346 | 0.0014654 | 0.0017069 | 0.0017391 | 0.0017031 | 0.0016542 | 0.0016023 | 0.0015496 | 0.0015058 | 0.0014557 | 0.0014213
| 0.8 | 0.00033499 | 0.0014633 | 0.0016893 | 0.0017156 | 0.0016773 | 0.0016261 | 0.0015626 | 0.0015102 | 0.0014617 | 0.001421 | 0.0013791
| 0.85 | 0.00031105 | 0.0014641 | 0.0016854 | 0.0016961 | 0.0016477 | 0.0015959 | 0.0015294 | 0.0014775 | 0.0014245 | 0.0013886 | 0.001352
| 0.9 | 0.00030965 | 0.0014613 | 0.0016763 | 0.0016729 | 0.0016171 | 0.0015602 | 0.0014966 | 0.0014449 | 0.0013962 | 0.0013598 | 0.0013194
| 0.95 | 0.00028898 | 0.0014639 | 0.0016566 | 0.0016471 | 0.0015893 | 0.0015273 | 0.001467 | 0.0014149 | 0.0013719 | 0.0013258 | 0.0012928
| 1 | 0.00025023 | 0.0014643 | 0.0016458 | 0.0016295 | 0.0015624 | 0.0014986 | 0.0014482 | 0.0013892 | 0.001341 | 0.0013053 | 0.0012635
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.4044 | 1.5599 | 1.6875 | 1.7931 | 1.882 | 1.9572 | 2.0199 | 2.0661 | 2.1127 | 2.1363 | 2.1686
| 0.1 | 1.4522 | 1.8093 | 2.0854 | 2.2996 | 2.4703 | 2.6085 | 2.7135 | 2.8047 | 2.8896 | 2.9369 | 2.987
| 0.15 | 1.4211 | 1.9837 | 2.3978 | 2.7126 | 2.9722 | 3.1645 | 3.2974 | 3.4346 | 3.522 | 3.587 | 3.6343
| 0.2 | 1.3767 | 2.1357 | 2.6885 | 3.0776 | 3.3829 | 3.6337 | 3.7939 | 4.0023 | 4.0711 | 4.1574 | 4.2215
| 0.25 | 1.3425 | 2.276 | 2.9304 | 3.4358 | 3.8111 | 4.0926 | 4.2431 | 4.4409 | 4.5824 | 4.651 | 4.6613
| 0.3 | 1.3076 | 2.4173 | 3.1867 | 3.719 | 4.123 | 4.4643 | 4.6946 | 4.8139 | 4.9676 | 5.0458 | 5.1087
| 0.35 | 1.2781 | 2.5576 | 3.4067 | 4.0355 | 4.3741 | 4.7572 | 4.9932 | 5.1914 | 5.3577 | 5.467 | 5.5553
| 0.4 | 1.2534 | 2.6694 | 3.6615 | 4.2604 | 4.707 | 5.091 | 5.3458 | 5.5649 | 5.729 | 5.8411 | 5.9292
| 0.45 | 1.2397 | 2.8062 | 3.8711 | 4.5053 | 4.9982 | 5.3961 | 5.6805 | 5.8928 | 6.0766 | 6.1745 | 6.2962
| 0.5 | 1.2229 | 2.9375 | 4.0137 | 4.7501 | 5.2758 | 5.6829 | 5.9772 | 6.2126 | 6.3933 | 6.5191 | 6.6343
| 0.55 | 1.2071 | 3.0336 | 4.1723 | 4.9704 | 5.5434 | 5.9638 | 6.2711 | 6.5212 | 6.7012 | 6.8253 | 6.9447
| 0.6 | 1.1934 | 3.147 | 4.3472 | 5.1974 | 5.7809 | 6.2212 | 6.5429 | 6.8037 | 6.9898 | 7.1423 | 7.2489
| 0.65 | 1.1883 | 3.2559 | 4.5265 | 5.393 | 5.9976 | 6.4639 | 6.807 | 7.0743 | 7.2791 | 7.4169 | 7.5412
| 0.7 | 1.1784 | 3.3648 | 4.7078 | 5.5815 | 6.221 | 6.6847 | 7.0544 | 7.3317 | 7.5517 | 7.7035 | 7.8334
| 0.75 | 1.1686 | 3.4699 | 4.86 | 5.7719 | 6.343 | 6.9328 | 7.3029 | 7.5894 | 7.8072 | 7.9709 | 8.1025
| 0.8 | 1.161 | 3.5792 | 5.0091 | 5.955 | 6.6384 | 7.1496 | 7.5301 | 7.832 | 8.0638 | 8.2278 | 8.3602
| 0.85 | 1.1594 | 3.6775 | 5.1533 | 6.1309 | 6.8322 | 7.3598 | 7.7626 | 8.0621 | 8.311 | 8.4844 | 8.6135
| 0.9 | 1.1517 | 3.7757 | 5.2818 | 6.2896 | 7.0303 | 7.5659 | 7.9786 | 8.2959 | 8.5436 | 8.7276 | 8.8636
| 0.95 | 1.1438 | 3.8694 | 5.4234 | 6.4642 | 7.2084 | 7.7743 | 8.1942 | 8.5232 | 8.7682 | 8.965 | 9.1065
| 1 | 1.1382 | 3.8653 | 5.5639 | 6.6249 | 7.3961 | 7.9701 | 8.401 | 8.7396 | 8.9994 | 9.1939 | 9.3411
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0012522 | -0.00012407 | 0.0012379 | 0.0029483 | 0.0047839 | 0.0065812 | 0.010021 | 0.011678 | 0.011523 | 0.012747 | 0.014075
| 0.1 | 0.0046071 | 0.0071665 | 0.010329 | 0.01364 | 0.01622 | 0.019458 | 0.023411 | 0.024681 | 0.026876 | 0.030948 | 0.030647
| 0.15 | 0.0051005 | 0.011617 | 0.016392 | 0.02297 | 0.025292 | 0.03169 | 0.034776 | 0.034789 | 0.039553 | 0.041746 | 0.042323
| 0.2 | 0.0045028 | 0.013931 | 0.023033 | 0.031684 | 0.033421 | 0.041108 | 0.04402 | 0.045747 | 0.051247 | 0.053267 | 0.05306
| 0.25 | -4.2346e-05 | 0.017103 | 0.029356 | 0.037545 | 0.041551 | 0.050526 | 0.055065 | 0.056704 | 0.062941 | 0.064787 | 0.065673
| 0.3 | -0.0022571 | 0.016269 | 0.03373 | 0.043405 | 0.04968 | 0.059944 | 0.066386 | 0.067662 | 0.074635 | 0.076307 | 0.0775
| 0.35 | -0.0044227 | 0.017206 | 0.038105 | 0.049266 | 0.05781 | 0.069362 | 0.077706 | 0.078619 | 0.086329 | 0.087828 | 0.089326
| 0.4 | -0.0046357 | 0.023513 | 0.04248 | 0.055126 | 0.065939 | 0.07878 | 0.088246 | 0.089577 | 0.098024 | 0.099348 | 0.10115
| 0.45 | -0.006776 | 0.024454 | 0.046855 | 0.060987 | 0.074069 | 0.088198 | 0.098785 | 0.10053 | 0.10859 | 0.11087 | 0.11298
| 0.5 | -0.0093046 | 0.025395 | 0.051229 | 0.066848 | 0.082198 | 0.099413 | 0.10703 | 0.11149 | 0.11291 | 0.11429 | 0.11772
| 0.55 | -0.011233 | 0.026336 | 0.055604 | 0.072708 | 0.090327 | 0.10723 | 0.11473 | 0.12203 | 0.12337 | 0.12409 | 0.12649
| 0.6 | -0.010424 | 0.027278 | 0.059979 | 0.080453 | 0.10048 | 0.11368 | 0.12374 | 0.12787 | 0.12965 | 0.13388 | 0.13644
| 0.65 | -0.01072 | 0.028219 | 0.063346 | 0.089848 | 0.1093 | 0.12045 | 0.12762 | 0.13406 | 0.13696 | 0.13848 | 0.14169
| 0.7 | -0.011788 | 0.02916 | 0.069244 | 0.095835 | 0.11738 | 0.12524 | 0.1339 | 0.13922 | 0.14376 | 0.14469 | 0.148
| 0.75 | -0.0143 | 0.02639 | 0.072009 | 0.10227 | 0.12275 | 0.13589 | 0.14032 | 0.14558 | 0.1486 | 0.15049 | 0.15165
| 0.8 | -0.013344 | 0.03025 | 0.077895 | 0.1087 | 0.12903 | 0.13812 | 0.14656 | 0.14988 | 0.15404 | 0.15629 | 0.15698
| 0.85 | -0.014577 | 0.028235 | 0.083139 | 0.11391 | 0.13351 | 0.14281 | 0.15102 | 0.15604 | 0.15947 | 0.16342 | 0.16359
| 0.9 | -0.014382 | 0.029444 | 0.090483 | 0.11939 | 0.13475 | 0.1472 | 0.15548 | 0.16016 | 0.16339 | 0.16775 | 0.17033
| 0.95 | -0.01706 | 0.030654 | 0.094966 | 0.1241 | 0.13921 | 0.15218 | 0.16124 | 0.16744 | 0.16754 | 0.17234 | 0.17572
| 1 | -0.015472 | 0.03406 | 0.10624 | 0.12962 | 0.14434 | 0.15587 | 0.16564 | 0.17116 | 0.17276 | 0.17795 | 0.17907
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0007853 | -0.0021679 | -0.0032469 | -0.0041511 | -0.0048194 | -0.0053784 | -0.0059595 | -0.0063258 | -0.0066344 | -0.0067292 | -0.0066908
| 0.1 | 0.00020754 | -0.0027432 | -0.004737 | -0.0061672 | -0.0072531 | -0.0080794 | -0.0089495 | -0.0093583 | -0.0095464 | -0.010058 | -0.010218
| 0.15 | 0.00068884 | -0.0032223 | -0.0058908 | -0.0079322 | -0.0095895 | -0.0099835 | -0.010955 | -0.011307 | -0.012364 | -0.013229 | -0.012479
| 0.2 | 0.0011796 | -0.0040299 | -0.0072425 | -0.01047 | -0.011443 | -0.012145 | -0.012534 | -0.012797 | -0.013841 | -0.015272 | -0.014741
| 0.25 | 0.0014929 | -0.0046847 | -0.0088264 | -0.010956 | -0.012466 | -0.013111 | -0.014009 | -0.014288 | -0.015319 | -0.01629 | -0.017002
| 0.3 | 0.0016873 | -0.0052103 | -0.0095245 | -0.011771 | -0.013488 | -0.014077 | -0.015515 | -0.015778 | -0.016796 | -0.017308 | -0.01796
| 0.35 | 0.0014274 | -0.0059047 | -0.010311 | -0.012367 | -0.01393 | -0.015044 | -0.016869 | -0.017269 | -0.017785 | -0.018325 | -0.018918
| 0.4 | 0.0015382 | -0.0065079 | -0.011097 | -0.012963 | -0.014371 | -0.016091 | -0.01767 | -0.018236 | -0.018748 | -0.019074 | -0.019159
| 0.45 | 0.0015196 | -0.007437 | -0.01184 | -0.013559 | -0.015337 | -0.016966 | -0.018471 | -0.019217 | -0.019592 | -0.019964 | -0.020327
| 0.5 | 0.0017675 | -0.008075 | -0.012443 | -0.014155 | -0.016302 | -0.017771 | -0.019221 | -0.020134 | -0.02043 | -0.021026 | -0.021078
| 0.55 | 0.0015853 | -0.0080839 | -0.013052 | -0.014751 | -0.017595 | -0.018484 | -0.019608 | -0.020707 | -0.021509 | -0.021814 | -0.022042
| 0.6 | 0.0015852 | -0.0084095 | -0.013661 | -0.01632 | -0.017818 | -0.019196 | -0.020342 | -0.021526 | -0.022075 | -0.022725 | -0.023126
| 0.65 | 0.0016244 | -0.009106 | -0.014118 | -0.016513 | -0.018642 | -0.019817 | -0.02128 | -0.022164 | -0.023305 | -0.023333 | -0.024262
| 0.7 | 0.0016206 | -0.0098024 | -0.014501 | -0.016602 | -0.019075 | -0.020559 | -0.021856 | -0.023009 | -0.023901 | -0.024323 | -0.025162
| 0.75 | 0.0016187 | -0.010224 | -0.014774 | -0.017915 | -0.019703 | -0.021154 | -0.022723 | -0.023741 | -0.024597 | -0.025404 | -0.025358
| 0.8 | 0.0016431 | -0.010277 | -0.015048 | -0.018118 | -0.020232 | -0.021764 | -0.02345 | -0.024548 | -0.025523 | -0.026145 | -0.02633
| 0.85 | 0.0015997 | -0.010329 | -0.01549 | -0.018901 | -0.020997 | -0.022372 | -0.024263 | -0.025157 | -0.026299 | -0.026995 | -0.027054
| 0.9 | 0.0014346 | -0.010588 | -0.015932 | -0.018944 | -0.021246 | -0.023142 | -0.024951 | -0.025992 | -0.027022 | -0.027609 | -0.028074
| 0.95 | 0.0014732 | -0.010847 | -0.016105 | -0.019455 | -0.021685 | -0.023788 | -0.025266 | -0.026721 | -0.027402 | -0.028213 | -0.02862
| 1 | 0.0016686 | -0.011106 | -0.016852 | -0.019879 | -0.022271 | -0.024387 | -0.026035 | -0.027425 | -0.028145 | -0.028741 | -0.029425
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.10) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-160.60))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.10) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-160.60))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS8_LS>= (hidden)
If Iload/Isc x 5.6569 ≥1 | [12 empty] | If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 |  | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 0.9972 | 1.0023 | 1.0058 | 1.0079 | 1.0087 | 1.0085 | 1.0074 | 1.0056 | 1.0031 | 1.0002 | 0.99688 |  | 0.05 | 0.9972 | 1.0023 | 1.0058 | 1.0079 | 1.0087 | 1.0085 | 1.0074 | 1.0056 | 1.0031 | 1.0002 | 0.99688
| 0.1 | 1.0291 | 1.0459 | 1.0588 | 1.0675 | 1.0722 | 1.0738 | 1.0728 | 1.0697 | 1.0652 | 1.0594 | 1.0528 |  | 0.1 | 1.0291 | 1.0459 | 1.0588 | 1.0675 | 1.0722 | 1.0738 | 1.0728 | 1.0697 | 1.0652 | 1.0594 | 1.0528
| 0.15 | 1.0375 | 1.0659 | 1.0877 | 1.1017 | 1.109 | 1.1111 | 1.1094 | 1.1048 | 1.0982 | 1.0902 | 1.0811 |  | 0.15 | 1.0375 | 1.0659 | 1.0877 | 1.1017 | 1.109 | 1.1111 | 1.1094 | 1.1048 | 1.0982 | 1.0902 | 1.0811
| 0.2 | 1.0384 | 1.0738 | 1.1038 | 1.122 | 1.1309 | 1.1331 | 1.1307 | 1.1249 | 1.117 | 1.1075 | 1.0969 |  | 0.2 | 1.0384 | 1.0738 | 1.1038 | 1.122 | 1.1309 | 1.1331 | 1.1307 | 1.1249 | 1.117 | 1.1075 | 1.0969
| 0.25 | 1.0359 | 1.0761 | 1.1127 | 1.1344 | 1.1446 | 1.1469 | 1.144 | 1.1375 | 1.1287 | 1.1183 | 1.1068 |  | 0.25 | 1.0359 | 1.0761 | 1.1127 | 1.1344 | 1.1446 | 1.1469 | 1.144 | 1.1375 | 1.1287 | 1.1183 | 1.1068
| 0.3 | 1.0289 | 1.0767 | 1.1175 | 1.1422 | 1.1535 | 1.1561 | 1.1529 | 1.146 | 1.1366 | 1.1256 | 1.1134 |  | 0.3 | 1.0289 | 1.0767 | 1.1175 | 1.1422 | 1.1535 | 1.1561 | 1.1529 | 1.146 | 1.1366 | 1.1256 | 1.1134
| 0.35 | 1.019 | 1.0764 | 1.12 | 1.1474 | 1.1597 | 1.1625 | 1.1593 | 1.1521 | 1.1423 | 1.1309 | 1.1183 |  | 0.35 | 1.019 | 1.0764 | 1.12 | 1.1474 | 1.1597 | 1.1625 | 1.1593 | 1.1521 | 1.1423 | 1.1309 | 1.1183
| 0.4 | 1.0075 | 1.0746 | 1.1212 | 1.1509 | 1.1641 | 1.1672 | 1.1639 | 1.1566 | 1.1466 | 1.135 | 1.1222 |  | 0.4 | 1.0075 | 1.0746 | 1.1212 | 1.1509 | 1.1641 | 1.1672 | 1.1639 | 1.1566 | 1.1466 | 1.135 | 1.1222
| 0.45 | 0.99523 | 1.0718 | 1.1226 | 1.1532 | 1.1673 | 1.1707 | 1.1675 | 1.1602 | 1.1501 | 1.1384 | 1.1255 |  | 0.45 | 0.99523 | 1.0718 | 1.1226 | 1.1532 | 1.1673 | 1.1707 | 1.1675 | 1.1602 | 1.1501 | 1.1384 | 1.1255
| 0.5 | 0.98267 | 1.0686 | 1.1237 | 1.1548 | 1.1696 | 1.1734 | 1.1705 | 1.1632 | 1.1532 | 1.1413 | 1.1283 |  | 0.5 | 0.98267 | 1.0686 | 1.1237 | 1.1548 | 1.1696 | 1.1734 | 1.1705 | 1.1632 | 1.1532 | 1.1413 | 1.1283
| 0.55 | 0.97018 | 1.0651 | 1.1243 | 1.1558 | 1.1714 | 1.1757 | 1.173 | 1.1659 | 1.1559 | 1.144 | 1.1309 |  | 0.55 | 0.97018 | 1.0651 | 1.1243 | 1.1558 | 1.1714 | 1.1757 | 1.173 | 1.1659 | 1.1559 | 1.144 | 1.1309
| 0.6 | 0.958 | 1.0616 | 1.1243 | 1.1565 | 1.1729 | 1.1777 | 1.1753 | 1.1683 | 1.1583 | 1.1464 | 1.1332 |  | 0.6 | 0.958 | 1.0616 | 1.1243 | 1.1565 | 1.1729 | 1.1777 | 1.1753 | 1.1683 | 1.1583 | 1.1464 | 1.1332
| 0.65 | 0.94624 | 1.0582 | 1.1241 | 1.1572 | 1.1742 | 1.1794 | 1.1774 | 1.1705 | 1.1605 | 1.1485 | 1.1353 |  | 0.65 | 0.94624 | 1.0582 | 1.1241 | 1.1572 | 1.1742 | 1.1794 | 1.1774 | 1.1705 | 1.1605 | 1.1485 | 1.1353
| 0.7 | 0.93498 | 1.0548 | 1.1237 | 1.158 | 1.1753 | 1.1811 | 1.1793 | 1.1725 | 1.1625 | 1.1505 | 1.1371 |  | 0.7 | 0.93498 | 1.0548 | 1.1237 | 1.158 | 1.1753 | 1.1811 | 1.1793 | 1.1725 | 1.1625 | 1.1505 | 1.1371
| 0.75 | 0.92427 | 1.0517 | 1.1231 | 1.1584 | 1.1764 | 1.1827 | 1.1811 | 1.1744 | 1.1644 | 1.1522 | 1.1387 |  | 0.75 | 0.92427 | 1.0517 | 1.1231 | 1.1584 | 1.1764 | 1.1827 | 1.1811 | 1.1744 | 1.1644 | 1.1522 | 1.1387
| 0.8 | 0.91411 | 1.0486 | 1.1224 | 1.1587 | 1.1774 | 1.1842 | 1.1828 | 1.1761 | 1.166 | 1.1538 | 1.1402 |  | 0.8 | 0.91411 | 1.0486 | 1.1224 | 1.1587 | 1.1774 | 1.1842 | 1.1828 | 1.1761 | 1.166 | 1.1538 | 1.1402
| 0.85 | 0.90451 | 1.0458 | 1.1216 | 1.159 | 1.1785 | 1.1856 | 1.1843 | 1.1776 | 1.1675 | 1.1552 | 1.1415 |  | 0.85 | 0.90451 | 1.0458 | 1.1216 | 1.159 | 1.1785 | 1.1856 | 1.1843 | 1.1776 | 1.1675 | 1.1552 | 1.1415
| 0.9 | 0.89543 | 1.043 | 1.1207 | 1.1591 | 1.1795 | 1.1869 | 1.1857 | 1.179 | 1.1688 | 1.1564 | 1.1427 |  | 0.9 | 0.89543 | 1.043 | 1.1207 | 1.1591 | 1.1795 | 1.1869 | 1.1857 | 1.179 | 1.1688 | 1.1564 | 1.1427
| 0.95 | 0.88687 | 1.0405 | 1.1199 | 1.1592 | 1.1805 | 1.1882 | 1.187 | 1.1803 | 1.17 | 1.1576 | 1.1437 |  | 0.95 | 0.88687 | 1.0405 | 1.1199 | 1.1592 | 1.1805 | 1.1882 | 1.187 | 1.1803 | 1.17 | 1.1576 | 1.1437
| 1 | 0.87878 | 1.038 | 1.119 | 1.1593 | 1.1814 | 1.1893 | 1.1882 | 1.1814 | 1.1711 | 1.1586 | 1.1447 |  | 1 | 0.87878 | 1.038 | 1.119 | 1.1593 | 1.1814 | 1.1893 | 1.1882 | 1.1814 | 1.1711 | 1.1586 | 1.1447
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 |  | 0 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| 0.05 | 1.4938 | 1.4728 | 1.4515 | 1.4305 | 1.4097 | 1.3894 | 1.3694 | 1.3501 | 1.3323 | 1.3141 | 1.2965 |  | 0.05 | 1.4938 | 1.4728 | 1.4515 | 1.4305 | 1.4097 | 1.3894 | 1.3694 | 1.3501 | 1.3323 | 1.3141 | 1.2965
| 0.1 | 1.352 | 1.3215 | 1.2912 | 1.2614 | 1.2326 | 1.205 | 1.1789 | 1.1544 | 1.1308 | 1.1083 | 1.0872 |  | 0.1 | 1.352 | 1.3215 | 1.2912 | 1.2614 | 1.2326 | 1.205 | 1.1789 | 1.1544 | 1.1308 | 1.1083 | 1.0872
| 0.15 | 1.2555 | 1.2178 | 1.1816 | 1.1473 | 1.1147 | 1.0843 | 1.0557 | 1.0292 | 1.0042 | 0.9805 | 0.95858 |  | 0.15 | 1.2555 | 1.2178 | 1.1816 | 1.1473 | 1.1147 | 1.0843 | 1.0557 | 1.0292 | 1.0042 | 0.9805 | 0.95858
| 0.2 | 1.1862 | 1.1413 | 1.1006 | 1.0634 | 1.029 | 0.99711 | 0.96777 | 0.94037 | 0.91491 | 0.89119 | 0.86916 |  | 0.2 | 1.1862 | 1.1413 | 1.1006 | 1.0634 | 1.029 | 0.99711 | 0.96777 | 0.94037 | 0.91491 | 0.89119 | 0.86916
| 0.25 | 1.1339 | 1.0818 | 1.038 | 0.99868 | 0.96325 | 0.93047 | 0.90064 | 0.87302 | 0.84756 | 0.82414 | 0.80207 |  | 0.25 | 1.1339 | 1.0818 | 1.038 | 0.99868 | 0.96325 | 0.93047 | 0.90064 | 0.87302 | 0.84756 | 0.82414 | 0.80207
| 0.3 | 1.0945 | 1.0336 | 0.98705 | 0.94679 | 0.91041 | 0.87713 | 0.847 | 0.81947 | 0.79399 | 0.77083 | 0.74923 |  | 0.3 | 1.0945 | 1.0336 | 0.98705 | 0.94679 | 0.91041 | 0.87713 | 0.847 | 0.81947 | 0.79399 | 0.77083 | 0.74923
| 0.35 | 1.0635 | 0.99404 | 0.94468 | 0.90389 | 0.86681 | 0.8331 | 0.80274 | 0.77502 | 0.7498 | 0.72665 | 0.70598 |  | 0.35 | 1.0635 | 0.99404 | 0.94468 | 0.90389 | 0.86681 | 0.8331 | 0.80274 | 0.77502 | 0.7498 | 0.72665 | 0.70598
| 0.4 | 1.0385 | 0.96038 | 0.90914 | 0.86708 | 0.82923 | 0.79527 | 0.76483 | 0.73709 | 0.71195 | 0.68988 | 0.66895 |  | 0.4 | 1.0385 | 0.96038 | 0.90914 | 0.86708 | 0.82923 | 0.79527 | 0.76483 | 0.73709 | 0.71195 | 0.68988 | 0.66895
| 0.45 | 1.0181 | 0.93123 | 0.87846 | 0.83542 | 0.79681 | 0.76214 | 0.73171 | 0.70423 | 0.67948 | 0.65751 | 0.63731 |  | 0.45 | 1.0181 | 0.93123 | 0.87846 | 0.83542 | 0.79681 | 0.76214 | 0.73171 | 0.70423 | 0.67948 | 0.65751 | 0.63731
| 0.5 | 1.0006 | 0.90574 | 0.85141 | 0.80686 | 0.76773 | 0.73295 | 0.70242 | 0.67542 | 0.65129 | 0.62972 | 0.61009 |  | 0.5 | 1.0006 | 0.90574 | 0.85141 | 0.80686 | 0.76773 | 0.73295 | 0.70242 | 0.67542 | 0.65129 | 0.62972 | 0.61009
| 0.55 | 0.98619 | 0.88311 | 0.8272 | 0.78159 | 0.74177 | 0.70684 | 0.67658 | 0.6497 | 0.62622 | 0.60459 | 0.58564 |  | 0.55 | 0.98619 | 0.88311 | 0.8272 | 0.78159 | 0.74177 | 0.70684 | 0.67658 | 0.6497 | 0.62622 | 0.60459 | 0.58564
| 0.6 | 0.97398 | 0.86244 | 0.8054 | 0.75819 | 0.71786 | 0.68309 | 0.65312 | 0.62691 | 0.60328 | 0.58281 | 0.56385 |  | 0.6 | 0.97398 | 0.86244 | 0.8054 | 0.75819 | 0.71786 | 0.68309 | 0.65312 | 0.62691 | 0.60328 | 0.58281 | 0.56385
| 0.65 | 0.96331 | 0.84404 | 0.78527 | 0.73704 | 0.69629 | 0.66194 | 0.63202 | 0.60611 | 0.58335 | 0.56282 | 0.54441 |  | 0.65 | 0.96331 | 0.84404 | 0.78527 | 0.73704 | 0.69629 | 0.66194 | 0.63202 | 0.60611 | 0.58335 | 0.56282 | 0.54441
| 0.7 | 0.95361 | 0.8273 | 0.76703 | 0.71751 | 0.67672 | 0.64205 | 0.61261 | 0.58736 | 0.56466 | 0.54485 | 0.52717 |  | 0.7 | 0.95361 | 0.8273 | 0.76703 | 0.71751 | 0.67672 | 0.64205 | 0.61261 | 0.58736 | 0.56466 | 0.54485 | 0.52717
| 0.75 | 0.94559 | 0.81213 | 0.74954 | 0.6997 | 0.65851 | 0.62413 | 0.59517 | 0.57012 | 0.54818 | 0.52858 | 0.51102 |  | 0.75 | 0.94559 | 0.81213 | 0.74954 | 0.6997 | 0.65851 | 0.62413 | 0.59517 | 0.57012 | 0.54818 | 0.52858 | 0.51102
| 0.8 | 0.93838 | 0.79787 | 0.73359 | 0.68269 | 0.64183 | 0.60767 | 0.579 | 0.5541 | 0.53279 | 0.51375 | 0.49631 |  | 0.8 | 0.93838 | 0.79787 | 0.73359 | 0.68269 | 0.64183 | 0.60767 | 0.579 | 0.5541 | 0.53279 | 0.51375 | 0.49631
| 0.85 | 0.93196 | 0.78456 | 0.71839 | 0.66702 | 0.62584 | 0.59231 | 0.56395 | 0.53967 | 0.51868 | 0.49978 | 0.48315 |  | 0.85 | 0.93196 | 0.78456 | 0.71839 | 0.66702 | 0.62584 | 0.59231 | 0.56395 | 0.53967 | 0.51868 | 0.49978 | 0.48315
| 0.9 | 0.92631 | 0.77225 | 0.70428 | 0.65243 | 0.61127 | 0.5781 | 0.55031 | 0.52631 | 0.50537 | 0.48726 | 0.4707 |  | 0.9 | 0.92631 | 0.77225 | 0.70428 | 0.65243 | 0.61127 | 0.5781 | 0.55031 | 0.52631 | 0.50537 | 0.48726 | 0.4707
| 0.95 | 0.92068 | 0.76061 | 0.69097 | 0.63871 | 0.59775 | 0.56458 | 0.53725 | 0.51362 | 0.49328 | 0.4755 | 0.45926 |  | 0.95 | 0.92068 | 0.76061 | 0.69097 | 0.63871 | 0.59775 | 0.56458 | 0.53725 | 0.51362 | 0.49328 | 0.4755 | 0.45926
| 1 | 0.91605 | 0.74955 | 0.67826 | 0.62576 | 0.58492 | 0.55226 | 0.52518 | 0.50207 | 0.48196 | 0.46423 | 0.44871 |  | 1 | 0.91605 | 0.74955 | 0.67826 | 0.62576 | 0.58492 | 0.55226 | 0.52518 | 0.50207 | 0.48196 | 0.46423 | 0.44871
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0062025 | 0.0066867 | 0.0072234 | 0.0077447 | 0.008252 | 0.0089278 | 0.0093949 | 0.0096176 | 0.0099932 | 0.010346 | 0.010672 |  | 0.05 | 0.0062025 | 0.0066867 | 0.0072234 | 0.0077447 | 0.008252 | 0.0089278 | 0.0093949 | 0.0096176 | 0.0099932 | 0.010346 | 0.010672
| 0.1 | 0.0083147 | 0.0089906 | 0.0096356 | 0.010152 | 0.010625 | 0.01099 | 0.011325 | 0.011636 | 0.011835 | 0.011983 | 0.01219 |  | 0.1 | 0.0083147 | 0.0089906 | 0.0096356 | 0.010152 | 0.010625 | 0.01099 | 0.011325 | 0.011636 | 0.011835 | 0.011983 | 0.01219
| 0.15 | 0.0088665 | 0.0097686 | 0.010384 | 0.010845 | 0.011211 | 0.011473 | 0.011678 | 0.011849 | 0.011945 | 0.012007 | 0.012091 |  | 0.15 | 0.0088665 | 0.0097686 | 0.010384 | 0.010845 | 0.011211 | 0.011473 | 0.011678 | 0.011849 | 0.011945 | 0.012007 | 0.012091
| 0.2 | 0.0086217 | 0.0098631 | 0.010503 | 0.010928 | 0.011148 | 0.011312 | 0.011493 | 0.011581 | 0.01168 | 0.011667 | 0.011664 |  | 0.2 | 0.0086217 | 0.0098631 | 0.010503 | 0.010928 | 0.011148 | 0.011312 | 0.011493 | 0.011581 | 0.01168 | 0.011667 | 0.011664
| 0.25 | 0.0081482 | 0.009718 | 0.010341 | 0.010734 | 0.010963 | 0.011183 | 0.011244 | 0.011341 | 0.01135 | 0.01136 | 0.011353 |  | 0.25 | 0.0081482 | 0.009718 | 0.010341 | 0.010734 | 0.010963 | 0.011183 | 0.011244 | 0.011341 | 0.01135 | 0.01136 | 0.011353
| 0.3 | 0.0075368 | 0.0093828 | 0.010187 | 0.010537 | 0.010818 | 0.010935 | 0.011069 | 0.011085 | 0.011117 | 0.011057 | 0.011091 |  | 0.3 | 0.0075368 | 0.0093828 | 0.010187 | 0.010537 | 0.010818 | 0.010935 | 0.011069 | 0.011085 | 0.011117 | 0.011057 | 0.011091
| 0.35 | 0.0069321 | 0.0093273 | 0.0098545 | 0.010355 | 0.010625 | 0.010825 | 0.01088 | 0.010948 | 0.010877 | 0.010863 | 0.010698 |  | 0.35 | 0.0069321 | 0.0093273 | 0.0098545 | 0.010355 | 0.010625 | 0.010825 | 0.01088 | 0.010948 | 0.010877 | 0.010863 | 0.010698
| 0.4 | 0.0063894 | 0.0091063 | 0.0097509 | 0.010209 | 0.010544 | 0.010765 | 0.010758 | 0.010777 | 0.010689 | 0.010611 | 0.010486 |  | 0.4 | 0.0063894 | 0.0091063 | 0.0097509 | 0.010209 | 0.010544 | 0.010765 | 0.010758 | 0.010777 | 0.010689 | 0.010611 | 0.010486
| 0.45 | 0.0057367 | 0.0088519 | 0.0096525 | 0.010161 | 0.01053 | 0.010661 | 0.010715 | 0.010619 | 0.010474 | 0.010327 | 0.010186 |  | 0.45 | 0.0057367 | 0.0088519 | 0.0096525 | 0.010161 | 0.01053 | 0.010661 | 0.010715 | 0.010619 | 0.010474 | 0.010327 | 0.010186
| 0.5 | 0.0053071 | 0.0087388 | 0.0094922 | 0.010116 | 0.010471 | 0.010575 | 0.010543 | 0.010341 | 0.010304 | 0.010074 | 0.0099184 |  | 0.5 | 0.0053071 | 0.0087388 | 0.0094922 | 0.010116 | 0.010471 | 0.010575 | 0.010543 | 0.010341 | 0.010304 | 0.010074 | 0.0099184
| 0.55 | 0.0050339 | 0.0085654 | 0.0094692 | 0.010073 | 0.0104 | 0.010489 | 0.010367 | 0.010191 | 0.010033 | 0.0097969 | 0.0096215 |  | 0.55 | 0.0050339 | 0.0085654 | 0.0094692 | 0.010073 | 0.0104 | 0.010489 | 0.010367 | 0.010191 | 0.010033 | 0.0097969 | 0.0096215
| 0.6 | 0.0046892 | 0.008342 | 0.0095074 | 0.0101 | 0.010267 | 0.010305 | 0.010084 | 0.0099451 | 0.0098194 | 0.0095988 | 0.0093871 |  | 0.6 | 0.0046892 | 0.008342 | 0.0095074 | 0.0101 | 0.010267 | 0.010305 | 0.010084 | 0.0099451 | 0.0098194 | 0.0095988 | 0.0093871
| 0.65 | 0.0042505 | 0.0083295 | 0.0094539 | 0.010076 | 0.010234 | 0.01017 | 0.009969 | 0.0097083 | 0.0095516 | 0.0093841 | 0.009131 |  | 0.65 | 0.0042505 | 0.0083295 | 0.0094539 | 0.010076 | 0.010234 | 0.01017 | 0.009969 | 0.0097083 | 0.0095516 | 0.0093841 | 0.009131
| 0.7 | 0.0039384 | 0.0082177 | 0.0093835 | 0.01006 | 0.010168 | 0.010036 | 0.0097839 | 0.009586 | 0.0093017 | 0.0091869 | 0.0089264 |  | 0.7 | 0.0039384 | 0.0082177 | 0.0093835 | 0.01006 | 0.010168 | 0.010036 | 0.0097839 | 0.009586 | 0.0093017 | 0.0091869 | 0.0089264
| 0.75 | 0.00371 | 0.0081149 | 0.0094316 | 0.0099472 | 0.0099646 | 0.0097775 | 0.0096062 | 0.0094292 | 0.0091558 | 0.0089915 | 0.0087698 |  | 0.75 | 0.00371 | 0.0081149 | 0.0094316 | 0.0099472 | 0.0099646 | 0.0097775 | 0.0096062 | 0.0094292 | 0.0091558 | 0.0089915 | 0.0087698
| 0.8 | 0.0036015 | 0.0079289 | 0.0093945 | 0.0098521 | 0.0098036 | 0.0096565 | 0.0094768 | 0.0091835 | 0.00899 | 0.0088054 | 0.0085292 |  | 0.8 | 0.0036015 | 0.0079289 | 0.0093945 | 0.0098521 | 0.0098036 | 0.0096565 | 0.0094768 | 0.0091835 | 0.00899 | 0.0088054 | 0.0085292
| 0.85 | 0.0033809 | 0.0079339 | 0.0094523 | 0.0097735 | 0.0096927 | 0.0095028 | 0.0092538 | 0.0090258 | 0.0087737 | 0.0086202 | 0.0083637 |  | 0.85 | 0.0033809 | 0.0079339 | 0.0094523 | 0.0097735 | 0.0096927 | 0.0095028 | 0.0092538 | 0.0090258 | 0.0087737 | 0.0086202 | 0.0083637
| 0.9 | 0.003108 | 0.007907 | 0.0094359 | 0.009652 | 0.009563 | 0.0093816 | 0.0091456 | 0.0088734 | 0.0085388 | 0.0083878 | 0.0081634 |  | 0.9 | 0.003108 | 0.007907 | 0.0094359 | 0.009652 | 0.009563 | 0.0093816 | 0.0091456 | 0.0088734 | 0.0085388 | 0.0083878 | 0.0081634
| 0.95 | 0.0029318 | 0.007903 | 0.0094072 | 0.009572 | 0.0094161 | 0.0092425 | 0.0088925 | 0.0086933 | 0.0084853 | 0.0081681 | 0.0080225 |  | 0.95 | 0.0029318 | 0.007903 | 0.0094072 | 0.009572 | 0.0094161 | 0.0092425 | 0.0088925 | 0.0086933 | 0.0084853 | 0.0081681 | 0.0080225
| 1 | 0.0027518 | 0.0079344 | 0.0093686 | 0.0094826 | 0.0093255 | 0.0090655 | 0.0087775 | 0.008547 | 0.0082984 | 0.0080694 | 0.00781 |  | 1 | 0.0027518 | 0.0079344 | 0.0093686 | 0.0094826 | 0.0093255 | 0.0090655 | 0.0087775 | 0.008547 | 0.0082984 | 0.0080694 | 0.00781
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.00090381 | 0.00098913 | 0.0010622 | 0.0011389 | 0.0012091 | 0.0012787 | 0.0013412 | 0.0013993 | 0.0014528 | 0.0014991 | 0.0015219 |  | 0.05 | 0.00090381 | 0.00098913 | 0.0010622 | 0.0011389 | 0.0012091 | 0.0012787 | 0.0013412 | 0.0013993 | 0.0014528 | 0.0014991 | 0.0015219
| 0.1 | 0.0010662 | 0.0011827 | 0.0012903 | 0.0013803 | 0.001459 | 0.0015212 | 0.0015741 | 0.0016152 | 0.0016451 | 0.0016691 | 0.0017091 |  | 0.1 | 0.0010662 | 0.0011827 | 0.0012903 | 0.0013803 | 0.001459 | 0.0015212 | 0.0015741 | 0.0016152 | 0.0016451 | 0.0016691 | 0.0017091
| 0.15 | 0.0011005 | 0.001276 | 0.0013911 | 0.0014802 | 0.00155 | 0.0016091 | 0.0016333 | 0.0016596 | 0.0016875 | 0.0017045 | 0.0017131 |  | 0.15 | 0.0011005 | 0.001276 | 0.0013911 | 0.0014802 | 0.00155 | 0.0016091 | 0.0016333 | 0.0016596 | 0.0016875 | 0.0017045 | 0.0017131
| 0.2 | 0.0010517 | 0.0012948 | 0.0014325 | 0.0015149 | 0.0015725 | 0.00161 | 0.0016305 | 0.0016396 | 0.0016588 | 0.0016639 | 0.0016687 |  | 0.2 | 0.0010517 | 0.0012948 | 0.0014325 | 0.0015149 | 0.0015725 | 0.00161 | 0.0016305 | 0.0016396 | 0.0016588 | 0.0016639 | 0.0016687
| 0.25 | 0.00097197 | 0.0012948 | 0.00144 | 0.0015214 | 0.0015594 | 0.0015842 | 0.0016073 | 0.0016098 | 0.0016147 | 0.0016276 | 0.001609 |  | 0.25 | 0.00097197 | 0.0012948 | 0.00144 | 0.0015214 | 0.0015594 | 0.0015842 | 0.0016073 | 0.0016098 | 0.0016147 | 0.0016276 | 0.001609
| 0.3 | 0.00088344 | 0.0012796 | 0.0014436 | 0.0014977 | 0.0015406 | 0.0015663 | 0.0015769 | 0.0015952 | 0.00159 | 0.0015879 | 0.0015654 |  | 0.3 | 0.00088344 | 0.0012796 | 0.0014436 | 0.0014977 | 0.0015406 | 0.0015663 | 0.0015769 | 0.0015952 | 0.00159 | 0.0015879 | 0.0015654
| 0.35 | 0.00080351 | 0.0012632 | 0.0014091 | 0.0014746 | 0.001514 | 0.0015438 | 0.001557 | 0.0015639 | 0.0015578 | 0.0015497 | 0.0015255 |  | 0.35 | 0.00080351 | 0.0012632 | 0.0014091 | 0.0014746 | 0.001514 | 0.0015438 | 0.001557 | 0.0015639 | 0.0015578 | 0.0015497 | 0.0015255
| 0.4 | 0.00073868 | 0.0012501 | 0.0013913 | 0.0014668 | 0.0015041 | 0.0015404 | 0.0015441 | 0.0015398 | 0.0015339 | 0.0015194 | 0.0014981 |  | 0.4 | 0.00073868 | 0.0012501 | 0.0013913 | 0.0014668 | 0.0015041 | 0.0015404 | 0.0015441 | 0.0015398 | 0.0015339 | 0.0015194 | 0.0014981
| 0.45 | 0.00067278 | 0.0012371 | 0.0013703 | 0.0014414 | 0.0014947 | 0.0015221 | 0.0015235 | 0.0015202 | 0.0014981 | 0.0014783 | 0.0014634 |  | 0.45 | 0.00067278 | 0.0012371 | 0.0013703 | 0.0014414 | 0.0014947 | 0.0015221 | 0.0015235 | 0.0015202 | 0.0014981 | 0.0014783 | 0.0014634
| 0.5 | 0.00059144 | 0.0012306 | 0.0013496 | 0.0014416 | 0.0014855 | 0.0015102 | 0.0015049 | 0.001493 | 0.0014764 | 0.0014467 | 0.0014275 |  | 0.5 | 0.00059144 | 0.0012306 | 0.0013496 | 0.0014416 | 0.0014855 | 0.0015102 | 0.0015049 | 0.001493 | 0.0014764 | 0.0014467 | 0.0014275
| 0.55 | 0.00053802 | 0.0012136 | 0.0013446 | 0.0014357 | 0.0014849 | 0.0014967 | 0.0014822 | 0.0014769 | 0.0014498 | 0.0014202 | 0.0013852 |  | 0.55 | 0.00053802 | 0.0012136 | 0.0013446 | 0.0014357 | 0.0014849 | 0.0014967 | 0.0014822 | 0.0014769 | 0.0014498 | 0.0014202 | 0.0013852
| 0.6 | 0.00050307 | 0.0011882 | 0.0013425 | 0.0014416 | 0.001475 | 0.0014843 | 0.0014601 | 0.00145 | 0.0014206 | 0.0013941 | 0.0013569 |  | 0.6 | 0.00050307 | 0.0011882 | 0.0013425 | 0.0014416 | 0.001475 | 0.0014843 | 0.0014601 | 0.00145 | 0.0014206 | 0.0013941 | 0.0013569
| 0.65 | 0.00046001 | 0.0011751 | 0.0013391 | 0.0014391 | 0.0014762 | 0.0014616 | 0.0014425 | 0.0014168 | 0.0013828 | 0.0013638 | 0.0013282 |  | 0.65 | 0.00046001 | 0.0011751 | 0.0013391 | 0.0014391 | 0.0014762 | 0.0014616 | 0.0014425 | 0.0014168 | 0.0013828 | 0.0013638 | 0.0013282
| 0.7 | 0.0004179 | 0.001164 | 0.0013448 | 0.0014316 | 0.0014617 | 0.0014531 | 0.0014235 | 0.0013921 | 0.0013615 | 0.0013343 | 0.0013008 |  | 0.7 | 0.0004179 | 0.001164 | 0.0013448 | 0.0014316 | 0.0014617 | 0.0014531 | 0.0014235 | 0.0013921 | 0.0013615 | 0.0013343 | 0.0013008
| 0.75 | 0.00036886 | 0.001157 | 0.0013324 | 0.001429 | 0.0014397 | 0.0014318 | 0.001399 | 0.0013629 | 0.0013399 | 0.0013006 | 0.0012674 |  | 0.75 | 0.00036886 | 0.001157 | 0.0013324 | 0.001429 | 0.0014397 | 0.0014318 | 0.001399 | 0.0013629 | 0.0013399 | 0.0013006 | 0.0012674
| 0.8 | 0.00035304 | 0.0011458 | 0.0013321 | 0.0014223 | 0.0014328 | 0.0014155 | 0.0013821 | 0.0013519 | 0.0013081 | 0.0012709 | 0.0012532 |  | 0.8 | 0.00035304 | 0.0011458 | 0.0013321 | 0.0014223 | 0.0014328 | 0.0014155 | 0.0013821 | 0.0013519 | 0.0013081 | 0.0012709 | 0.0012532
| 0.85 | 0.00032448 | 0.0011355 | 0.0013402 | 0.0014144 | 0.0014214 | 0.0013881 | 0.0013561 | 0.001317 | 0.0012951 | 0.0012443 | 0.0012164 |  | 0.85 | 0.00032448 | 0.0011355 | 0.0013402 | 0.0014144 | 0.0014214 | 0.0013881 | 0.0013561 | 0.001317 | 0.0012951 | 0.0012443 | 0.0012164
| 0.9 | 0.0002992 | 0.0011198 | 0.0013427 | 0.001411 | 0.0014016 | 0.0013688 | 0.0013372 | 0.0012882 | 0.0012607 | 0.0012219 | 0.0011903 |  | 0.9 | 0.0002992 | 0.0011198 | 0.0013427 | 0.001411 | 0.0014016 | 0.0013688 | 0.0013372 | 0.0012882 | 0.0012607 | 0.0012219 | 0.0011903
| 0.95 | 0.00027385 | 0.0011132 | 0.0013457 | 0.0013983 | 0.0013865 | 0.0013613 | 0.001313 | 0.0012747 | 0.0012372 | 0.0012046 | 0.0011659 |  | 0.95 | 0.00027385 | 0.0011132 | 0.0013457 | 0.0013983 | 0.0013865 | 0.0013613 | 0.001313 | 0.0012747 | 0.0012372 | 0.0012046 | 0.0011659
| 1 | 0.00025421 | 0.0011126 | 0.0013489 | 0.0013878 | 0.0013718 | 0.0013327 | 0.0012954 | 0.0012522 | 0.0012136 | 0.0011739 | 0.001147 |  | 1 | 0.00025421 | 0.0011126 | 0.0013489 | 0.0013878 | 0.0013718 | 0.0013327 | 0.0012954 | 0.0012522 | 0.0012136 | 0.0011739 | 0.001147
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | [12 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 0 to 1
| 0.05 | 1.4117 | 1.5265 | 1.6236 | 1.7064 | 1.7769 | 1.8364 | 1.8894 | 1.934 | 1.9645 | 1.9994 | 2.0279 |  | 0.05 | 1.4117 | 1.5265 | 1.6236 | 1.7064 | 1.7769 | 1.8364 | 1.8894 | 1.934 | 1.9645 | 1.9994 | 2.0279
| 0.1 | 1.5227 | 1.807 | 2.0291 | 2.2057 | 2.3493 | 2.463 | 2.5571 | 2.6271 | 2.693 | 2.7457 | 2.7876 |  | 0.1 | 1.5227 | 1.807 | 2.0291 | 2.2057 | 2.3493 | 2.463 | 2.5571 | 2.6271 | 2.693 | 2.7457 | 2.7876
| 0.15 | 1.5235 | 1.9901 | 2.3359 | 2.6008 | 2.8169 | 2.9696 | 3.1144 | 3.2068 | 3.2811 | 3.3564 | 3.4027 |  | 0.15 | 1.5235 | 1.9901 | 2.3359 | 2.6008 | 2.8169 | 2.9696 | 3.1144 | 3.2068 | 3.2811 | 3.3564 | 3.4027
| 0.2 | 1.4918 | 2.1352 | 2.6189 | 2.9416 | 3.2173 | 3.4297 | 3.579 | 3.7081 | 3.8065 | 3.9962 | 3.9539 |  | 0.2 | 1.4918 | 2.1352 | 2.6189 | 2.9416 | 3.2173 | 3.4297 | 3.579 | 3.7081 | 3.8065 | 3.9962 | 3.9539
| 0.25 | 1.4562 | 2.263 | 2.8613 | 3.1551 | 3.585 | 3.8293 | 3.9903 | 4.1918 | 4.2735 | 4.3894 | 4.3464 |  | 0.25 | 1.4562 | 2.263 | 2.8613 | 3.1551 | 3.585 | 3.8293 | 3.9903 | 4.1918 | 4.2735 | 4.3894 | 4.3464
| 0.3 | 1.4157 | 2.3897 | 3.0491 | 3.578 | 3.95 | 4.2411 | 4.3156 | 4.5476 | 4.6498 | 4.7826 | 4.8257 |  | 0.3 | 1.4157 | 2.3897 | 3.0491 | 3.578 | 3.95 | 4.2411 | 4.3156 | 4.5476 | 4.6498 | 4.7826 | 4.8257
| 0.35 | 1.3786 | 2.5047 | 3.278 | 3.7764 | 4.2555 | 4.5211 | 4.6982 | 4.9243 | 5.0504 | 5.1516 | 5.244 |  | 0.35 | 1.3786 | 2.5047 | 3.278 | 3.7764 | 4.2555 | 4.5211 | 4.6982 | 4.9243 | 5.0504 | 5.1516 | 5.244
| 0.4 | 1.3472 | 2.6406 | 3.4545 | 4.0627 | 4.561 | 4.7825 | 5.0656 | 5.263 | 5.4189 | 5.4468 | 5.6126 |  | 0.4 | 1.3472 | 2.6406 | 3.4545 | 4.0627 | 4.561 | 4.7825 | 5.0656 | 5.263 | 5.4189 | 5.4468 | 5.6126
| 0.45 | 1.3195 | 2.7504 | 3.631 | 4.3654 | 4.7707 | 5.1307 | 5.3843 | 5.5994 | 5.7461 | 5.8663 | 5.9579 |  | 0.45 | 1.3195 | 2.7504 | 3.631 | 4.3654 | 4.7707 | 5.1307 | 5.3843 | 5.5994 | 5.7461 | 5.8663 | 5.9579
| 0.5 | 1.3058 | 2.8244 | 3.8359 | 4.5306 | 5.0331 | 5.4184 | 5.6909 | 5.9068 | 6.0643 | 6.192 | 6.2881 |  | 0.5 | 1.3058 | 2.8244 | 3.8359 | 4.5306 | 5.0331 | 5.4184 | 5.6909 | 5.9068 | 6.0643 | 6.192 | 6.2881
| 0.55 | 1.2825 | 3.0025 | 4.0041 | 4.737 | 5.2786 | 5.6768 | 5.9662 | 6.1919 | 6.3626 | 6.4817 | 6.5904 |  | 0.55 | 1.2825 | 3.0025 | 4.0041 | 4.737 | 5.2786 | 5.6768 | 5.9662 | 6.1919 | 6.3626 | 6.4817 | 6.5904
| 0.6 | 1.2656 | 3.0368 | 4.1743 | 4.953 | 5.5118 | 5.9231 | 6.2264 | 6.474 | 6.6413 | 6.7794 | 6.8795 |  | 0.6 | 1.2656 | 3.0368 | 4.1743 | 4.953 | 5.5118 | 5.9231 | 6.2264 | 6.474 | 6.6413 | 6.7794 | 6.8795
| 0.65 | 1.2467 | 3.1342 | 4.3289 | 5.1604 | 5.7363 | 6.1772 | 6.4831 | 6.7364 | 6.918 | 7.0599 | 7.1599 |  | 0.65 | 1.2467 | 3.1342 | 4.3289 | 5.1604 | 5.7363 | 6.1772 | 6.4831 | 6.7364 | 6.918 | 7.0599 | 7.1599
| 0.7 | 1.2405 | 3.2329 | 4.4874 | 5.3535 | 5.9468 | 6.3986 | 6.7242 | 6.9845 | 7.1753 | 7.3217 | 7.4347 |  | 0.7 | 1.2405 | 3.2329 | 4.4874 | 5.3535 | 5.9468 | 6.3986 | 6.7242 | 6.9845 | 7.1753 | 7.3217 | 7.4347
| 0.75 | 1.2272 | 3.3282 | 4.6629 | 5.5342 | 6.1568 | 6.6242 | 6.9596 | 7.2294 | 7.4292 | 7.5749 | 7.6927 |  | 0.75 | 1.2272 | 3.3282 | 4.6629 | 5.5342 | 6.1568 | 6.6242 | 6.9596 | 7.2294 | 7.4292 | 7.5749 | 7.6927
| 0.8 | 1.215 | 3.4232 | 4.8098 | 5.7121 | 6.3551 | 6.8334 | 7.191 | 7.4605 | 7.6706 | 7.8252 | 7.9427 |  | 0.8 | 1.215 | 3.4232 | 4.8098 | 5.7121 | 6.3551 | 6.8334 | 7.191 | 7.4605 | 7.6706 | 7.8252 | 7.9427
| 0.85 | 1.2035 | 3.5252 | 4.9504 | 5.8789 | 6.556 | 7.0354 | 7.4016 | 7.6886 | 7.9058 | 8.0612 | 8.1911 |  | 0.85 | 1.2035 | 3.5252 | 4.9504 | 5.8789 | 6.556 | 7.0354 | 7.4016 | 7.6886 | 7.9058 | 8.0612 | 8.1911
| 0.9 | 1.1952 | 3.6162 | 5.0873 | 6.0514 | 6.7326 | 7.2393 | 7.6176 | 7.9037 | 8.1295 | 8.298 | 8.4137 |  | 0.9 | 1.1952 | 3.6162 | 5.0873 | 6.0514 | 6.7326 | 7.2393 | 7.6176 | 7.9037 | 8.1295 | 8.298 | 8.4137
| 0.95 | 1.1927 | 3.7042 | 5.2199 | 6.2054 | 6.9143 | 7.4274 | 7.8184 | 8.1089 | 8.3497 | 8.5201 | 8.6447 |  | 0.95 | 1.1927 | 3.7042 | 5.2199 | 6.2054 | 6.9143 | 7.4274 | 7.8184 | 8.1089 | 8.3497 | 8.5201 | 8.6447
| 1 | 1.183 | 3.725 | 5.3362 | 6.3637 | 7.0865 | 7.6198 | 8.018 | 8.3247 | 8.5644 | 8.7382 | 8.8727 |  | 1 | 1.183 | 3.725 | 5.3362 | 6.3637 | 7.0865 | 7.6198 | 8.018 | 8.3247 | 8.5644 | 8.7382 | 8.8727
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0044477 | 0.0045792 | 0.0044699 | 0.0054261 | 0.0059469 | 0.0053588 | 0.0054164 | 0.0083319 | 0.0097078 | 0.010194 | 0.010983 |  | 0.05 | 0.0044477 | 0.0045792 | 0.0044699 | 0.0054261 | 0.0059469 | 0.0053588 | 0.0054164 | 0.0083319 | 0.0097078 | 0.010194 | 0.010983
| 0.1 | 0.013469 | 0.01322 | 0.014607 | 0.015231 | 0.016699 | 0.01784 | 0.019465 | 0.022568 | 0.023628 | 0.022369 | 0.026239 |  | 0.1 | 0.013469 | 0.01322 | 0.014607 | 0.015231 | 0.016699 | 0.01784 | 0.019465 | 0.022568 | 0.023628 | 0.022369 | 0.026239
| 0.15 | 0.018379 | 0.019359 | 0.021035 | 0.022886 | 0.028037 | 0.028225 | 0.028525 | 0.030526 | 0.034106 | 0.033301 | 0.034731 |  | 0.15 | 0.018379 | 0.019359 | 0.021035 | 0.022886 | 0.028037 | 0.028225 | 0.028525 | 0.030526 | 0.034106 | 0.033301 | 0.034731
| 0.2 | 0.020184 | 0.02323 | 0.029762 | 0.027418 | 0.03335 | 0.034273 | 0.035458 | 0.037841 | 0.041502 | 0.041363 | 0.043132 |  | 0.2 | 0.020184 | 0.02323 | 0.029762 | 0.027418 | 0.03335 | 0.034273 | 0.035458 | 0.037841 | 0.041502 | 0.041363 | 0.043132
| 0.25 | 0.019124 | 0.024471 | 0.032701 | 0.03195 | 0.038662 | 0.040322 | 0.042391 | 0.045156 | 0.048898 | 0.049425 | 0.051533 |  | 0.25 | 0.019124 | 0.024471 | 0.032701 | 0.03195 | 0.038662 | 0.040322 | 0.042391 | 0.045156 | 0.048898 | 0.049425 | 0.051533
| 0.3 | 0.01911 | 0.025712 | 0.035641 | 0.036483 | 0.043974 | 0.04637 | 0.049324 | 0.05247 | 0.056294 | 0.057487 | 0.059934 |  | 0.3 | 0.01911 | 0.025712 | 0.035641 | 0.036483 | 0.043974 | 0.04637 | 0.049324 | 0.05247 | 0.056294 | 0.057487 | 0.059934
| 0.35 | 0.01703 | 0.026954 | 0.038581 | 0.041015 | 0.049287 | 0.052418 | 0.056257 | 0.059785 | 0.06369 | 0.065549 | 0.068334 |  | 0.35 | 0.01703 | 0.026954 | 0.038581 | 0.041015 | 0.049287 | 0.052418 | 0.056257 | 0.059785 | 0.06369 | 0.065549 | 0.068334
| 0.4 | 0.014132 | 0.028195 | 0.041521 | 0.045548 | 0.054599 | 0.058467 | 0.06319 | 0.0671 | 0.071086 | 0.073611 | 0.076735 |  | 0.4 | 0.014132 | 0.028195 | 0.041521 | 0.045548 | 0.054599 | 0.058467 | 0.06319 | 0.0671 | 0.071086 | 0.073611 | 0.076735
| 0.45 | 0.01479 | 0.029436 | 0.04446 | 0.05008 | 0.059911 | 0.064515 | 0.070123 | 0.074415 | 0.078482 | 0.081673 | 0.085136 |  | 0.45 | 0.01479 | 0.029436 | 0.04446 | 0.05008 | 0.059911 | 0.064515 | 0.070123 | 0.074415 | 0.078482 | 0.081673 | 0.085136
| 0.5 | 0.012295 | 0.030678 | 0.0474 | 0.054613 | 0.065224 | 0.070564 | 0.077056 | 0.081729 | 0.085878 | 0.089735 | 0.091931 |  | 0.5 | 0.012295 | 0.030678 | 0.0474 | 0.054613 | 0.065224 | 0.070564 | 0.077056 | 0.081729 | 0.085878 | 0.089735 | 0.091931
| 0.55 | 0.0093476 | 0.031919 | 0.05034 | 0.059145 | 0.074903 | 0.078846 | 0.083989 | 0.088274 | 0.093274 | 0.097797 | 0.097139 |  | 0.55 | 0.0093476 | 0.031919 | 0.05034 | 0.059145 | 0.074903 | 0.078846 | 0.083989 | 0.088274 | 0.093274 | 0.097797 | 0.097139
| 0.6 | 0.0078389 | 0.03316 | 0.05328 | 0.063678 | 0.079907 | 0.084875 | 0.091607 | 0.093727 | 0.10067 | 0.10179 | 0.10235 |  | 0.6 | 0.0078389 | 0.03316 | 0.05328 | 0.063678 | 0.079907 | 0.084875 | 0.091607 | 0.093727 | 0.10067 | 0.10179 | 0.10235
| 0.65 | 0.0084306 | 0.034402 | 0.056219 | 0.06821 | 0.083987 | 0.09063 | 0.096392 | 0.099368 | 0.1066 | 0.10552 | 0.10756 |  | 0.65 | 0.0084306 | 0.034402 | 0.056219 | 0.06821 | 0.083987 | 0.09063 | 0.096392 | 0.099368 | 0.1066 | 0.10552 | 0.10756
| 0.7 | 0.0075077 | 0.035643 | 0.059159 | 0.072743 | 0.08793 | 0.096979 | 0.09993 | 0.10495 | 0.10776 | 0.11112 | 0.11277 |  | 0.7 | 0.0075077 | 0.035643 | 0.059159 | 0.072743 | 0.08793 | 0.096979 | 0.09993 | 0.10495 | 0.10776 | 0.11112 | 0.11277
| 0.75 | 0.006964 | 0.036884 | 0.062099 | 0.077275 | 0.091872 | 0.099025 | 0.10623 | 0.1093 | 0.1142 | 0.11588 | 0.11797 |  | 0.75 | 0.006964 | 0.036884 | 0.062099 | 0.077275 | 0.091872 | 0.099025 | 0.10623 | 0.1093 | 0.1142 | 0.11588 | 0.11797
| 0.8 | 0.0034 | 0.038126 | 0.065039 | 0.082805 | 0.098272 | 0.10385 | 0.11055 | 0.11183 | 0.11939 | 0.12136 | 0.12318 |  | 0.8 | 0.0034 | 0.038126 | 0.065039 | 0.082805 | 0.098272 | 0.10385 | 0.11055 | 0.11183 | 0.11939 | 0.12136 | 0.12318
| 0.85 | 0.0030979 | 0.039367 | 0.067978 | 0.085341 | 0.099042 | 0.10653 | 0.11481 | 0.11758 | 0.12328 | 0.1292 | 0.12839 |  | 0.85 | 0.0030979 | 0.039367 | 0.067978 | 0.085341 | 0.099042 | 0.10653 | 0.11481 | 0.11758 | 0.12328 | 0.1292 | 0.12839
| 0.9 | 0.0038918 | 0.040608 | 0.070918 | 0.091407 | 0.10433 | 0.11184 | 0.11824 | 0.12222 | 0.1265 | 0.13207 | 0.1336 |  | 0.9 | 0.0038918 | 0.040608 | 0.070918 | 0.091407 | 0.10433 | 0.11184 | 0.11824 | 0.12222 | 0.1265 | 0.13207 | 0.1336
| 0.95 | 0.0036052 | 0.04185 | 0.073858 | 0.092788 | 0.10607 | 0.11802 | 0.1206 | 0.12578 | 0.13077 | 0.13604 | 0.13881 |  | 0.95 | 0.0036052 | 0.04185 | 0.073858 | 0.092788 | 0.10607 | 0.11802 | 0.1206 | 0.12578 | 0.13077 | 0.13604 | 0.13881
| 1 | 0.0027186 | 0.043091 | 0.078002 | 0.098195 | 0.10863 | 0.11984 | 0.12576 | 0.13217 | 0.13444 | 0.13815 | 0.14116 |  | 1 | 0.0027186 | 0.043091 | 0.078002 | 0.098195 | 0.10863 | 0.11984 | 0.12576 | 0.13217 | 0.13444 | 0.13815 | 0.14116
k = Cg/Cs | [12 empty] | k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0013866 | -0.0021897 | -0.0029077 | -0.0034282 | -0.0038202 | -0.0041091 | -0.0043748 | -0.00457 | -0.0048097 | -0.0048972 | -0.0047844 |  | 0.05 | -0.0013866 | -0.0021897 | -0.0029077 | -0.0034282 | -0.0038202 | -0.0041091 | -0.0043748 | -0.00457 | -0.0048097 | -0.0048972 | -0.0047844
| 0.1 | -0.00069863 | -0.00271 | -0.004129 | -0.0051562 | -0.0058695 | -0.0064295 | -0.0068139 | -0.0074445 | -0.0074012 | -0.007383 | -0.007713 |  | 0.1 | -0.00069863 | -0.00271 | -0.004129 | -0.0051562 | -0.0058695 | -0.0064295 | -0.0068139 | -0.0074445 | -0.0074012 | -0.007383 | -0.007713
| 0.15 | -2.76e-05 | -0.0030148 | -0.0050508 | -0.0064348 | -0.0071414 | -0.0081024 | -0.0094302 | -0.0091645 | -0.009374 | -0.010105 | -0.0099738 |  | 0.15 | -2.76e-05 | -0.0030148 | -0.0050508 | -0.0064348 | -0.0071414 | -0.0081024 | -0.0094302 | -0.0091645 | -0.009374 | -0.010105 | -0.0099738
| 0.2 | 0.00042327 | -0.0034244 | -0.0058656 | -0.0075644 | -0.0087558 | -0.0096046 | -0.01025 | -0.010465 | -0.010953 | -0.011329 | -0.011231 |  | 0.2 | 0.00042327 | -0.0034244 | -0.0058656 | -0.0075644 | -0.0087558 | -0.0096046 | -0.01025 | -0.010465 | -0.010953 | -0.011329 | -0.011231
| 0.25 | 0.00053678 | -0.0038624 | -0.0066088 | -0.0085934 | -0.0099306 | -0.01096 | -0.011626 | -0.011765 | -0.012532 | -0.012372 | -0.012487 |  | 0.25 | 0.00053678 | -0.0038624 | -0.0066088 | -0.0085934 | -0.0099306 | -0.01096 | -0.011626 | -0.011765 | -0.012532 | -0.012372 | -0.012487
| 0.3 | 0.00067109 | -0.0049519 | -0.0069044 | -0.0096108 | -0.01047 | -0.01214 | -0.012741 | -0.013066 | -0.013687 | -0.013415 | -0.013744 |  | 0.3 | 0.00067109 | -0.0049519 | -0.0069044 | -0.0096108 | -0.01047 | -0.01214 | -0.012741 | -0.013066 | -0.013687 | -0.013415 | -0.013744
| 0.35 | 0.00069948 | -0.0053748 | -0.0077229 | -0.01053 | -0.011546 | -0.013153 | -0.013855 | -0.014366 | -0.014753 | -0.014458 | -0.015001 |  | 0.35 | 0.00069948 | -0.0053748 | -0.0077229 | -0.01053 | -0.011546 | -0.013153 | -0.013855 | -0.014366 | -0.014753 | -0.014458 | -0.015001
| 0.4 | 0.00044877 | -0.0057978 | -0.0085414 | -0.011185 | -0.012622 | -0.014477 | -0.014911 | -0.015249 | -0.015629 | -0.015501 | -0.016068 |  | 0.4 | 0.00044877 | -0.0057978 | -0.0085414 | -0.011185 | -0.012622 | -0.014477 | -0.014911 | -0.015249 | -0.015629 | -0.015501 | -0.016068
| 0.45 | 0.00044717 | -0.0062207 | -0.0097954 | -0.011841 | -0.013698 | -0.01508 | -0.015264 | -0.016071 | -0.016558 | -0.016607 | -0.017232 |  | 0.45 | 0.00044717 | -0.0062207 | -0.0097954 | -0.011841 | -0.013698 | -0.01508 | -0.015264 | -0.016071 | -0.016558 | -0.016607 | -0.017232
| 0.5 | 0.00060627 | -0.0066436 | -0.010449 | -0.012496 | -0.014377 | -0.015381 | -0.015968 | -0.017087 | -0.017241 | -0.017294 | -0.017948 |  | 0.5 | 0.00060627 | -0.0066436 | -0.010449 | -0.012496 | -0.014377 | -0.015381 | -0.015968 | -0.017087 | -0.017241 | -0.017294 | -0.017948
| 0.55 | 0.000576 | -0.0070665 | -0.011177 | -0.013151 | -0.014683 | -0.016003 | -0.016278 | -0.017442 | -0.017943 | -0.018265 | -0.018575 |  | 0.55 | 0.000576 | -0.0070665 | -0.011177 | -0.013151 | -0.014683 | -0.016003 | -0.016278 | -0.017442 | -0.017943 | -0.018265 | -0.018575
| 0.6 | 0.00030643 | -0.0074894 | -0.011906 | -0.013914 | -0.015437 | -0.016548 | -0.017285 | -0.01838 | -0.018293 | -0.019158 | -0.019202 |  | 0.6 | 0.00030643 | -0.0074894 | -0.011906 | -0.013914 | -0.015437 | -0.016548 | -0.017285 | -0.01838 | -0.018293 | -0.019158 | -0.019202
| 0.65 | 0.00031652 | -0.0079124 | -0.012635 | -0.014288 | -0.015941 | -0.017105 | -0.017779 | -0.018858 | -0.019145 | -0.019891 | -0.019816 |  | 0.65 | 0.00031652 | -0.0079124 | -0.012635 | -0.014288 | -0.015941 | -0.017105 | -0.017779 | -0.018858 | -0.019145 | -0.019891 | -0.019816
| 0.7 | 0.00021668 | -0.0083353 | -0.012498 | -0.014961 | -0.016643 | -0.017862 | -0.018532 | -0.020143 | -0.019707 | -0.020431 | -0.020601 |  | 0.7 | 0.00021668 | -0.0083353 | -0.012498 | -0.014961 | -0.016643 | -0.017862 | -0.018532 | -0.020143 | -0.019707 | -0.020431 | -0.020601
| 0.75 | 0.00043081 | -0.0087582 | -0.012531 | -0.015291 | -0.016982 | -0.017941 | -0.019416 | -0.02015 | -0.020668 | -0.021112 | -0.021642 |  | 0.75 | 0.00043081 | -0.0087582 | -0.012531 | -0.015291 | -0.016982 | -0.017941 | -0.019416 | -0.02015 | -0.020668 | -0.021112 | -0.021642
| 0.8 | 0.00018251 | -0.0091811 | -0.013187 | -0.015583 | -0.01749 | -0.018621 | -0.019807 | -0.020412 | -0.021266 | -0.021715 | -0.022045 |  | 0.8 | 0.00018251 | -0.0091811 | -0.013187 | -0.015583 | -0.01749 | -0.018621 | -0.019807 | -0.020412 | -0.021266 | -0.021715 | -0.022045
| 0.85 | 0.00016481 | -0.009604 | -0.013469 | -0.016236 | -0.017744 | -0.019388 | -0.020383 | -0.021783 | -0.021786 | -0.022266 | -0.02268 |  | 0.85 | 0.00016481 | -0.009604 | -0.013469 | -0.016236 | -0.017744 | -0.019388 | -0.020383 | -0.021783 | -0.021786 | -0.022266 | -0.02268
| 0.9 | 0.00014352 | -0.010027 | -0.013918 | -0.016448 | -0.018176 | -0.019911 | -0.020992 | -0.021924 | -0.022583 | -0.02293 | -0.023373 |  | 0.9 | 0.00014352 | -0.010027 | -0.013918 | -0.016448 | -0.018176 | -0.019911 | -0.020992 | -0.021924 | -0.022583 | -0.02293 | -0.023373
| 0.95 | 0.00012006 | -0.01045 | -0.01437 | -0.016971 | -0.018959 | -0.020098 | -0.021617 | -0.022158 | -0.023057 | -0.023683 | -0.024077 |  | 0.95 | 0.00012006 | -0.01045 | -0.01437 | -0.016971 | -0.018959 | -0.020098 | -0.021617 | -0.022158 | -0.023057 | -0.023683 | -0.024077
| 1 | 8.299e-05 | -0.010873 | -0.014417 | -0.017374 | -0.018991 | -0.020693 | -0.021953 | -0.022717 | -0.023537 | -0.02448 | -0.024566 |  | 1 | 8.299e-05 | -0.010873 | -0.014417 | -0.017374 | -0.018991 | -0.020693 | -0.021953 | -0.022717 | -0.023537 | -0.02448 | -0.024566
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)

## CLASS8_LS< (hidden)
If Iload/Isc x 5.6569 <1
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| 0.05 | 0.9972 | 1.0023 | 1.0058 | 1.0079 | 1.0087 | 1.0085 | 1.0074 | 1.0056 | 1.0031 | 1.0002 | 0.99688
| 0.1 | 1.0291 | 1.0459 | 1.0588 | 1.0675 | 1.0722 | 1.0738 | 1.0728 | 1.0697 | 1.0652 | 1.0594 | 1.0528
| 0.15 | 1.0375 | 1.0659 | 1.0877 | 1.1017 | 1.109 | 1.1111 | 1.1094 | 1.1048 | 1.0982 | 1.0902 | 1.0811
| 0.2 | 1.0384 | 1.0738 | 1.1038 | 1.122 | 1.1309 | 1.1331 | 1.1307 | 1.1249 | 1.117 | 1.1075 | 1.0969
| 0.25 | 1.0359 | 1.0761 | 1.1127 | 1.1344 | 1.1446 | 1.1469 | 1.144 | 1.1375 | 1.1287 | 1.1183 | 1.1068
| 0.3 | 1.0289 | 1.0767 | 1.1175 | 1.1422 | 1.1535 | 1.1561 | 1.1529 | 1.146 | 1.1366 | 1.1256 | 1.1134
| 0.35 | 1.019 | 1.0764 | 1.12 | 1.1474 | 1.1597 | 1.1625 | 1.1593 | 1.1521 | 1.1423 | 1.1309 | 1.1183
| 0.4 | 1.0075 | 1.0746 | 1.1212 | 1.1509 | 1.1641 | 1.1672 | 1.1639 | 1.1566 | 1.1466 | 1.135 | 1.1222
| 0.45 | 0.99523 | 1.0718 | 1.1226 | 1.1532 | 1.1673 | 1.1707 | 1.1675 | 1.1602 | 1.1501 | 1.1384 | 1.1255
| 0.5 | 0.98267 | 1.0686 | 1.1237 | 1.1548 | 1.1696 | 1.1734 | 1.1705 | 1.1632 | 1.1532 | 1.1413 | 1.1283
| 0.55 | 0.97018 | 1.0651 | 1.1243 | 1.1558 | 1.1714 | 1.1757 | 1.173 | 1.1659 | 1.1559 | 1.144 | 1.1309
| 0.6 | 0.958 | 1.0616 | 1.1243 | 1.1565 | 1.1729 | 1.1777 | 1.1753 | 1.1683 | 1.1583 | 1.1464 | 1.1332
| 0.65 | 0.94624 | 1.0582 | 1.1241 | 1.1572 | 1.1742 | 1.1794 | 1.1774 | 1.1705 | 1.1605 | 1.1485 | 1.1353
| 0.7 | 0.93498 | 1.0548 | 1.1237 | 1.158 | 1.1753 | 1.1811 | 1.1793 | 1.1725 | 1.1625 | 1.1505 | 1.1371
| 0.75 | 0.92427 | 1.0517 | 1.1231 | 1.1584 | 1.1764 | 1.1827 | 1.1811 | 1.1744 | 1.1644 | 1.1522 | 1.1387
| 0.8 | 0.91411 | 1.0486 | 1.1224 | 1.1587 | 1.1774 | 1.1842 | 1.1828 | 1.1761 | 1.166 | 1.1538 | 1.1402
| 0.85 | 0.90451 | 1.0458 | 1.1216 | 1.159 | 1.1785 | 1.1856 | 1.1843 | 1.1776 | 1.1675 | 1.1552 | 1.1415
| 0.9 | 0.89543 | 1.043 | 1.1207 | 1.1591 | 1.1795 | 1.1869 | 1.1857 | 1.179 | 1.1688 | 1.1564 | 1.1427
| 0.95 | 0.88687 | 1.0405 | 1.1199 | 1.1592 | 1.1805 | 1.1882 | 1.187 | 1.1803 | 1.17 | 1.1576 | 1.1437
| 1 | 0.87878 | 1.038 | 1.119 | 1.1593 | 1.1814 | 1.1893 | 1.1882 | 1.1814 | 1.1711 | 1.1586 | 1.1447
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| 0.05 | 1.4938 | 1.4728 | 1.4515 | 1.4305 | 1.4097 | 1.3894 | 1.3694 | 1.3501 | 1.3323 | 1.3141 | 1.2965
| 0.1 | 1.352 | 1.3215 | 1.2912 | 1.2614 | 1.2326 | 1.205 | 1.1789 | 1.1544 | 1.1308 | 1.1083 | 1.0872
| 0.15 | 1.2555 | 1.2178 | 1.1816 | 1.1473 | 1.1147 | 1.0843 | 1.0557 | 1.0292 | 1.0042 | 0.9805 | 0.95858
| 0.2 | 1.1862 | 1.1413 | 1.1006 | 1.0634 | 1.029 | 0.99711 | 0.96777 | 0.94037 | 0.91491 | 0.89119 | 0.86916
| 0.25 | 1.1339 | 1.0818 | 1.038 | 0.99868 | 0.96325 | 0.93047 | 0.90064 | 0.87302 | 0.84756 | 0.82414 | 0.80207
| 0.3 | 1.0945 | 1.0336 | 0.98705 | 0.94679 | 0.91041 | 0.87713 | 0.847 | 0.81947 | 0.79399 | 0.77083 | 0.74923
| 0.35 | 1.0635 | 0.99404 | 0.94468 | 0.90389 | 0.86681 | 0.8331 | 0.80274 | 0.77502 | 0.7498 | 0.72665 | 0.70598
| 0.4 | 1.0385 | 0.96038 | 0.90914 | 0.86708 | 0.82923 | 0.79527 | 0.76483 | 0.73709 | 0.71195 | 0.68988 | 0.66895
| 0.45 | 1.0181 | 0.93123 | 0.87846 | 0.83542 | 0.79681 | 0.76214 | 0.73171 | 0.70423 | 0.67948 | 0.65751 | 0.63731
| 0.5 | 1.0006 | 0.90574 | 0.85141 | 0.80686 | 0.76773 | 0.73295 | 0.70242 | 0.67542 | 0.65129 | 0.62972 | 0.61009
| 0.55 | 0.98619 | 0.88311 | 0.8272 | 0.78159 | 0.74177 | 0.70684 | 0.67658 | 0.6497 | 0.62622 | 0.60459 | 0.58564
| 0.6 | 0.97398 | 0.86244 | 0.8054 | 0.75819 | 0.71786 | 0.68309 | 0.65312 | 0.62691 | 0.60328 | 0.58281 | 0.56385
| 0.65 | 0.96331 | 0.84404 | 0.78527 | 0.73704 | 0.69629 | 0.66194 | 0.63202 | 0.60611 | 0.58335 | 0.56282 | 0.54441
| 0.7 | 0.95361 | 0.8273 | 0.76703 | 0.71751 | 0.67672 | 0.64205 | 0.61261 | 0.58736 | 0.56466 | 0.54485 | 0.52717
| 0.75 | 0.94559 | 0.81213 | 0.74954 | 0.6997 | 0.65851 | 0.62413 | 0.59517 | 0.57012 | 0.54818 | 0.52858 | 0.51102
| 0.8 | 0.93838 | 0.79787 | 0.73359 | 0.68269 | 0.64183 | 0.60767 | 0.579 | 0.5541 | 0.53279 | 0.51375 | 0.49631
| 0.85 | 0.93196 | 0.78456 | 0.71839 | 0.66702 | 0.62584 | 0.59231 | 0.56395 | 0.53967 | 0.51868 | 0.49978 | 0.48315
| 0.9 | 0.92631 | 0.77225 | 0.70428 | 0.65243 | 0.61127 | 0.5781 | 0.55031 | 0.52631 | 0.50537 | 0.48726 | 0.4707
| 0.95 | 0.92068 | 0.76061 | 0.69097 | 0.63871 | 0.59775 | 0.56458 | 0.53725 | 0.51362 | 0.49328 | 0.4755 | 0.45926
| 1 | 0.91605 | 0.74955 | 0.67826 | 0.62576 | 0.58492 | 0.55226 | 0.52518 | 0.50207 | 0.48196 | 0.46423 | 0.44871
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0062025 | 0.0066867 | 0.0072234 | 0.0077447 | 0.008252 | 0.0089278 | 0.0093949 | 0.0096176 | 0.0099932 | 0.010346 | 0.010672
| 0.1 | 0.0083147 | 0.0089906 | 0.0096356 | 0.010152 | 0.010625 | 0.01099 | 0.011325 | 0.011636 | 0.011835 | 0.011983 | 0.01219
| 0.15 | 0.0088665 | 0.0097686 | 0.010384 | 0.010845 | 0.011211 | 0.011473 | 0.011678 | 0.011849 | 0.011945 | 0.012007 | 0.012091
| 0.2 | 0.0086217 | 0.0098631 | 0.010503 | 0.010928 | 0.011148 | 0.011312 | 0.011493 | 0.011581 | 0.01168 | 0.011667 | 0.011664
| 0.25 | 0.0081482 | 0.009718 | 0.010341 | 0.010734 | 0.010963 | 0.011183 | 0.011244 | 0.011341 | 0.01135 | 0.01136 | 0.011353
| 0.3 | 0.0075368 | 0.0093828 | 0.010187 | 0.010537 | 0.010818 | 0.010935 | 0.011069 | 0.011085 | 0.011117 | 0.011057 | 0.011091
| 0.35 | 0.0069321 | 0.0093273 | 0.0098545 | 0.010355 | 0.010625 | 0.010825 | 0.01088 | 0.010948 | 0.010877 | 0.010863 | 0.010698
| 0.4 | 0.0063894 | 0.0091063 | 0.0097509 | 0.010209 | 0.010544 | 0.010765 | 0.010758 | 0.010777 | 0.010689 | 0.010611 | 0.010486
| 0.45 | 0.0057367 | 0.0088519 | 0.0096525 | 0.010161 | 0.01053 | 0.010661 | 0.010715 | 0.010619 | 0.010474 | 0.010327 | 0.010186
| 0.5 | 0.0053071 | 0.0087388 | 0.0094922 | 0.010116 | 0.010471 | 0.010575 | 0.010543 | 0.010341 | 0.010304 | 0.010074 | 0.0099184
| 0.55 | 0.0050339 | 0.0085654 | 0.0094692 | 0.010073 | 0.0104 | 0.010489 | 0.010367 | 0.010191 | 0.010033 | 0.0097969 | 0.0096215
| 0.6 | 0.0046892 | 0.008342 | 0.0095074 | 0.0101 | 0.010267 | 0.010305 | 0.010084 | 0.0099451 | 0.0098194 | 0.0095988 | 0.0093871
| 0.65 | 0.0042505 | 0.0083295 | 0.0094539 | 0.010076 | 0.010234 | 0.01017 | 0.009969 | 0.0097083 | 0.0095516 | 0.0093841 | 0.009131
| 0.7 | 0.0039384 | 0.0082177 | 0.0093835 | 0.01006 | 0.010168 | 0.010036 | 0.0097839 | 0.009586 | 0.0093017 | 0.0091869 | 0.0089264
| 0.75 | 0.00371 | 0.0081149 | 0.0094316 | 0.0099472 | 0.0099646 | 0.0097775 | 0.0096062 | 0.0094292 | 0.0091558 | 0.0089915 | 0.0087698
| 0.8 | 0.0036015 | 0.0079289 | 0.0093945 | 0.0098521 | 0.0098036 | 0.0096565 | 0.0094768 | 0.0091835 | 0.00899 | 0.0088054 | 0.0085292
| 0.85 | 0.0033809 | 0.0079339 | 0.0094523 | 0.0097735 | 0.0096927 | 0.0095028 | 0.0092538 | 0.0090258 | 0.0087737 | 0.0086202 | 0.0083637
| 0.9 | 0.003108 | 0.007907 | 0.0094359 | 0.009652 | 0.009563 | 0.0093816 | 0.0091456 | 0.0088734 | 0.0085388 | 0.0083878 | 0.0081634
| 0.95 | 0.0029318 | 0.007903 | 0.0094072 | 0.009572 | 0.0094161 | 0.0092425 | 0.0088925 | 0.0086933 | 0.0084853 | 0.0081681 | 0.0080225
| 1 | 0.0027518 | 0.0079344 | 0.0093686 | 0.0094826 | 0.0093255 | 0.0090655 | 0.0087775 | 0.008547 | 0.0082984 | 0.0080694 | 0.00781
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.00090381 | 0.00098913 | 0.0010622 | 0.0011389 | 0.0012091 | 0.0012787 | 0.0013412 | 0.0013993 | 0.0014528 | 0.0014991 | 0.0015219
| 0.1 | 0.0010662 | 0.0011827 | 0.0012903 | 0.0013803 | 0.001459 | 0.0015212 | 0.0015741 | 0.0016152 | 0.0016451 | 0.0016691 | 0.0017091
| 0.15 | 0.0011005 | 0.001276 | 0.0013911 | 0.0014802 | 0.00155 | 0.0016091 | 0.0016333 | 0.0016596 | 0.0016875 | 0.0017045 | 0.0017131
| 0.2 | 0.0010517 | 0.0012948 | 0.0014325 | 0.0015149 | 0.0015725 | 0.00161 | 0.0016305 | 0.0016396 | 0.0016588 | 0.0016639 | 0.0016687
| 0.25 | 0.00097197 | 0.0012948 | 0.00144 | 0.0015214 | 0.0015594 | 0.0015842 | 0.0016073 | 0.0016098 | 0.0016147 | 0.0016276 | 0.001609
| 0.3 | 0.00088344 | 0.0012796 | 0.0014436 | 0.0014977 | 0.0015406 | 0.0015663 | 0.0015769 | 0.0015952 | 0.00159 | 0.0015879 | 0.0015654
| 0.35 | 0.00080351 | 0.0012632 | 0.0014091 | 0.0014746 | 0.001514 | 0.0015438 | 0.001557 | 0.0015639 | 0.0015578 | 0.0015497 | 0.0015255
| 0.4 | 0.00073868 | 0.0012501 | 0.0013913 | 0.0014668 | 0.0015041 | 0.0015404 | 0.0015441 | 0.0015398 | 0.0015339 | 0.0015194 | 0.0014981
| 0.45 | 0.00067278 | 0.0012371 | 0.0013703 | 0.0014414 | 0.0014947 | 0.0015221 | 0.0015235 | 0.0015202 | 0.0014981 | 0.0014783 | 0.0014634
| 0.5 | 0.00059144 | 0.0012306 | 0.0013496 | 0.0014416 | 0.0014855 | 0.0015102 | 0.0015049 | 0.001493 | 0.0014764 | 0.0014467 | 0.0014275
| 0.55 | 0.00053802 | 0.0012136 | 0.0013446 | 0.0014357 | 0.0014849 | 0.0014967 | 0.0014822 | 0.0014769 | 0.0014498 | 0.0014202 | 0.0013852
| 0.6 | 0.00050307 | 0.0011882 | 0.0013425 | 0.0014416 | 0.001475 | 0.0014843 | 0.0014601 | 0.00145 | 0.0014206 | 0.0013941 | 0.0013569
| 0.65 | 0.00046001 | 0.0011751 | 0.0013391 | 0.0014391 | 0.0014762 | 0.0014616 | 0.0014425 | 0.0014168 | 0.0013828 | 0.0013638 | 0.0013282
| 0.7 | 0.0004179 | 0.001164 | 0.0013448 | 0.0014316 | 0.0014617 | 0.0014531 | 0.0014235 | 0.0013921 | 0.0013615 | 0.0013343 | 0.0013008
| 0.75 | 0.00036886 | 0.001157 | 0.0013324 | 0.001429 | 0.0014397 | 0.0014318 | 0.001399 | 0.0013629 | 0.0013399 | 0.0013006 | 0.0012674
| 0.8 | 0.00035304 | 0.0011458 | 0.0013321 | 0.0014223 | 0.0014328 | 0.0014155 | 0.0013821 | 0.0013519 | 0.0013081 | 0.0012709 | 0.0012532
| 0.85 | 0.00032448 | 0.0011355 | 0.0013402 | 0.0014144 | 0.0014214 | 0.0013881 | 0.0013561 | 0.001317 | 0.0012951 | 0.0012443 | 0.0012164
| 0.9 | 0.0002992 | 0.0011198 | 0.0013427 | 0.001411 | 0.0014016 | 0.0013688 | 0.0013372 | 0.0012882 | 0.0012607 | 0.0012219 | 0.0011903
| 0.95 | 0.00027385 | 0.0011132 | 0.0013457 | 0.0013983 | 0.0013865 | 0.0013613 | 0.001313 | 0.0012747 | 0.0012372 | 0.0012046 | 0.0011659
| 1 | 0.00025421 | 0.0011126 | 0.0013489 | 0.0013878 | 0.0013718 | 0.0013327 | 0.0012954 | 0.0012522 | 0.0012136 | 0.0011739 | 0.001147
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0 | bar: 0 to 1
| 0.05 | 1.4117 | 1.5265 | 1.6236 | 1.7064 | 1.7769 | 1.8364 | 1.8894 | 1.934 | 1.9645 | 1.9994 | 2.0279
| 0.1 | 1.5227 | 1.807 | 2.0291 | 2.2057 | 2.3493 | 2.463 | 2.5571 | 2.6271 | 2.693 | 2.7457 | 2.7876
| 0.15 | 1.5235 | 1.9901 | 2.3359 | 2.6008 | 2.8169 | 2.9696 | 3.1144 | 3.2068 | 3.2811 | 3.3564 | 3.4027
| 0.2 | 1.4918 | 2.1352 | 2.6189 | 2.9416 | 3.2173 | 3.4297 | 3.579 | 3.7081 | 3.8065 | 3.9962 | 3.9539
| 0.25 | 1.4562 | 2.263 | 2.8613 | 3.1551 | 3.585 | 3.8293 | 3.9903 | 4.1918 | 4.2735 | 4.3894 | 4.3464
| 0.3 | 1.4157 | 2.3897 | 3.0491 | 3.578 | 3.95 | 4.2411 | 4.3156 | 4.5476 | 4.6498 | 4.7826 | 4.8257
| 0.35 | 1.3786 | 2.5047 | 3.278 | 3.7764 | 4.2555 | 4.5211 | 4.6982 | 4.9243 | 5.0504 | 5.1516 | 5.244
| 0.4 | 1.3472 | 2.6406 | 3.4545 | 4.0627 | 4.561 | 4.7825 | 5.0656 | 5.263 | 5.4189 | 5.4468 | 5.6126
| 0.45 | 1.3195 | 2.7504 | 3.631 | 4.3654 | 4.7707 | 5.1307 | 5.3843 | 5.5994 | 5.7461 | 5.8663 | 5.9579
| 0.5 | 1.3058 | 2.8244 | 3.8359 | 4.5306 | 5.0331 | 5.4184 | 5.6909 | 5.9068 | 6.0643 | 6.192 | 6.2881
| 0.55 | 1.2825 | 3.0025 | 4.0041 | 4.737 | 5.2786 | 5.6768 | 5.9662 | 6.1919 | 6.3626 | 6.4817 | 6.5904
| 0.6 | 1.2656 | 3.0368 | 4.1743 | 4.953 | 5.5118 | 5.9231 | 6.2264 | 6.474 | 6.6413 | 6.7794 | 6.8795
| 0.65 | 1.2467 | 3.1342 | 4.3289 | 5.1604 | 5.7363 | 6.1772 | 6.4831 | 6.7364 | 6.918 | 7.0599 | 7.1599
| 0.7 | 1.2405 | 3.2329 | 4.4874 | 5.3535 | 5.9468 | 6.3986 | 6.7242 | 6.9845 | 7.1753 | 7.3217 | 7.4347
| 0.75 | 1.2272 | 3.3282 | 4.6629 | 5.5342 | 6.1568 | 6.6242 | 6.9596 | 7.2294 | 7.4292 | 7.5749 | 7.6927
| 0.8 | 1.215 | 3.4232 | 4.8098 | 5.7121 | 6.3551 | 6.8334 | 7.191 | 7.4605 | 7.6706 | 7.8252 | 7.9427
| 0.85 | 1.2035 | 3.5252 | 4.9504 | 5.8789 | 6.556 | 7.0354 | 7.4016 | 7.6886 | 7.9058 | 8.0612 | 8.1911
| 0.9 | 1.1952 | 3.6162 | 5.0873 | 6.0514 | 6.7326 | 7.2393 | 7.6176 | 7.9037 | 8.1295 | 8.298 | 8.4137
| 0.95 | 1.1927 | 3.7042 | 5.2199 | 6.2054 | 6.9143 | 7.4274 | 7.8184 | 8.1089 | 8.3497 | 8.5201 | 8.6447
| 1 | 1.183 | 3.725 | 5.3362 | 6.3637 | 7.0865 | 7.6198 | 8.018 | 8.3247 | 8.5644 | 8.7382 | 8.8727
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | 0.0044477 | 0.0045792 | 0.0044699 | 0.0054261 | 0.0059469 | 0.0053588 | 0.0054164 | 0.0083319 | 0.0097078 | 0.010194 | 0.010983
| 0.1 | 0.013469 | 0.01322 | 0.014607 | 0.015231 | 0.016699 | 0.01784 | 0.019465 | 0.022568 | 0.023628 | 0.022369 | 0.026239
| 0.15 | 0.018379 | 0.019359 | 0.021035 | 0.022886 | 0.028037 | 0.028225 | 0.028525 | 0.030526 | 0.034106 | 0.033301 | 0.034731
| 0.2 | 0.020184 | 0.02323 | 0.029762 | 0.027418 | 0.03335 | 0.034273 | 0.035458 | 0.037841 | 0.041502 | 0.041363 | 0.043132
| 0.25 | 0.019124 | 0.024471 | 0.032701 | 0.03195 | 0.038662 | 0.040322 | 0.042391 | 0.045156 | 0.048898 | 0.049425 | 0.051533
| 0.3 | 0.01911 | 0.025712 | 0.035641 | 0.036483 | 0.043974 | 0.04637 | 0.049324 | 0.05247 | 0.056294 | 0.057487 | 0.059934
| 0.35 | 0.01703 | 0.026954 | 0.038581 | 0.041015 | 0.049287 | 0.052418 | 0.056257 | 0.059785 | 0.06369 | 0.065549 | 0.068334
| 0.4 | 0.014132 | 0.028195 | 0.041521 | 0.045548 | 0.054599 | 0.058467 | 0.06319 | 0.0671 | 0.071086 | 0.073611 | 0.076735
| 0.45 | 0.01479 | 0.029436 | 0.04446 | 0.05008 | 0.059911 | 0.064515 | 0.070123 | 0.074415 | 0.078482 | 0.081673 | 0.085136
| 0.5 | 0.012295 | 0.030678 | 0.0474 | 0.054613 | 0.065224 | 0.070564 | 0.077056 | 0.081729 | 0.085878 | 0.089735 | 0.091931
| 0.55 | 0.0093476 | 0.031919 | 0.05034 | 0.059145 | 0.074903 | 0.078846 | 0.083989 | 0.088274 | 0.093274 | 0.097797 | 0.097139
| 0.6 | 0.0078389 | 0.03316 | 0.05328 | 0.063678 | 0.079907 | 0.084875 | 0.091607 | 0.093727 | 0.10067 | 0.10179 | 0.10235
| 0.65 | 0.0084306 | 0.034402 | 0.056219 | 0.06821 | 0.083987 | 0.09063 | 0.096392 | 0.099368 | 0.1066 | 0.10552 | 0.10756
| 0.7 | 0.0075077 | 0.035643 | 0.059159 | 0.072743 | 0.08793 | 0.096979 | 0.09993 | 0.10495 | 0.10776 | 0.11112 | 0.11277
| 0.75 | 0.006964 | 0.036884 | 0.062099 | 0.077275 | 0.091872 | 0.099025 | 0.10623 | 0.1093 | 0.1142 | 0.11588 | 0.11797
| 0.8 | 0.0034 | 0.038126 | 0.065039 | 0.082805 | 0.098272 | 0.10385 | 0.11055 | 0.11183 | 0.11939 | 0.12136 | 0.12318
| 0.85 | 0.0030979 | 0.039367 | 0.067978 | 0.085341 | 0.099042 | 0.10653 | 0.11481 | 0.11758 | 0.12328 | 0.1292 | 0.12839
| 0.9 | 0.0038918 | 0.040608 | 0.070918 | 0.091407 | 0.10433 | 0.11184 | 0.11824 | 0.12222 | 0.1265 | 0.13207 | 0.1336
| 0.95 | 0.0036052 | 0.04185 | 0.073858 | 0.092788 | 0.10607 | 0.11802 | 0.1206 | 0.12578 | 0.13077 | 0.13604 | 0.13881
| 1 | 0.0027186 | 0.043091 | 0.078002 | 0.098195 | 0.10863 | 0.11984 | 0.12576 | 0.13217 | 0.13444 | 0.13815 | 0.14116
k = Cg/Cs
Cs [µF] |  | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.05 | -0.0013866 | -0.0021897 | -0.0029077 | -0.0034282 | -0.0038202 | -0.0041091 | -0.0043748 | -0.00457 | -0.0048097 | -0.0048972 | -0.0047844
| 0.1 | -0.00069863 | -0.00271 | -0.004129 | -0.0051562 | -0.0058695 | -0.0064295 | -0.0068139 | -0.0074445 | -0.0074012 | -0.007383 | -0.007713
| 0.15 | -2.76e-05 | -0.0030148 | -0.0050508 | -0.0064348 | -0.0071414 | -0.0081024 | -0.0094302 | -0.0091645 | -0.009374 | -0.010105 | -0.0099738
| 0.2 | 0.00042327 | -0.0034244 | -0.0058656 | -0.0075644 | -0.0087558 | -0.0096046 | -0.01025 | -0.010465 | -0.010953 | -0.011329 | -0.011231
| 0.25 | 0.00053678 | -0.0038624 | -0.0066088 | -0.0085934 | -0.0099306 | -0.01096 | -0.011626 | -0.011765 | -0.012532 | -0.012372 | -0.012487
| 0.3 | 0.00067109 | -0.0049519 | -0.0069044 | -0.0096108 | -0.01047 | -0.01214 | -0.012741 | -0.013066 | -0.013687 | -0.013415 | -0.013744
| 0.35 | 0.00069948 | -0.0053748 | -0.0077229 | -0.01053 | -0.011546 | -0.013153 | -0.013855 | -0.014366 | -0.014753 | -0.014458 | -0.015001
| 0.4 | 0.00044877 | -0.0057978 | -0.0085414 | -0.011185 | -0.012622 | -0.014477 | -0.014911 | -0.015249 | -0.015629 | -0.015501 | -0.016068
| 0.45 | 0.00044717 | -0.0062207 | -0.0097954 | -0.011841 | -0.013698 | -0.01508 | -0.015264 | -0.016071 | -0.016558 | -0.016607 | -0.017232
| 0.5 | 0.00060627 | -0.0066436 | -0.010449 | -0.012496 | -0.014377 | -0.015381 | -0.015968 | -0.017087 | -0.017241 | -0.017294 | -0.017948
| 0.55 | 0.000576 | -0.0070665 | -0.011177 | -0.013151 | -0.014683 | -0.016003 | -0.016278 | -0.017442 | -0.017943 | -0.018265 | -0.018575
| 0.6 | 0.00030643 | -0.0074894 | -0.011906 | -0.013914 | -0.015437 | -0.016548 | -0.017285 | -0.01838 | -0.018293 | -0.019158 | -0.019202
| 0.65 | 0.00031652 | -0.0079124 | -0.012635 | -0.014288 | -0.015941 | -0.017105 | -0.017779 | -0.018858 | -0.019145 | -0.019891 | -0.019816
| 0.7 | 0.00021668 | -0.0083353 | -0.012498 | -0.014961 | -0.016643 | -0.017862 | -0.018532 | -0.020143 | -0.019707 | -0.020431 | -0.020601
| 0.75 | 0.00043081 | -0.0087582 | -0.012531 | -0.015291 | -0.016982 | -0.017941 | -0.019416 | -0.02015 | -0.020668 | -0.021112 | -0.021642
| 0.8 | 0.00018251 | -0.0091811 | -0.013187 | -0.015583 | -0.01749 | -0.018621 | -0.019807 | -0.020412 | -0.021266 | -0.021715 | -0.022045
| 0.85 | 0.00016481 | -0.009604 | -0.013469 | -0.016236 | -0.017744 | -0.019388 | -0.020383 | -0.021783 | -0.021786 | -0.022266 | -0.02268
| 0.9 | 0.00014352 | -0.010027 | -0.013918 | -0.016448 | -0.018176 | -0.019911 | -0.020992 | -0.021924 | -0.022583 | -0.02293 | -0.023373
| 0.95 | 0.00012006 | -0.01045 | -0.01437 | -0.016971 | -0.018959 | -0.020098 | -0.021617 | -0.022158 | -0.023057 | -0.023683 | -0.024077
| 1 | 8.299e-05 | -0.010873 | -0.014417 | -0.017374 | -0.018991 | -0.020693 | -0.021953 | -0.022717 | -0.023537 | -0.02448 | -0.024566
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
𝐸2=𝐾_𝐸2∙𝑈
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))∙
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))∙
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))
-)-
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-
𝑅𝑅𝑅𝑉=〖(𝑅𝑅𝑅𝑉〗_0+𝐾_(𝑅𝑅𝑅𝑉−𝑈)∙(𝑈-26.54) + 𝐾_(𝑅𝑅𝑅𝑉−𝐼)∙(𝐼_𝑠𝑐-179.47))/(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)/3)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)
-)-*0.383)
𝑡𝑑=〖(𝑡𝑑〗_0+𝐾_(𝑡𝑑−𝑈)∙(𝑈-26.54) + 𝐾_(𝑡𝑑−𝐼)∙(𝐼_𝑠𝑐-179.47))∗(1−(𝐼𝑙𝑜𝑎𝑑/𝐼𝑠𝑐∙5.656854−1)*0.383)