## Interpolation
Losses and Efficiency Interpolation
(c) 2020 IEC TC2 WG31
Version 1.1, 2020-04-22
Please enter data into the green fields only!
Induction Motor Direct-on-Line (DOL)
Rated Power | 2.2 | kW | (0,12, 0,18, 0,25, ..., 900, 1000)
Frequency | 50 | Hz | (50)
Poles | 8 |  | (2, 4, 6, 8)
Eff. Class | IE2 |  | (IE1, IE2, IE3, IE4)
Actual Power | 0.7 | kW | (0 up to rated power)
Nominal Eff. | 77.6 | % | from tables
75% Eff. | 77.6 | % | from tables
vl | 0.16495
vo | 0.12371
Actual Eff. | 69.3823 | % | Interpolated motor efficiency at actual power
see IEC 60034-31, Chapter 7.7
Power Drive Systems (Motor + VFD)
Motor alone
Rated Power | 1.1 | kW | (0,12, 0,18, 0,25, ..., 900, 1000)
Eff. Class | IE2 |  | (IE1, IE2, IE3, IE4)
Rated Speed | 1500 | /min | (750, 1000, 1500, 3000)
Rated Torque | 7.0033 | Nm
Actual Speed | 1400 | /min | (0 up to rated speed)
Actual Torque | 4.8 | Nm | (0 up to rated torque)
cL1 | 0.069172 |  | from tables
cL2 | 0.038244 |  | from tables
cL3 | 0.02724 |  | from tables
cL4 | 0.00087186 |  | from tables
cL5 | 0.0013175 |  | from tables
cL6 | -0.016191 |  | from tables
cL7 | 0.14077 |  | from tables
n | 0.93333 |  | relative speed (0 ... 1)
T | 0.68539 |  | relative torque (0 ... 1)
pL | 0.18455 |  | Interpolated relative losses at actual power and speed
see IEC 60034-2-3, Chapter 7.3
Actual Eff. | 77.6103 | %
VFD alone
Rated Power | 1.5 | kW | (0,12, 0,18, 0,25, ..., 900, 1000)
Eff. Class | IE2 |  | (IE1, IE2, IE3) - IE2 and IE3 non-normative!
(0;25) | 0.0417 |  | from tables
(0;50) | 0.043725 |  | from tables
(0;100) | 0.0489 |  | from tables
(50;25) | 0.042225 |  | from tables
(50;50) | 0.045225 |  | from tables
(50;100) | 0.05325 |  | from tables
(90;50) | 0.04785 |  | from tables
(90;100) | 0.061575 |  | from tables
f | 0.93333 |  | relative frequency (0 ... 1)
iq | 0.50262 |  | relative torque producing current (0 ... 1)
PL1 | 0.04658 |  | interpolated relative losses in segment 1
PL2 | 0.048143 |  | interpolated relative losses in segment 2
PL3 | 0.046565 |  | interpolated relative losses in segment 3
PL4 | 0.048125 |  | interpolated relative losses in segment 4
see IEC 61800-9-2, Chapter E.2.3.1
Segment | 2 |  | see IEC 61800-9-2, Chapter E.2.1, Figure E.1
pL | 0.048143 |  | interpolated losses at actual current and speed
Actual Eff. | 90.6925 | %
PDS = Motor + VFD
Actual Eff. | 70.3867 | % | Total Efficiency of Power Drive System

## Motor DOL
IE2
|  |  |  | 34-30-1 | Estimation
|  |  |  | Nominal | 75% Load
Power / kW | f / Hz | Poles | Class | % | %
0.12 | 50 | 4 | IE2 | 59.1 | 58.1
0.18 | 50 | 4 | IE2 | 64.7 | 64.7
0.25 | 50 | 4 | IE2 | 68.5 | 68.5
0.37 | 50 | 4 | IE2 | 72.7 | 72.7
0.55 | 50 | 4 | IE2 | 77.1 | 77.1
0.75 | 50 | 4 | IE2 | 79.6 | 79.6
1.1 | 50 | 4 | IE2 | 81.4 | 81.4
1.5 | 50 | 4 | IE2 | 82.8 | 82.8
2.2 | 50 | 4 | IE2 | 84.3 | 84.8
3 | 50 | 4 | IE2 | 85.5 | 86
4 | 50 | 4 | IE2 | 86.6 | 87.1
5.5 | 50 | 4 | IE2 | 87.7 | 88.2
7.5 | 50 | 4 | IE2 | 88.7 | 89.2
11 | 50 | 4 | IE2 | 89.8 | 90.3
15 | 50 | 4 | IE2 | 90.6 | 91.1
18.5 | 50 | 4 | IE2 | 91.2 | 91.2
22 | 50 | 4 | IE2 | 91.6 | 91.6
30 | 50 | 4 | IE2 | 92.3 | 92.3
37 | 50 | 4 | IE2 | 92.7 | 92.7
45 | 50 | 4 | IE2 | 93.1 | 93.1
55 | 50 | 4 | IE2 | 93.5 | 93.5
75 | 50 | 4 | IE2 | 94 | 94
90 | 50 | 4 | IE2 | 94.2 | 94.2
110 | 50 | 4 | IE2 | 94.5 | 94.5
132 | 50 | 4 | IE2 | 94.7 | 94.7
160 | 50 | 4 | IE2 | 94.9 | 94.9
200 | 50 | 4 | IE2 | 95.1 | 95.1
250 | 50 | 4 | IE2 | 95.1 | 95.1
315 | 50 | 4 | IE2 | 95.1 | 95.1
355 | 50 | 4 | IE2 | 95.1 | 95.1
400 | 50 | 4 | IE2 | 95.1 | 95.1
500 | 50 | 4 | IE2 | 95.1 | 95.1
560 | 50 | 4 | IE2 | 95.1 | 95.1
630 | 50 | 4 | IE2 | 95.1 | 95.1
710 | 50 | 4 | IE2 | 95.1 | 95.1
800 | 50 | 4 | IE2 | 95.1 | 95.1
900 | 50 | 4 | IE2 | 95.1 | 95.1
1000 | 50 | 4 | IE2 | 95.1 | 95.1
0.12 | 50 | 2 | IE2 | 53.6 | 52.6
0.18 | 50 | 2 | IE2 | 60.4 | 59.4
0.25 | 50 | 2 | IE2 | 64.8 | 63.8
0.37 | 50 | 2 | IE2 | 69.5 | 68.5
0.55 | 50 | 2 | IE2 | 74.1 | 73.1
0.75 | 50 | 2 | IE2 | 77.4 | 77.4
1.1 | 50 | 2 | IE2 | 79.6 | 79.6
1.5 | 50 | 2 | IE2 | 81.3 | 81.3
2.2 | 50 | 2 | IE2 | 83.2 | 83.2
3 | 50 | 2 | IE2 | 84.6 | 84.6
4 | 50 | 2 | IE2 | 85.8 | 85.8
5.5 | 50 | 2 | IE2 | 87 | 87
7.5 | 50 | 2 | IE2 | 88.1 | 88.1
11 | 50 | 2 | IE2 | 89.4 | 89.4
15 | 50 | 2 | IE2 | 90.3 | 90.3
18.5 | 50 | 2 | IE2 | 90.9 | 90.9
22 | 50 | 2 | IE2 | 91.3 | 91.3
30 | 50 | 2 | IE2 | 92 | 92
37 | 50 | 2 | IE2 | 92.5 | 92.5
45 | 50 | 2 | IE2 | 92.9 | 92.9
55 | 50 | 2 | IE2 | 93.2 | 93.2
75 | 50 | 2 | IE2 | 93.8 | 93.8
90 | 50 | 2 | IE2 | 94.1 | 94.1
110 | 50 | 2 | IE2 | 94.3 | 94.3
132 | 50 | 2 | IE2 | 94.6 | 94.6
160 | 50 | 2 | IE2 | 94.8 | 94.8
200 | 50 | 2 | IE2 | 95 | 95
250 | 50 | 2 | IE2 | 95 | 95
315 | 50 | 2 | IE2 | 95 | 95
355 | 50 | 2 | IE2 | 95 | 95
400 | 50 | 2 | IE2 | 95 | 95
500 | 50 | 2 | IE2 | 95 | 95
560 | 50 | 2 | IE2 | 95 | 95
630 | 50 | 2 | IE2 | 95 | 95
710 | 50 | 2 | IE2 | 95 | 95
800 | 50 | 2 | IE2 | 95 | 95
900 | 50 | 2 | IE2 | 95 | 95
1000 | 50 | 2 | IE2 | 95 | 95
0.12 | 50 | 6 | IE2 | 50.6 | 49.6
0.18 | 50 | 6 | IE2 | 56.6 | 55.6
0.25 | 50 | 6 | IE2 | 61.6 | 60.6
0.37 | 50 | 6 | IE2 | 67.6 | 66.6
0.55 | 50 | 6 | IE2 | 73.1 | 72.1
0.75 | 50 | 6 | IE2 | 75.9 | 75.9
1.1 | 50 | 6 | IE2 | 78.1 | 78.1
1.5 | 50 | 6 | IE2 | 79.8 | 79.8
2.2 | 50 | 6 | IE2 | 81.8 | 81.8
3 | 50 | 6 | IE2 | 83.3 | 83.3
4 | 50 | 6 | IE2 | 84.6 | 84.6
5.5 | 50 | 6 | IE2 | 86 | 86
7.5 | 50 | 6 | IE2 | 87.2 | 87.2
11 | 50 | 6 | IE2 | 88.7 | 88.7
15 | 50 | 6 | IE2 | 89.7 | 89.7
18.5 | 50 | 6 | IE2 | 90.4 | 90.4
22 | 50 | 6 | IE2 | 90.9 | 90.9
30 | 50 | 6 | IE2 | 91.7 | 91.7
37 | 50 | 6 | IE2 | 92.2 | 92.2
45 | 50 | 6 | IE2 | 92.7 | 92.7
55 | 50 | 6 | IE2 | 93.1 | 93.1
75 | 50 | 6 | IE2 | 93.7 | 93.7
90 | 50 | 6 | IE2 | 94 | 94
110 | 50 | 6 | IE2 | 94.3 | 94.3
132 | 50 | 6 | IE2 | 94.6 | 94.6
160 | 50 | 6 | IE2 | 94.8 | 94.8
200 | 50 | 6 | IE2 | 95 | 95
250 | 50 | 6 | IE2 | 95 | 95
315 | 50 | 6 | IE2 | 95 | 95
355 | 50 | 6 | IE2 | 95 | 95
400 | 50 | 6 | IE2 | 95 | 95
500 | 50 | 6 | IE2 | 95 | 95
560 | 50 | 6 | IE2 | 95 | 95
630 | 50 | 6 | IE2 | 95 | 95
710 | 50 | 6 | IE2 | 95 | 95
800 | 50 | 6 | IE2 | 95 | 95
900 | 50 | 6 | IE2 | 95 | 95
1000 | 50 | 6 | IE2 | 95 | 95
0.12 | 50 | 8 | IE2 | 39.8 | 38.8
0.18 | 50 | 8 | IE2 | 45.9 | 44.9
0.25 | 50 | 8 | IE2 | 50.6 | 49.6
0.37 | 50 | 8 | IE2 | 56.1 | 55.1
0.55 | 50 | 8 | IE2 | 61.7 | 60.7
0.75 | 50 | 8 | IE2 | 66.2 | 66.2
1.1 | 50 | 8 | IE2 | 70.8 | 70.8
1.5 | 50 | 8 | IE2 | 74.1 | 74.1
2.2 | 50 | 8 | IE2 | 77.6 | 77.6
3 | 50 | 8 | IE2 | 80 | 80
4 | 50 | 8 | IE2 | 81.9 | 81.9
5.5 | 50 | 8 | IE2 | 83.8 | 83.8
7.5 | 50 | 8 | IE2 | 85.3 | 85.3
11 | 50 | 8 | IE2 | 86.9 | 86.9
15 | 50 | 8 | IE2 | 88 | 88
18.5 | 50 | 8 | IE2 | 88.6 | 88.6
22 | 50 | 8 | IE2 | 89.1 | 89.1
30 | 50 | 8 | IE2 | 89.8 | 89.8
37 | 50 | 8 | IE2 | 90.3 | 90.3
45 | 50 | 8 | IE2 | 90.7 | 90.7
55 | 50 | 8 | IE2 | 91 | 91
75 | 50 | 8 | IE2 | 91.6 | 91.6
90 | 50 | 8 | IE2 | 91.9 | 91.9
110 | 50 | 8 | IE2 | 92.3 | 92.3
132 | 50 | 8 | IE2 | 92.6 | 92.6
160 | 50 | 8 | IE2 | 93 | 93
200 | 50 | 8 | IE2 | 93.5 | 93.5
250 | 50 | 8 | IE2 | 93.5 | 93.5
315 | 50 | 8 | IE2 | 93.5 | 93.5
355 | 50 | 8 | IE2 | 93.5 | 93.5
400 | 50 | 8 | IE2 | 93.5 | 93.5
500 | 50 | 8 | IE2 | 93.5 | 93.5
560 | 50 | 8 | IE2 | 93.5 | 93.5
630 | 50 | 8 | IE2 | 93.5 | 93.5
710 | 50 | 8 | IE2 | 93.5 | 93.5
800 | 50 | 8 | IE2 | 93.5 | 93.5
900 | 50 | 8 | IE2 | 93.5 | 93.5
1000 | 50 | 8 | IE2 | 93.5 | 93.5
IE1
|  |  |  | 34-30-2 | Estimation
Losses increased |  |  |  | Nominal | 75% Load
Power [kW] | f / Hz | Poles | Class | % | %
0.12 | 50 | 4 | IE1 | 50 | 48.7775
0.18 | 50 | 4 | IE1 | 57 | 57
0.25 | 50 | 4 | IE1 | 61.5 | 61.5
0.37 | 50 | 4 | IE1 | 66 | 66
0.55 | 50 | 4 | IE1 | 70 | 70
0.75 | 50 | 4 | IE1 | 72.1 | 72.1
1.1 | 50 | 4 | IE1 | 75 | 75
1.5 | 50 | 4 | IE1 | 77.2 | 77.2
2.2 | 50 | 4 | IE1 | 79.7 | 80.3465
3 | 50 | 4 | IE1 | 81.5 | 82.1379
4 | 50 | 4 | IE1 | 83.1 | 83.7306
5.5 | 50 | 4 | IE1 | 84.7 | 85.322
7.5 | 50 | 4 | IE1 | 86 | 86.6195
11 | 50 | 4 | IE1 | 87.6 | 88.2078
15 | 50 | 4 | IE1 | 88.7 | 89.3011
18.5 | 50 | 4 | IE1 | 89.3 | 89.3
22 | 50 | 4 | IE1 | 89.9 | 89.9
30 | 50 | 4 | IE1 | 90.7 | 90.7
37 | 50 | 4 | IE1 | 91.2 | 91.2
45 | 50 | 4 | IE1 | 91.7 | 91.7
55 | 50 | 4 | IE1 | 92.1 | 92.1
75 | 50 | 4 | IE1 | 92.7 | 92.7
90 | 50 | 4 | IE1 | 93 | 93
110 | 50 | 4 | IE1 | 93.3 | 93.3
132 | 50 | 4 | IE1 | 93.5 | 93.5
160 | 50 | 4 | IE1 | 93.8 | 93.8
200 | 50 | 4 | IE1 | 94 | 94
250 | 50 | 4 | IE1 | 94 | 94
315 | 50 | 4 | IE1 | 94 | 94
355 | 50 | 4 | IE1 | 94 | 94
400 | 50 | 4 | IE1 | 94 | 94
500 | 50 | 4 | IE1 | 94 | 94
560 | 50 | 4 | IE1 | 94 | 94
630 | 50 | 4 | IE1 | 94 | 94
710 | 50 | 4 | IE1 | 94 | 94
800 | 50 | 4 | IE1 | 94 | 94
900 | 50 | 4 | IE1 | 94 | 94
1000 | 50 | 4 | IE1 | 94 | 94
0.12 | 50 | 2 | IE1 | 45 | 43.8147
0.18 | 50 | 2 | IE1 | 52.8 | 51.6081
0.25 | 50 | 2 | IE1 | 58.2 | 57.0125
0.37 | 50 | 2 | IE1 | 63.9 | 62.7164
0.55 | 50 | 2 | IE1 | 69 | 67.8031
0.75 | 50 | 2 | IE1 | 72.1 | 72.1
1.1 | 50 | 2 | IE1 | 75 | 75
1.5 | 50 | 2 | IE1 | 77.2 | 77.2
2.2 | 50 | 2 | IE1 | 79.7 | 79.7
3 | 50 | 2 | IE1 | 81.5 | 81.5
4 | 50 | 2 | IE1 | 83.1 | 83.1
5.5 | 50 | 2 | IE1 | 84.7 | 84.7
7.5 | 50 | 2 | IE1 | 86 | 86
11 | 50 | 2 | IE1 | 87.6 | 87.6
15 | 50 | 2 | IE1 | 88.7 | 88.7
18.5 | 50 | 2 | IE1 | 89.3 | 89.3
22 | 50 | 2 | IE1 | 89.9 | 89.9
30 | 50 | 2 | IE1 | 90.7 | 90.7
37 | 50 | 2 | IE1 | 91.2 | 91.2
45 | 50 | 2 | IE1 | 91.7 | 91.7
55 | 50 | 2 | IE1 | 92.1 | 92.1
75 | 50 | 2 | IE1 | 92.7 | 92.7
90 | 50 | 2 | IE1 | 93 | 93
110 | 50 | 2 | IE1 | 93.3 | 93.3
132 | 50 | 2 | IE1 | 93.5 | 93.5
160 | 50 | 2 | IE1 | 93.8 | 93.8
200 | 50 | 2 | IE1 | 94 | 94
250 | 50 | 2 | IE1 | 94 | 94
315 | 50 | 2 | IE1 | 94 | 94
355 | 50 | 2 | IE1 | 94 | 94
400 | 50 | 2 | IE1 | 94 | 94
500 | 50 | 2 | IE1 | 94 | 94
560 | 50 | 2 | IE1 | 94 | 94
630 | 50 | 2 | IE1 | 94 | 94
710 | 50 | 2 | IE1 | 94 | 94
800 | 50 | 2 | IE1 | 94 | 94
900 | 50 | 2 | IE1 | 94 | 94
1000 | 50 | 2 | IE1 | 94 | 94
0.12 | 50 | 6 | IE1 | 38.3 | 37.051
0.18 | 50 | 6 | IE1 | 45.5 | 44.2442
0.25 | 50 | 6 | IE1 | 52.1 | 50.8526
0.37 | 50 | 6 | IE1 | 59.7 | 58.4562
0.55 | 50 | 6 | IE1 | 65.8 | 64.5286
0.75 | 50 | 6 | IE1 | 70 | 70
1.1 | 50 | 6 | IE1 | 72.9 | 72.9
1.5 | 50 | 6 | IE1 | 75.2 | 75.2
2.2 | 50 | 6 | IE1 | 77.7 | 77.7
3 | 50 | 6 | IE1 | 79.7 | 79.7
4 | 50 | 6 | IE1 | 81.4 | 81.4
5.5 | 50 | 6 | IE1 | 83.1 | 83.1
7.5 | 50 | 6 | IE1 | 84.7 | 84.7
11 | 50 | 6 | IE1 | 86.4 | 86.4
15 | 50 | 6 | IE1 | 87.7 | 87.7
18.5 | 50 | 6 | IE1 | 88.6 | 88.6
22 | 50 | 6 | IE1 | 89.2 | 89.2
30 | 50 | 6 | IE1 | 90.2 | 90.2
37 | 50 | 6 | IE1 | 90.8 | 90.8
45 | 50 | 6 | IE1 | 91.4 | 91.4
55 | 50 | 6 | IE1 | 91.9 | 91.9
75 | 50 | 6 | IE1 | 92.6 | 92.6
90 | 50 | 6 | IE1 | 92.9 | 92.9
110 | 50 | 6 | IE1 | 93.3 | 93.3
132 | 50 | 6 | IE1 | 93.5 | 93.5
160 | 50 | 6 | IE1 | 93.8 | 93.8
200 | 50 | 6 | IE1 | 94 | 94
250 | 50 | 6 | IE1 | 94 | 94
315 | 50 | 6 | IE1 | 94 | 94
355 | 50 | 6 | IE1 | 94 | 94
400 | 50 | 6 | IE1 | 94 | 94
500 | 50 | 6 | IE1 | 94 | 94
560 | 50 | 6 | IE1 | 94 | 94
630 | 50 | 6 | IE1 | 94 | 94
710 | 50 | 6 | IE1 | 94 | 94
800 | 50 | 6 | IE1 | 94 | 94
900 | 50 | 6 | IE1 | 94 | 94
1000 | 50 | 6 | IE1 | 94 | 94
0.12 | 50 | 8 | IE1 | 31 | 29.8538
0.18 | 50 | 8 | IE1 | 38 | 36.854
0.25 | 50 | 8 | IE1 | 43.3 | 42.1522
0.37 | 50 | 8 | IE1 | 49.7 | 48.5542
0.55 | 50 | 8 | IE1 | 56.1 | 54.9538
0.75 | 50 | 8 | IE1 | 61.2 | 61.2
1.1 | 50 | 8 | IE1 | 68.5 | 68.5
1.5 | 50 | 8 | IE1 | 70.2 | 70.2
2.2 | 50 | 8 | IE1 | 74.2 | 74.2
3 | 50 | 8 | IE1 | 77 | 77
4 | 50 | 8 | IE1 | 79.2 | 79.2
5.5 | 50 | 8 | IE1 | 81.4 | 81.4
7.5 | 50 | 8 | IE1 | 83.1 | 83.1
11 | 50 | 8 | IE1 | 85 | 85
15 | 50 | 8 | IE1 | 86.2 | 86.2
18.5 | 50 | 8 | IE1 | 86.9 | 86.9
22 | 50 | 8 | IE1 | 87.4 | 87.4
30 | 50 | 8 | IE1 | 88.3 | 88.3
37 | 50 | 8 | IE1 | 88.8 | 88.8
45 | 50 | 8 | IE1 | 89.2 | 89.2
55 | 50 | 8 | IE1 | 89.7 | 89.7
75 | 50 | 8 | IE1 | 90.3 | 90.3
90 | 50 | 8 | IE1 | 90.7 | 90.7
110 | 50 | 8 | IE1 | 91.1 | 91.1
132 | 50 | 8 | IE1 | 91.5 | 91.5
160 | 50 | 8 | IE1 | 91.9 | 91.9
200 | 50 | 8 | IE1 | 92.5 | 92.5
250 | 50 | 8 | IE1 | 92.5 | 92.5
315 | 50 | 8 | IE1 | 92.5 | 92.5
355 | 50 | 8 | IE1 | 92.5 | 92.5
400 | 50 | 8 | IE1 | 92.5 | 92.5
500 | 50 | 8 | IE1 | 92.5 | 92.5
560 | 50 | 8 | IE1 | 92.5 | 92.5
630 | 50 | 8 | IE1 | 92.5 | 92.5
710 | 50 | 8 | IE1 | 92.5 | 92.5
800 | 50 | 8 | IE1 | 92.5 | 92.5
900 | 50 | 8 | IE1 | 92.5 | 92.5
1000 | 50 | 8 | IE1 | 92.5 | 92.5
IE3
|  |  |  | 34-30-2 | Estimation
Losses increased |  |  |  | Nominal | 75% Load
Power [kW] | f / Hz | Poles | Class | % | %
0.12 | 50 | 4 | IE3 | 64.8 | 63.9394
0.18 | 50 | 4 | IE3 | 69.9 | 69.9
0.25 | 50 | 4 | IE3 | 73.5 | 73.5
0.37 | 50 | 4 | IE3 | 77.3 | 77.3
0.55 | 50 | 4 | IE3 | 80.8 | 80.8
0.75 | 50 | 4 | IE3 | 82.5 | 82.5
1.1 | 50 | 4 | IE3 | 64.1 | 64.1
1.5 | 50 | 4 | IE3 | 85.3 | 85.3
2.2 | 50 | 4 | IE3 | 86.7 | 87.1236
3 | 50 | 4 | IE3 | 87.7 | 88.1241
4 | 50 | 4 | IE3 | 88.6 | 89.0254
5.5 | 50 | 4 | IE3 | 89.6 | 90.0228
7.5 | 50 | 4 | IE3 | 90.4 | 90.8248
11 | 50 | 4 | IE3 | 91.4 | 91.8216
15 | 50 | 4 | IE3 | 92.1 | 92.5202
18.5 | 50 | 4 | IE3 | 92.6 | 92.6
22 | 50 | 4 | IE3 | 93 | 93
30 | 50 | 4 | IE3 | 93.6 | 93.6
37 | 50 | 4 | IE3 | 93.9 | 93.9
45 | 50 | 4 | IE3 | 94.2 | 94.2
55 | 50 | 4 | IE3 | 94.6 | 94.6
75 | 50 | 4 | IE3 | 95 | 95
90 | 50 | 4 | IE3 | 95.2 | 95.2
110 | 50 | 4 | IE3 | 95.4 | 95.4
132 | 50 | 4 | IE3 | 95.6 | 95.6
160 | 50 | 4 | IE3 | 95.8 | 95.8
200 | 50 | 4 | IE3 | 96 | 96
250 | 50 | 4 | IE3 | 96 | 96
315 | 50 | 4 | IE3 | 96 | 96
355 | 50 | 4 | IE3 | 96 | 96
400 | 50 | 4 | IE3 | 96 | 96
500 | 50 | 4 | IE3 | 96 | 96
560 | 50 | 4 | IE3 | 96 | 96
630 | 50 | 4 | IE3 | 96 | 96
710 | 50 | 4 | IE3 | 96 | 96
800 | 50 | 4 | IE3 | 96 | 96
900 | 50 | 4 | IE3 | 96 | 96
1000 | 50 | 4 | IE3 | 96 | 96
0.12 | 50 | 2 | IE3 | 60.8 | 59.9552
0.18 | 50 | 2 | IE3 | 65.9 | 65.0389
0.25 | 50 | 2 | IE3 | 69.7 | 68.8392
0.37 | 50 | 2 | IE3 | 73.5 | 72.6311
0.55 | 50 | 2 | IE3 | 77.8 | 76.9429
0.75 | 50 | 2 | IE3 | 80.7 | 80.7
1.1 | 50 | 2 | IE3 | 82.7 | 82.7
1.5 | 50 | 2 | IE3 | 84.2 | 84.2
2.2 | 50 | 2 | IE3 | 85.9 | 85.9
3 | 50 | 2 | IE3 | 87.1 | 87.1
4 | 50 | 2 | IE3 | 88.1 | 88.1
5.5 | 50 | 2 | IE3 | 89.2 | 89.2
7.5 | 50 | 2 | IE3 | 90.1 | 90.1
11 | 50 | 2 | IE3 | 91.2 | 91.2
15 | 50 | 2 | IE3 | 91.9 | 91.9
18.5 | 50 | 2 | IE3 | 92.4 | 92.4
22 | 50 | 2 | IE3 | 92.7 | 92.7
30 | 50 | 2 | IE3 | 93.3 | 93.3
37 | 50 | 2 | IE3 | 93.7 | 93.7
45 | 50 | 2 | IE3 | 94 | 94
55 | 50 | 2 | IE3 | 94.3 | 94.3
75 | 50 | 2 | IE3 | 94.7 | 94.7
90 | 50 | 2 | IE3 | 95 | 95
110 | 50 | 2 | IE3 | 95.2 | 95.2
132 | 50 | 2 | IE3 | 95.4 | 95.4
160 | 50 | 2 | IE3 | 95.6 | 95.6
200 | 50 | 2 | IE3 | 95.8 | 95.8
250 | 50 | 2 | IE3 | 95.8 | 95.8
315 | 50 | 2 | IE3 | 95.8 | 95.8
355 | 50 | 2 | IE3 | 95.8 | 95.8
400 | 50 | 2 | IE3 | 95.8 | 95.8
500 | 50 | 2 | IE3 | 95.8 | 95.8
560 | 50 | 2 | IE3 | 95.8 | 95.8
630 | 50 | 2 | IE3 | 95.8 | 95.8
710 | 50 | 2 | IE3 | 95.8 | 95.8
800 | 50 | 2 | IE3 | 95.8 | 95.8
900 | 50 | 2 | IE3 | 95.8 | 95.8
1000 | 50 | 2 | IE3 | 95.8 | 95.8
0.12 | 50 | 6 | IE3 | 57.7 | 56.8437
0.18 | 50 | 6 | IE3 | 63.9 | 63.0682
0.25 | 50 | 6 | IE3 | 68.6 | 67.7823
0.37 | 50 | 6 | IE3 | 73.5 | 72.6821
0.55 | 50 | 6 | IE3 | 77.2 | 76.3524
0.75 | 50 | 6 | IE3 | 78.6 | 78.6
1.1 | 50 | 6 | IE3 | 81 | 81
1.5 | 50 | 6 | IE3 | 82.5 | 82.5
2.2 | 50 | 6 | IE3 | 84.3 | 84.3
3 | 50 | 6 | IE3 | 85.6 | 85.6
4 | 50 | 6 | IE3 | 86.8 | 86.8
5.5 | 50 | 6 | IE3 | 88 | 88
7.5 | 50 | 6 | IE3 | 89.1 | 89.1
11 | 50 | 6 | IE3 | 90.3 | 90.3
15 | 50 | 6 | IE3 | 91.2 | 91.2
18.5 | 50 | 6 | IE3 | 91.7 | 91.7
22 | 50 | 6 | IE3 | 92.2 | 92.2
30 | 50 | 6 | IE3 | 92.9 | 92.9
37 | 50 | 6 | IE3 | 93.3 | 93.3
45 | 50 | 6 | IE3 | 93.7 | 93.7
55 | 50 | 6 | IE3 | 94.1 | 94.1
75 | 50 | 6 | IE3 | 94.6 | 94.6
90 | 50 | 6 | IE3 | 94.9 | 94.9
110 | 50 | 6 | IE3 | 95.1 | 95.1
132 | 50 | 6 | IE3 | 95.4 | 95.4
160 | 50 | 6 | IE3 | 95.6 | 95.6
200 | 50 | 6 | IE3 | 95.8 | 95.8
250 | 50 | 6 | IE3 | 95.8 | 95.8
315 | 50 | 6 | IE3 | 95.8 | 95.8
355 | 50 | 6 | IE3 | 95.8 | 95.8
400 | 50 | 6 | IE3 | 95.8 | 95.8
500 | 50 | 6 | IE3 | 95.8 | 95.8
560 | 50 | 6 | IE3 | 95.8 | 95.8
630 | 50 | 6 | IE3 | 95.8 | 95.8
710 | 50 | 6 | IE3 | 95.8 | 95.8
800 | 50 | 6 | IE3 | 95.8 | 95.8
900 | 50 | 6 | IE3 | 95.8 | 95.8
1000 | 50 | 6 | IE3 | 95.8 | 95.8
0.12 | 50 | 8 | IE3 | 50.7 | 49.8811
0.18 | 50 | 8 | IE3 | 58.7 | 57.9366
0.25 | 50 | 8 | IE3 | 64.1 | 63.3733
0.37 | 50 | 8 | IE3 | 69.3 | 68.6007
0.55 | 50 | 8 | IE3 | 73 | 72.295
0.75 | 50 | 8 | IE3 | 75 | 75
1.1 | 50 | 8 | IE3 | 77.7 | 77.7
1.5 | 50 | 8 | IE3 | 79.7 | 79.7
2.2 | 50 | 8 | IE3 | 81.9 | 81.9
3 | 50 | 8 | IE3 | 83.5 | 83.5
4 | 50 | 8 | IE3 | 84.8 | 84.8
5.5 | 50 | 8 | IE3 | 86.2 | 86.2
7.5 | 50 | 8 | IE3 | 87.3 | 87.3
11 | 50 | 8 | IE3 | 88.6 | 88.6
15 | 50 | 8 | IE3 | 89.6 | 89.6
18.5 | 50 | 8 | IE3 | 90.1 | 90.1
22 | 50 | 8 | IE3 | 90.6 | 90.6
30 | 50 | 8 | IE3 | 91.3 | 91.3
37 | 50 | 8 | IE3 | 91.8 | 91.8
45 | 50 | 8 | IE3 | 92.2 | 92.2
55 | 50 | 8 | IE3 | 92.5 | 92.5
75 | 50 | 8 | IE3 | 93.1 | 93.1
90 | 50 | 8 | IE3 | 93.4 | 93.4
110 | 50 | 8 | IE3 | 93.7 | 93.7
132 | 50 | 8 | IE3 | 94 | 94
160 | 50 | 8 | IE3 | 94.3 | 94.3
200 | 50 | 8 | IE3 | 94.6 | 94.6
250 | 50 | 8 | IE3 | 94.6 | 94.6
315 | 50 | 8 | IE3 | 94.6 | 94.6
355 | 50 | 8 | IE3 | 94.6 | 94.6
400 | 50 | 8 | IE3 | 94.6 | 94.6
500 | 50 | 8 | IE3 | 94.6 | 94.6
560 | 50 | 8 | IE3 | 94.6 | 94.6
630 | 50 | 8 | IE3 | 94.6 | 94.6
710 | 50 | 8 | IE3 | 94.6 | 94.6
800 | 50 | 8 | IE3 | 94.6 | 94.6
900 | 50 | 8 | IE3 | 94.6 | 94.6
1000 | 50 | 8 | IE3 | 94.6 | 94.6
IE4
|  |  |  | 34-30-2 | Estimation
Losses increased |  |  |  | Nominal | 75% Load
Power [kW] | f / Hz | Poles | Class | % | %
0.12 | 50 | 4 | IE4 | 69.8 | 69.0616
0.18 | 50 | 4 | IE4 | 74.7 | 74.7
0.25 | 50 | 4 | IE4 | 77.9 | 77.9
0.37 | 50 | 4 | IE4 | 81.1 | 81.1
0.55 | 50 | 4 | IE4 | 83.9 | 83.9
0.75 | 50 | 4 | IE4 | 85.7 | 85.7
1.1 | 50 | 4 | IE4 | 87.2 | 87.2
1.5 | 50 | 4 | IE4 | 88.2 | 88.2
2.2 | 50 | 4 | IE4 | 89.5 | 89.8344
3 | 50 | 4 | IE4 | 90.4 | 90.731
4 | 50 | 4 | IE4 | 91.1 | 91.4321
5.5 | 50 | 4 | IE4 | 91.9 | 92.2293
7.5 | 50 | 4 | IE4 | 92.6 | 92.9274
11 | 50 | 4 | IE4 | 93.3 | 93.6284
15 | 50 | 4 | IE4 | 93.9 | 94.2245
18.5 | 50 | 4 | IE4 | 94.2 | 94.2
22 | 50 | 4 | IE4 | 94.5 | 94.5
30 | 50 | 4 | IE4 | 94.9 | 94.9
37 | 50 | 4 | IE4 | 95.2 | 95.2
45 | 50 | 4 | IE4 | 95.4 | 95.4
55 | 50 | 4 | IE4 | 95.7 | 95.7
75 | 50 | 4 | IE4 | 96 | 96
90 | 50 | 4 | IE4 | 96.1 | 96.1
110 | 50 | 4 | IE4 | 96.3 | 96.3
132 | 50 | 4 | IE4 | 96.4 | 96.4
160 | 50 | 4 | IE4 | 96.6 | 96.6
200 | 50 | 4 | IE4 | 96.7 | 96.7
250 | 50 | 4 | IE4 | 96.7 | 96.7
315 | 50 | 4 | IE4 | 96.7 | 96.7
355 | 50 | 4 | IE4 | 96.7 | 96.7
400 | 50 | 4 | IE4 | 96.7 | 96.7
500 | 50 | 4 | IE4 | 96.7 | 96.7
560 | 50 | 4 | IE4 | 96.7 | 96.7
630 | 50 | 4 | IE4 | 96.7 | 96.7
710 | 50 | 4 | IE4 | 96.7 | 96.7
800 | 50 | 4 | IE4 | 96.7 | 96.7
900 | 50 | 4 | IE4 | 96.7 | 96.7
1000 | 50 | 4 | IE4 | 96.7 | 96.7
0.12 | 50 | 2 | IE4 | 66.5 | 65.778
0.18 | 50 | 2 | IE4 | 70.8 | 70.0626
0.25 | 50 | 2 | IE4 | 74.3 | 73.5699
0.37 | 50 | 2 | IE4 | 78.1 | 77.382
0.55 | 50 | 2 | IE4 | 81.5 | 80.7857
0.75 | 50 | 2 | IE4 | 83.5 | 83.5
1.1 | 50 | 2 | IE4 | 85.2 | 85.2
1.5 | 50 | 2 | IE4 | 86.5 | 86.5
2.2 | 50 | 2 | IE4 | 88 | 88
3 | 50 | 2 | IE4 | 89.1 | 89.1
4 | 50 | 2 | IE4 | 90 | 90
5.5 | 50 | 2 | IE4 | 90.9 | 90.9
7.5 | 50 | 2 | IE4 | 91.7 | 91.7
11 | 50 | 2 | IE4 | 92.6 | 92.6
15 | 50 | 2 | IE4 | 93.3 | 93.3
18.5 | 50 | 2 | IE4 | 93.7 | 93.7
22 | 50 | 2 | IE4 | 94 | 94
30 | 50 | 2 | IE4 | 94.5 | 94.5
37 | 50 | 2 | IE4 | 94.8 | 94.8
45 | 50 | 2 | IE4 | 95 | 95
55 | 50 | 2 | IE4 | 95.3 | 95.3
75 | 50 | 2 | IE4 | 95.6 | 95.6
90 | 50 | 2 | IE4 | 95.8 | 95.8
110 | 50 | 2 | IE4 | 96 | 96
132 | 50 | 2 | IE4 | 96.2 | 96.2
160 | 50 | 2 | IE4 | 96.3 | 96.3
200 | 50 | 2 | IE4 | 96.5 | 96.5
250 | 50 | 2 | IE4 | 96.5 | 96.5
315 | 50 | 2 | IE4 | 96.5 | 96.5
355 | 50 | 2 | IE4 | 96.5 | 96.5
400 | 50 | 2 | IE4 | 96.5 | 96.5
500 | 50 | 2 | IE4 | 96.5 | 96.5
560 | 50 | 2 | IE4 | 96.5 | 96.5
630 | 50 | 2 | IE4 | 96.5 | 96.5
710 | 50 | 2 | IE4 | 96.5 | 96.5
800 | 50 | 2 | IE4 | 96.5 | 96.5
900 | 50 | 2 | IE4 | 96.5 | 96.5
1000 | 50 | 2 | IE4 | 96.5 | 96.5
0.12 | 50 | 6 | IE4 | 64.9 | 64.1895
0.18 | 50 | 6 | IE4 | 70.1 | 69.4111
0.25 | 50 | 6 | IE4 | 74.1 | 73.4255
0.37 | 50 | 6 | IE4 | 78 | 77.321
0.55 | 50 | 6 | IE4 | 80.9 | 80.19
0.75 | 50 | 6 | IE4 | 82.7 | 82.7
1.1 | 50 | 6 | IE4 | 84.5 | 84.5
1.5 | 50 | 6 | IE4 | 85.9 | 85.9
2.2 | 50 | 6 | IE4 | 87.4 | 87.4
3 | 50 | 6 | IE4 | 88.6 | 88.6
4 | 50 | 6 | IE4 | 89.5 | 89.5
5.5 | 50 | 6 | IE4 | 90.5 | 90.5
7.5 | 50 | 6 | IE4 | 91.3 | 91.3
11 | 50 | 6 | IE4 | 92.3 | 92.3
15 | 50 | 6 | IE4 | 92.9 | 92.9
18.5 | 50 | 6 | IE4 | 93.4 | 93.4
22 | 50 | 6 | IE4 | 93.7 | 93.7
30 | 50 | 6 | IE4 | 94.2 | 94.2
37 | 50 | 6 | IE4 | 94.5 | 94.5
45 | 50 | 6 | IE4 | 94.8 | 94.8
55 | 50 | 6 | IE4 | 95.1 | 95.1
75 | 50 | 6 | IE4 | 95.4 | 95.4
90 | 50 | 6 | IE4 | 95.6 | 95.6
110 | 50 | 6 | IE4 | 95.8 | 95.8
132 | 50 | 6 | IE4 | 96 | 96
160 | 50 | 6 | IE4 | 96.2 | 96.2
200 | 50 | 6 | IE4 | 96.3 | 96.3
250 | 50 | 6 | IE4 | 96.5 | 96.5
315 | 50 | 6 | IE4 | 96.6 | 96.6
355 | 50 | 6 | IE4 | 96.6 | 96.6
400 | 50 | 6 | IE4 | 96.6 | 96.6
500 | 50 | 6 | IE4 | 96.6 | 96.6
560 | 50 | 6 | IE4 | 96.6 | 96.6
630 | 50 | 6 | IE4 | 96.6 | 96.6
710 | 50 | 6 | IE4 | 96.6 | 96.6
800 | 50 | 6 | IE4 | 96.6 | 96.6
900 | 50 | 6 | IE4 | 96.6 | 96.6
1000 | 50 | 6 | IE4 | 96.6 | 96.6
0.12 | 50 | 8 | IE4 | 62.3 | 61.6738
0.18 | 50 | 8 | IE4 | 67.2 | 66.5937
0.25 | 50 | 8 | IE4 | 70.8 | 70.2089
0.37 | 50 | 8 | IE4 | 74.3 | 73.7146
0.55 | 50 | 8 | IE4 | 77 | 76.3995
0.75 | 50 | 8 | IE4 | 78.4 | 78.4
1.1 | 50 | 8 | IE4 | 80.8 | 80.8
1.5 | 50 | 8 | IE4 | 82.6 | 82.6
2.2 | 50 | 8 | IE4 | 84.5 | 84.5
3 | 50 | 8 | IE4 | 85.9 | 85.9
4 | 50 | 8 | IE4 | 87.1 | 87.1
5.5 | 50 | 8 | IE4 | 88.3 | 88.3
7.5 | 50 | 8 | IE4 | 89.3 | 89.3
11 | 50 | 8 | IE4 | 90.4 | 90.4
15 | 50 | 8 | IE4 | 91.2 | 91.2
18.5 | 50 | 8 | IE4 | 91.7 | 91.7
22 | 50 | 8 | IE4 | 92.1 | 92.1
30 | 50 | 8 | IE4 | 92.7 | 92.7
37 | 50 | 8 | IE4 | 93.1 | 93.1
45 | 50 | 8 | IE4 | 93.4 | 93.4
55 | 50 | 8 | IE4 | 93.7 | 93.7
75 | 50 | 8 | IE4 | 94.2 | 94.2
90 | 50 | 8 | IE4 | 94.4 | 94.4
110 | 50 | 8 | IE4 | 94.7 | 94.7
132 | 50 | 8 | IE4 | 94.9 | 94.9
160 | 50 | 8 | IE4 | 95.1 | 95.1
200 | 50 | 8 | IE4 | 95.4 | 95.4
250 | 50 | 8 | IE4 | 95.4 | 95.4
315 | 50 | 8 | IE4 | 95.4 | 95.4
355 | 50 | 8 | IE4 | 95.4 | 95.4
400 | 50 | 8 | IE4 | 95.4 | 95.4
500 | 50 | 8 | IE4 | 95.4 | 95.4
560 | 50 | 8 | IE4 | 95.4 | 95.4
630 | 50 | 8 | IE4 | 95.4 | 95.4
710 | 50 | 8 | IE4 | 95.4 | 95.4
800 | 50 | 8 | IE4 | 95.4 | 95.4
900 | 50 | 8 | IE4 | 95.4 | 95.4
1000 | 50 | 8 | IE4 | 95.4 | 95.4

## Motor on VFD
All data is based on the tables in IEC 61800-9-2, Annex D.4
IE2
[10 empty] | 34-30-2 | 34-30-2 | Losses | PL7 | PL3 | PL6 | PL5 | PL2 | PL4 | PL1 | Eff / %
[10 empty] | Reference | Nominal | n= | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
Power / kW | Class | Speed | cL1 | cL2 | cL3 | cL4 | cL5 | cL6 | cL7 | % | % | T= | 0.25 | 1 | 0.25 | 0.5 | 1 | 0.5 | 1 | 1
0.12 | IE2 | 1500 | 0.32432 | 0.11659 | 0.076506 | 0.0029873 | 0.0039144 | -0.29282 | 0.55186 | 59.1 | 55.6838 |  | 0.31959 | 0.61827 | 0.36318 | 0.39391 | 0.66324 | 0.51069 | 0.78334 | 56.0744
0.18 | IE2 | 1500 | 0.25022 | 0.094236 | 0.061948 | 0.0020824 | 0.0029485 | -0.11952 | 0.31662 | 64.7 | 61.4464 |  | 0.26761 | 0.47547 | 0.30285 | 0.33267 | 0.51172 | 0.42706 | 0.60855 | 62.1679
0.25 | IE2 | 1500 | 0.19566 | 0.083798 | 0.060563 | 0.0059594 | 0.0067848 | -0.10021 | 0.24935 | 68.5 | 65.4094 |  | 0.21104 | 0.37144 | 0.24352 | 0.2661 | 0.40651 | 0.35544 | 0.5019 | 66.5823
0.37 | IE2 | 1500 | 0.1371 | 0.062496 | 0.042114 | 0.0040639 | 0.0045614 | -0.042812 | 0.20437 | 72.7 | 69.84 |  | 0.15751 | 0.31821 | 0.18114 | 0.20935 | 0.3436 | 0.27355 | 0.41189 | 70.8271
0.55 | IE2 | 1500 | 0.11148 | 0.04733 | 0.031814 | 9.537e-06 | 0.00041586 | -0.026457 | 0.16136 | 77.1 | 74.5396 |  | 0.12878 | 0.26024 | 0.14658 | 0.17024 | 0.27811 | 0.21784 | 0.32596 | 75.4173
0.75 | IE2 | 1500 | 0.085781 | 0.04166 | 0.026726 | 0.001532 | 0.0018556 | -0.020927 | 0.1524 | 79.6 | 77.2366 |  | 0.10219 | 0.22984 | 0.11766 | 0.14124 | 0.246 | 0.18265 | 0.28903 | 77.5778
1.1 | IE2 | 1500 | 0.069172 | 0.038244 | 0.02724 | 0.00087186 | 0.0013175 | -0.016191 | 0.14077 | 81.4 | 79.1906 |  | 0.085205 | 0.20531 | 0.099902 | 0.12239 | 0.22044 | 0.1623 | 0.26142 | 79.2757
1.5 | IE2 | 1500 | 0.05958 | 0.03476 | 0.022242 | 0.0011551 | 0.0016386 | -0.018775 | 0.13828 | 82.8 | 80.7175 |  | 0.073634 | 0.18956 | 0.086531 | 0.10795 | 0.20301 | 0.14246 | 0.23888 | 80.7181
2.2 | IE2 | 1500 | 0.036978 | 0.031347 | 0.021183 | 0.0098769 | 0.0084467 | 0.01619 | 0.091365 | 84.3 | 82.3604 |  | 0.056084 | 0.15669 | 0.068146 | 0.090646 | 0.17255 | 0.12503 | 0.21539 | 82.2783
3 | IE2 | 1500 | 0.038845 | 0.026351 | 0.015957 | 0.0044167 | 0.0046056 | -0.008363 | 0.11067 | 85.5 | 83.68 |  | 0.051343 | 0.15013 | 0.061046 | 0.080335 | 0.16167 | 0.10689 | 0.19248 | 83.8588
4 | IE2 | 1500 | 0.034853 | 0.027515 | 0.019177 | 0.0041634 | 0.0046914 | -0.012966 | 0.098248 | 86.6 | 84.8936 |  | 0.045912 | 0.12955 | 0.056507 | 0.072297 | 0.14194 | 0.10184 | 0.17568 | 85.057
5.5 | IE2 | 1500 | 0.029206 | 0.02454 | 0.018285 | 0.0072723 | 0.0076643 | -0.0094364 | 0.084946 | 87.7 | 86.1112 |  | 0.039577 | 0.11429 | 0.049344 | 0.063953 | 0.12711 | 0.092283 | 0.16248 | 86.0233
7.5 | IE2 | 1500 | 0.023744 | 0.022127 | 0.015244 | 0.0067529 | 0.0071959 | -0.016095 | 0.091724 | 88.7 | 87.2216 |  | 0.032071 | 0.108 | 0.040651 | 0.054796 | 0.11942 | 0.079486 | 0.15069 | 86.9042
11 | IE2 | 1500 | 0.019974 | 0.020315 | 0.014864 | 0.0057629 | 0.0059652 | -0.009032 | 0.072826 | 89.8 | 88.4468 |  | 0.028388 | 0.091588 | 0.036414 | 0.04863 | 0.10201 | 0.071775 | 0.13067 | 88.4428
15 | IE2 | 1500 | 0.016536 | 0.018496 | 0.013898 | 0.0061726 | 0.006388 | -0.0077659 | 0.064775 | 90.6 | 89.3403 |  | 0.024257 | 0.08098 | 0.031659 | 0.042741 | 0.090951 | 0.064382 | 0.1185 | 89.4054
18.5 | IE2 | 1500 | 0.014915 | 0.017047 | 0.012419 | 0.0055589 | 0.0057287 | -0.005309 | 0.063114 | 91.2 | 90.0118 |  | 0.022679 | 0.079506 | 0.029423 | 0.04072 | 0.08856 | 0.060326 | 0.11347 | 89.8091
22 | IE2 | 1500 | 0.014521 | 0.016611 | 0.012614 | 0.0025678 | 0.0028262 | -0.0056102 | 0.060415 | 91.6 | 90.4602 |  | 0.021886 | 0.075085 | 0.028477 | 0.038776 | 0.082774 | 0.057392 | 0.10394 | 90.5843
30 | IE2 | 1500 | 0.010356 | 0.013976 | 0.0086115 | 0.0065606 | 0.0092836 | 0.00033736 | 0.048029 | 92.3 | 91.2461 |  | 0.017614 | 0.064975 | 0.022934 | 0.033074 | 0.073465 | 0.049081 | 0.097155 | 91.1448
37 | IE2 | 1500 | 0.022059 | 0.0030518 | 0.014537 | 0.0090292 | -0.0025621 | -0.0080813 | 0.053231 | 92.7 | 91.6959 |  | 0.025168 | 0.070977 | 0.028767 | 0.037454 | 0.076243 | 0.050531 | 0.091264 | 91.6369
45 | IE2 | 1500 | 0.01047 | 0.013126 | 0.011908 | 0.0046679 | 0.0047677 | -0.0029438 | 0.045438 | 93.1 | 92.1463 |  | 0.016692 | 0.058455 | 0.022335 | 0.03078 | 0.06603 | 0.047751 | 0.087434 | 91.9596
55 | IE2 | 1500 | 0.0079532 | 0.013335 | 0.012556 | 0.0048989 | 0.0051277 | 0.0010525 | 0.033639 | 93.5 | 92.5972 |  | 0.014534 | 0.048308 | 0.020358 | 0.027628 | 0.056182 | 0.045287 | 0.078562 | 92.716
75 | IE2 | 1500 | 0.0081474 | 0.012746 | 0.012559 | 0.0068676 | 0.0077474 | -0.0062491 | 0.030899 | 94 | 93.1615 |  | 0.012625 | 0.03897 | 0.018365 | 0.023603 | 0.047681 | 0.041707 | 0.072718 | 93.2211
90 | IE2 | 1500 | 0.0074223 | 0.012923 | 0.01144 | 0.006342 | 0.0063531 | -0.0021744 | 0.027528 | 94.2 | 93.3875 |  | 0.012669 | 0.038704 | 0.018218 | 0.023728 | 0.046857 | 0.040754 | 0.069834 | 93.4724
110 | IE2 | 1500 | 0.0099876 | 0.015774 | 0.012799 | 0.0061964 | 0.0062425 | -0.0024184 | 0.023835 | 94.5 | 93.2182 |  | 0.015737 | 0.038087 | 0.022251 | 0.026989 | 0.04715 | 0.04642 | 0.072416 | 93.2474
132 | IE2 | 1500 | 0.0091501 | 0.012524 | 0.0087125 | 0.0070013 | 0.0072302 | -0.0044184 | 0.029462 | 94.7 | 93.4616 |  | 0.0137 | 0.040071 | 0.018659 | 0.024073 | 0.047942 | 0.0391 | 0.069661 | 93.4876
160 | IE2 | 1500 | 0.0086853 | 0.013137 | 0.0083467 | 0.0074115 | 0.0075949 | -0.0033585 | 0.025062 | 94.9 | 93.7053 |  | 0.013363 | 0.036522 | 0.018417 | 0.023328 | 0.044648 | 0.038507 | 0.066879 | 93.7314
200 | IE2 | 1500 | 0.0082529 | 0.012361 | 0.009287 | 0.006432 | 0.0066457 | -0.0033096 | 0.024648 | 95.1 | 93.9491 |  | 0.012763 | 0.035285 | 0.017773 | 0.022482 | 0.042971 | 0.037678 | 0.064317 | 93.957
250 | IE2 | 1500 | 0.0079731 | 0.011493 | 0.0087816 | 0.0059034 | 0.0061337 | -0.0026593 | 0.022575 | 95.1 | 93.9491 |  | 0.012258 | 0.03317 | 0.016942 | 0.021351 | 0.040316 | 0.035571 | 0.060201 | 94.3217
315 | IE2 | 1500 | 0.0077257 | 0.01063 | 0.0082663 | 0.0053731 | 0.0056223 | -0.0021701 | 0.020633 | 95.1 | 93.9491 |  | 0.011753 | 0.031058 | 0.01611 | 0.020204 | 0.037663 | 0.033444 | 0.056081 | 94.6897
355 | IE2 | 1500 | 0.007304 | 0.010197 | 0.0081038 | 0.0052904 | 0.0054729 | -0.0019811 | 0.019849 | 95.1 | 93.9491 |  | 0.011209 | 0.029892 | 0.015425 | 0.019403 | 0.03631 | 0.032267 | 0.054236 | 94.8554
400 | IE2 | 1500 | 0.0065486 | 0.0097449 | 0.007804 | 0.0052587 | 0.0055072 | -0.00033514 | 0.018033 | 95.1 | 93.9491 |  | 0.01062 | 0.02883 | 0.014666 | 0.018714 | 0.035076 | 0.03113 | 0.052562 | 95.0063
500 | IE2 | 1500 | 0.006472 | 0.0093219 | 0.0077839 | 0.0051422 | 0.0051559 | -0.0016401 | 0.018292 | 95.1 | 93.9491 |  | 0.010123 | 0.027549 | 0.014053 | 0.017797 | 0.033591 | 0.029905 | 0.050528 | 95.1902
560 | IE2 | 1500 | 0.0063678 | 0.0091945 | 0.008457 | 0.0050096 | 0.0048497 | -0.0018817 | 0.01617 | 95.1 | 93.9491 |  | 0.0098325 | 0.025039 | 0.013852 | 0.01711 | 0.031085 | 0.029586 | 0.048167 | 95.4047
630 | IE2 | 1500 | 0.0059866 | 0.0089597 | 0.0092417 | 0.0051039 | 0.0051582 | -0.00082636 | 0.012893 | 95.1 | 93.9491 |  | 0.0095032 | 0.022469 | 0.013616 | 0.016547 | 0.028685 | 0.029564 | 0.046517 | 95.5551
710 | IE2 | 1500 | 0.0060269 | 0.0089926 | 0.0098642 | 0.0051232 | 0.0051548 | -0.00082531 | 0.012505 | 95.1 | 93.9491 |  | 0.0095669 | 0.022174 | 0.013805 | 0.016665 | 0.028519 | 0.030167 | 0.046841 | 95.5255
800 | IE2 | 1500 | 0.0060701 | 0.0090229 | 0.010484 | 0.0051281 | 0.0051503 | -0.0008333 | 0.012126 | 95.1 | 93.9491 |  | 0.0096309 | 0.021877 | 0.013993 | 0.01678 | 0.028347 | 0.030761 | 0.047148 | 95.4975
900 | IE2 | 1500 | 0.0057138 | 0.008565 | 0.0094401 | 0.0051224 | 0.0051443 | -0.00088693 | 0.011977 | 95.1 | 93.9491 |  | 0.009072 | 0.021137 | 0.013124 | 0.015869 | 0.027294 | 0.028836 | 0.045076 | 95.6868
1000 | IE2 | 1500 | 0.005341 | 0.0081103 | 0.0083969 | 0.0051071 | 0.0051317 | -0.00087237 | 0.011765 | 95.1 | 93.9491 |  | 0.0085105 | 0.020384 | 0.012252 | 0.01496 | 0.026225 | 0.026913 | 0.04298 | 95.8791
0.12 | IE2 | 3000 | 0.30922 | 0.11162 | 0.11078 | -0.0013222 | 0.0029596 | -0.38355 | 0.72192 | 53.6 | 50.1122 |  | 0.29327 | 0.68227 | 0.34196 | 0.38145 | 0.73118 | 0.52073 | 0.87163 | 53.4293
0.18 | IE2 | 3000 | 0.274 | 0.083806 | 0.11529 | 0.0025875 | 0.0047089 | -0.34892 | 0.56111 | 60.4 | 57.0134 |  | 0.25005 | 0.51529 | 0.29272 | 0.31116 | 0.55939 | 0.44074 | 0.69259 | 59.0811
0.25 | IE2 | 3000 | 0.16754 | 0.073171 | 0.088958 | 0.0038667 | 0.0070111 | -0.18919 | 0.44092 | 64.8 | 61.5502 |  | 0.17174 | 0.44452 | 0.20686 | 0.24292 | 0.48178 | 0.34802 | 0.59227 | 62.8033
0.37 | IE2 | 3000 | 0.11036 | 0.055126 | 0.073582 | 0.0090974 | 0.011939 | -0.12104 | 0.31115 | 69.5 | 66.4595 |  | 0.11811 | 0.32186 | 0.14597 | 0.17547 | 0.35395 | 0.26159 | 0.45021 | 68.9558
0.55 | IE2 | 3000 | 0.07895 | 0.048581 | 0.063063 | 0.010411 | 0.013178 | -0.090696 | 0.25901 | 74.1 | 71.3289 |  | 0.088765 | 0.26678 | 0.11305 | 0.14054 | 0.29582 | 0.2159 | 0.3825 | 72.3329
0.75 | IE2 | 3000 | 0.070365 | 0.034987 | 0.032732 | 0.0087463 | 0.013292 | -0.049085 | 0.2387 | 77.4 | 74.8622 |  | 0.083993 | 0.27379 | 0.09917 | 0.1331 | 0.29335 | 0.17873 | 0.34974 | 74.0884
1.1 | IE2 | 3000 | 0.056385 | 0.031303 | 0.03086 | 0.0057932 | 0.0071145 | -0.035794 | 0.18016 | 79.6 | 77.2366 |  | 0.068569 | 0.2124 | 0.082355 | 0.10806 | 0.22879 | 0.14892 | 0.27582 | 78.3809
1.5 | IE2 | 3000 | 0.060191 | 0.030829 | 0.040748 | 0.00090363 | 0.0015935 | -0.022733 | 0.13669 | 81.3 | 79.0818 |  | 0.073325 | 0.18473 | 0.088706 | 0.10881 | 0.2006 | 0.1552 | 0.24823 | 80.1137
2.2 | IE2 | 3000 | 0.059162 | 0.03119 | 0.033312 | 0.0019138 | 0.0025866 | -0.028384 | 0.13722 | 83.2 | 81.1549 |  | 0.070562 | 0.17852 | 0.084666 | 0.1036 | 0.19353 | 0.1449 | 0.237 | 80.8405
3 | IE2 | 3000 | 0.043406 | 0.026104 | 0.028245 | 0.0057605 | 0.0060966 | -0.011705 | 0.11151 | 84.6 | 82.6899 |  | 0.055854 | 0.15333 | 0.067838 | 0.086646 | 0.16773 | 0.12275 | 0.20942 | 82.6842
4 | IE2 | 3000 | 0.031784 | 0.023241 | 0.027211 | 0.012913 | 0.013211 | -0.012423 | 0.095823 | 85.8 | 84.0106 |  | 0.042431 | 0.12675 | 0.0537 | 0.070391 | 0.14337 | 0.10651 | 0.19176 | 83.9096
5.5 | IE2 | 3000 | 0.028954 | 0.021007 | 0.030026 | 0.0027593 | 0.0031506 | -0.01074 | 0.088128 | 87 | 85.3359 |  | 0.038961 | 0.11436 | 0.049923 | 0.064168 | 0.12652 | 0.098127 | 0.16328 | 85.9635
7.5 | IE2 | 3000 | 0.024405 | 0.015308 | 0.019826 | 0.008659 | 0.008659 | -0.015092 | 0.085584 | 88.1 | 86.555 |  | 0.031216 | 0.10267 | 0.038997 | 0.052489 | 0.114 | 0.077718 | 0.14735 | 87.1574 | Error in Tables of 61800-9-2 has been corrected
11 | IE2 | 3000 | 0.016563 | 0.013228 | 0.014879 | 0.0061385 | 0.0062949 | -0.007512 | 0.067897 | 89.4 | 88.0008 |  | 0.023286 | 0.083114 | 0.029553 | 0.041276 | 0.091925 | 0.060997 | 0.11749 | 89.4863
15 | IE2 | 3000 | 0.016368 | 0.013568 | 0.02561 | 0.005575 | 0.0058481 | -0.0049066 | 0.059672 | 90.3 | 89.005 |  | 0.023973 | 0.077885 | 0.032323 | 0.043082 | 0.08857 | 0.070867 | 0.12174 | 89.1476
18.5 | IE2 | 3000 | 0.014745 | 0.011859 | 0.024222 | 0.0051097 | 0.0052638 | -0.0054358 | 0.052023 | 90.9 | 89.6759 |  | 0.021216 | 0.067417 | 0.028864 | 0.037985 | 0.077188 | 0.063707 | 0.10779 | 90.2701
22 | IE2 | 3000 | 0.011104 | 0.011228 | 0.019121 | 0.0060701 | 0.0062073 | -0.0041754 | 0.047999 | 91.3 | 90.1239 |  | 0.017181 | 0.060835 | 0.023741 | 0.032557 | 0.069909 | 0.054434 | 0.097554 | 91.1117
30 | IE2 | 3000 | 0.010892 | 0.010729 | 0.023913 | 0.0067917 | 0.0069587 | -0.0016682 | 0.040827 | 92 | 90.9091 |  | 0.017337 | 0.05636 | 0.02469 | 0.032891 | 0.066529 | 0.058344 | 0.098443 | 91.038
37 | IE2 | 3000 | 0.0098437 | 0.0091146 | 0.020941 | 0.0066408 | 0.0069573 | -0.0066463 | 0.04498 | 92.5 | 91.471 |  | 0.014712 | 0.05386 | 0.021102 | 0.028823 | 0.063029 | 0.05122 | 0.091831 | 91.5893
45 | IE2 | 3000 | 0.0079752 | 0.011238 | 0.019297 | 0.0039999 | 0.0043732 | -0.0029118 | 0.031165 | 92.9 | 91.921 |  | 0.01329 | 0.041517 | 0.019832 | 0.025527 | 0.049765 | 0.046939 | 0.075137 | 93.0114
55 | IE2 | 3000 | 0.00808 | 0.0094757 | 0.021905 | 0.004978 | 0.0048386 | -0.000467 | 0.030347 | 93.2 | 92.259 |  | 0.013695 | 0.043245 | 0.020305 | 0.026572 | 0.051873 | 0.049268 | 0.079157 | 92.6649
75 | IE2 | 3000 | 0.0081741 | 0.0095239 | 0.026133 | 0.0022451 | 0.0025463 | -0.0014707 | 0.025651 | 93.8 | 92.9357 |  | 0.013469 | 0.037089 | 0.020815 | 0.025586 | 0.045409 | 0.050706 | 0.072802 | 93.2138
90 | IE2 | 3000 | 0.010468 | 0.012436 | 0.020174 | 0.004593 | 0.0045924 | -0.00084934 | 0.02423 | 94.1 | 93.2745 |  | 0.01623 | 0.039654 | 0.023247 | 0.028224 | 0.048555 | 0.051008 | 0.075645 | 92.9675
110 | IE2 | 3000 | 0.0084633 | 0.010116 | 0.0194 | 0.0040501 | 0.0040785 | -0.0012511 | 0.019566 | 94.3 | 92.9751 |  | 0.013194 | 0.031787 | 0.019471 | 0.023398 | 0.039731 | 0.044277 | 0.064422 | 93.9477
132 | IE2 | 3000 | 0.007975 | 0.0089276 | 0.017852 | 0.0046019 | 0.0046405 | -0.00116 | 0.019363 | 94.6 | 93.3399 |  | 0.012333 | 0.030967 | 0.018038 | 0.022028 | 0.038566 | 0.041326 | 0.0622 | 94.1442
160 | IE2 | 3000 | 0.0074887 | 0.0077383 | 0.016304 | 0.0051476 | 0.0052033 | -0.0010809 | 0.019173 | 94.8 | 93.5834 |  | 0.011471 | 0.030146 | 0.016604 | 0.020655 | 0.0374 | 0.038371 | 0.059974 | 94.342
200 | IE2 | 3000 | 0.0075126 | 0.008009 | 0.013136 | 0.0057848 | 0.0062846 | -0.0036405 | 0.020405 | 95 | 93.8272 |  | 0.010816 | 0.028939 | 0.015445 | 0.019198 | 0.036029 | 0.034956 | 0.057492 | 94.5634
250 | IE2 | 3000 | 0.0073358 | 0.0074306 | 0.015691 | 0.0051612 | 0.0051826 | -0.0011112 | 0.016732 | 95 | 93.8272 |  | 0.011043 | 0.027409 | 0.015984 | 0.01957 | 0.034471 | 0.03667 | 0.056421 | 94.6592
315 | IE2 | 3000 | 0.0065008 | 0.0069902 | 0.012831 | 0.0051406 | 0.0051609 | -0.0011648 | 0.01642 | 95 | 93.8272 |  | 0.0098858 | 0.025914 | 0.01418 | 0.017692 | 0.03232 | 0.03242 | 0.051879 | 95.0679
355 | IE2 | 3000 | 0.0061966 | 0.0066335 | 0.012262 | 0.0051284 | 0.0051488 | -0.0011572 | 0.015445 | 95 | 93.8272 |  | 0.0093976 | 0.024513 | 0.013495 | 0.016824 | 0.030718 | 0.030944 | 0.049656 | 95.2693
400 | IE2 | 3000 | 0.0058874 | 0.006273 | 0.011683 | 0.0051271 | 0.0051527 | -0.001124 | 0.014452 | 95 | 93.8272 |  | 0.0089084 | 0.023118 | 0.012808 | 0.015959 | 0.029125 | 0.029464 | 0.047451 | 95.4698
500 | IE2 | 3000 | 0.0055707 | 0.0059154 | 0.011114 | 0.0051144 | 0.0051404 | -0.0010541 | 0.013422 | 95 | 93.8272 |  | 0.0084195 | 0.021712 | 0.012122 | 0.015096 | 0.027517 | 0.027992 | 0.045223 | 95.6734
560 | IE2 | 3000 | 0.0054257 | 0.0058394 | 0.011092 | 0.005071 | 0.0051853 | -0.0010092 | 0.012458 | 95 | 93.8272 |  | 0.0082046 | 0.020619 | 0.011884 | 0.014686 | 0.026399 | 0.027531 | 0.044062 | 95.7797
630 | IE2 | 3000 | 0.0052222 | 0.0057339 | 0.011155 | 0.0050724 | 0.0051447 | -0.00067823 | 0.011237 | 95 | 93.8272 |  | 0.007985 | 0.019501 | 0.01165 | 0.014304 | 0.025259 | 0.027136 | 0.042887 | 95.8876
710 | IE2 | 3000 | 0.0052261 | 0.0056554 | 0.012328 | 0.0050948 | 0.0051419 | -0.00057726 | 0.0098477 | 95 | 93.8272 |  | 0.0079814 | 0.018276 | 0.011847 | 0.014267 | 0.024239 | 0.027943 | 0.042717 | 95.9033
800 | IE2 | 3000 | 0.005216 | 0.0055934 | 0.013485 | 0.005074 | 0.0051624 | -0.00043522 | 0.0084386 | 95 | 93.8272 |  | 0.0079753 | 0.017052 | 0.012042 | 0.014233 | 0.023215 | 0.028745 | 0.042534 | 95.9201
900 | IE2 | 3000 | 0.005054 | 0.0053074 | 0.012116 | 0.0050898 | 0.005136 | -0.00065335 | 0.0094441 | 95 | 93.8272 |  | 0.0076646 | 0.017522 | 0.011403 | 0.013728 | 0.023356 | 0.027069 | 0.041494 | 96.0159
1000 | IE2 | 3000 | 0.0048746 | 0.0050399 | 0.010724 | 0.005098 | 0.0051211 | -0.00081396 | 0.010403 | 95 | 93.8272 |  | 0.0073512 | 0.017988 | 0.010762 | 0.013227 | 0.023494 | 0.025387 | 0.040447 | 96.1125
0.12 | IE2 | 1000 | 0.45752 | 0.16447 | 0.10793 | 0.0042143 | 0.0055221 | -0.41309 | 0.77852 | 50.6 | 47.1092 |  | 0.45085 | 0.8722 | 0.51234 | 0.55569 | 0.93565 | 0.72044 | 1.1051 | 47.5042
0.18 | IE2 | 1000 | 0.35167 | 0.13244 | 0.087063 | 0.0029266 | 0.0041439 | -0.16797 | 0.44499 | 56.6 | 53.1406 |  | 0.3761 | 0.66823 | 0.42563 | 0.46754 | 0.71917 | 0.6002 | 0.85526 | 53.9008
0.25 | IE2 | 1000 | 0.26523 | 0.1136 | 0.082098 | 0.0080785 | 0.0091975 | -0.13585 | 0.33802 | 61.6 | 58.2451 |  | 0.28609 | 0.50353 | 0.33012 | 0.36072 | 0.55106 | 0.48183 | 0.68037 | 59.5106
0.37 | IE2 | 1000 | 0.17499 | 0.079766 | 0.053752 | 0.005187 | 0.0058219 | -0.054643 | 0.26084 | 67.6 | 64.4669 |  | 0.20103 | 0.40615 | 0.2312 | 0.26721 | 0.43856 | 0.34915 | 0.52572 | 65.543
0.55 | IE2 | 1000 | 0.13812 | 0.058639 | 0.039416 | 1.1816e-05 | 0.00051523 | -0.032779 | 0.19992 | 73.1 | 70.2648 |  | 0.15955 | 0.32242 | 0.1816 | 0.21092 | 0.34457 | 0.2699 | 0.40384 | 71.2331
0.75 | IE2 | 1000 | 0.10628 | 0.051615 | 0.033112 | 0.0018981 | 0.002299 | -0.025928 | 0.18882 | 75.9 | 73.2519 |  | 0.12661 | 0.28476 | 0.14578 | 0.17499 | 0.30478 | 0.2263 | 0.3581 | 73.6325
1.1 | IE2 | 1000 | 0.084886 | 0.046932 | 0.033428 | 0.0010699 | 0.0016168 | -0.019869 | 0.17274 | 78.1 | 75.616 |  | 0.10456 | 0.25195 | 0.1226 | 0.1502 | 0.27052 | 0.19917 | 0.32081 | 75.7113
1.5 | IE2 | 1000 | 0.072603 | 0.042357 | 0.027103 | 0.0014076 | 0.0019968 | -0.022878 | 0.1685 | 79.8 | 77.4532 |  | 0.089728 | 0.23099 | 0.10544 | 0.13154 | 0.24738 | 0.1736 | 0.29109 | 77.4538
2.2 | IE2 | 1000 | 0.044176 | 0.037449 | 0.025307 | 0.0118 | 0.010091 | 0.019341 | 0.10915 | 81.8 | 79.6262 |  | 0.067001 | 0.18719 | 0.081411 | 0.10829 | 0.20614 | 0.14936 | 0.25732 | 79.5346
3 | IE2 | 1000 | 0.04592 | 0.031151 | 0.018864 | 0.0052211 | 0.0054445 | -0.0098863 | 0.13083 | 83.3 | 81.2643 |  | 0.060695 | 0.17747 | 0.072165 | 0.094968 | 0.19112 | 0.12636 | 0.22754 | 81.4638
4 | IE2 | 1000 | 0.041002 | 0.032369 | 0.022561 | 0.0048979 | 0.005519 | -0.015253 | 0.11558 | 84.6 | 82.6899 |  | 0.054013 | 0.1524 | 0.066476 | 0.085052 | 0.16698 | 0.1198 | 0.20668 | 82.8723
5.5 | IE2 | 1000 | 0.033899 | 0.028484 | 0.021224 | 0.0084411 | 0.008896 | -0.010953 | 0.098598 | 86 | 84.2311 |  | 0.045937 | 0.13266 | 0.057274 | 0.074231 | 0.14754 | 0.10711 | 0.18859 | 84.1334
7.5 | IE2 | 1000 | 0.027359 | 0.025496 | 0.017564 | 0.0077809 | 0.0082913 | -0.018545 | 0.10569 | 87.2 | 85.5573 |  | 0.036953 | 0.12444 | 0.046839 | 0.063138 | 0.1376 | 0.091586 | 0.17363 | 85.2055
11 | IE2 | 1000 | 0.022402 | 0.022784 | 0.016671 | 0.0064635 | 0.0066905 | -0.01013 | 0.08168 | 88.7 | 87.2216 |  | 0.03184 | 0.10272 | 0.040841 | 0.054543 | 0.11442 | 0.080501 | 0.14656 | 87.2173
15 | IE2 | 1000 | 0.018301 | 0.020471 | 0.015381 | 0.0068314 | 0.0070699 | -0.0085948 | 0.071689 | 89.7 | 88.3352 |  | 0.026847 | 0.089624 | 0.035038 | 0.047303 | 0.10066 | 0.071254 | 0.13115 | 88.4057
18.5 | IE2 | 1000 | 0.016415 | 0.018761 | 0.013668 | 0.0061179 | 0.0063048 | -0.0058429 | 0.069461 | 90.4 | 89.1167 |  | 0.02496 | 0.087501 | 0.032382 | 0.044815 | 0.097466 | 0.066393 | 0.12488 | 88.898
22 | IE2 | 1000 | 0.015852 | 0.018134 | 0.01377 | 0.0028032 | 0.0030853 | -0.0061245 | 0.065953 | 90.9 | 89.6759 |  | 0.023893 | 0.081968 | 0.031088 | 0.04233 | 0.090363 | 0.062654 | 0.11347 | 89.8091
30 | IE2 | 1000 | 0.011236 | 0.015164 | 0.0093432 | 0.0071181 | 0.010073 | 0.00036603 | 0.05211 | 91.7 | 90.5724 |  | 0.01911 | 0.070497 | 0.024882 | 0.035884 | 0.079708 | 0.053252 | 0.10541 | 90.4641
37 | IE2 | 1000 | 0.023697 | 0.0032785 | 0.015616 | 0.0096999 | -0.0027524 | -0.0086817 | 0.057186 | 92.2 | 91.1337 |  | 0.027038 | 0.07625 | 0.030905 | 0.040237 | 0.081907 | 0.054285 | 0.098044 | 91.0711
45 | IE2 | 1000 | 0.011125 | 0.013947 | 0.012653 | 0.0049598 | 0.0050658 | -0.0031278 | 0.048279 | 92.7 | 91.6959 |  | 0.017736 | 0.062111 | 0.023732 | 0.032704 | 0.07016 | 0.050737 | 0.092902 | 91.4995
55 | IE2 | 1000 | 0.0084789 | 0.014216 | 0.013386 | 0.0052228 | 0.0054666 | 0.0011221 | 0.035862 | 93.1 | 92.1463 |  | 0.015494 | 0.051501 | 0.021704 | 0.029455 | 0.059896 | 0.04828 | 0.083755 | 92.2718
75 | IE2 | 1000 | 0.0085822 | 0.013426 | 0.013229 | 0.0072341 | 0.0081608 | -0.0065826 | 0.032548 | 93.7 | 92.8228 |  | 0.013299 | 0.04105 | 0.019345 | 0.024863 | 0.050226 | 0.043932 | 0.076598 | 92.8851
90 | IE2 | 1000 | 0.0076945 | 0.013397 | 0.01186 | 0.0065746 | 0.0065862 | -0.0022542 | 0.028538 | 94 | 93.1615 |  | 0.013134 | 0.040124 | 0.018887 | 0.024599 | 0.048576 | 0.042249 | 0.072396 | 93.2492
110 | IE2 | 1000 | 0.010373 | 0.016382 | 0.013293 | 0.0064353 | 0.0064832 | -0.0025117 | 0.024754 | 94.3 | 92.9751 |  | 0.016344 | 0.039555 | 0.023109 | 0.028029 | 0.048968 | 0.04821 | 0.075209 | 93.0052
132 | IE2 | 1000 | 0.0093326 | 0.012773 | 0.0088863 | 0.0071409 | 0.0073744 | -0.0045065 | 0.030049 | 94.6 | 93.3399 |  | 0.013973 | 0.04087 | 0.019031 | 0.024553 | 0.048898 | 0.03988 | 0.07105 | 93.3663
160 | IE2 | 1000 | 0.008865 | 0.013409 | 0.0085194 | 0.0075647 | 0.007752 | -0.0034279 | 0.02558 | 94.8 | 93.5834 |  | 0.01364 | 0.037278 | 0.018798 | 0.02381 | 0.045572 | 0.039303 | 0.068262 | 93.61
200 | IE2 | 1000 | 0.0084302 | 0.012627 | 0.0094865 | 0.0065702 | 0.0067885 | -0.0033807 | 0.025177 | 95 | 93.8272 |  | 0.013037 | 0.036043 | 0.018155 | 0.022965 | 0.043894 | 0.038487 | 0.065699 | 93.8352
250 | IE2 | 1000 | 0.0081444 | 0.01174 | 0.0089703 | 0.0060303 | 0.0062654 | -0.0027164 | 0.02306 | 95 | 93.8272 |  | 0.012521 | 0.033883 | 0.017305 | 0.021809 | 0.041182 | 0.036335 | 0.061494 | 94.2068
315 | IE2 | 1000 | 0.0078917 | 0.010858 | 0.0084439 | 0.0054886 | 0.0057431 | -0.0022168 | 0.021077 | 95 | 93.8272 |  | 0.012005 | 0.031725 | 0.016456 | 0.020638 | 0.038472 | 0.034163 | 0.057285 | 94.5818
355 | IE2 | 1000 | 0.007461 | 0.010416 | 0.0082779 | 0.0054041 | 0.0055905 | -0.0020236 | 0.020275 | 95 | 93.8272 |  | 0.01145 | 0.030535 | 0.015756 | 0.01982 | 0.03709 | 0.03296 | 0.055401 | 94.7507
400 | IE2 | 1000 | 0.0066892 | 0.0099543 | 0.0079716 | 0.0053716 | 0.0056255 | -0.00034234 | 0.018421 | 95 | 93.8272 |  | 0.010848 | 0.029449 | 0.014981 | 0.019116 | 0.03583 | 0.031798 | 0.053691 | 94.9045
500 | IE2 | 1000 | 0.006611 | 0.0095221 | 0.0079512 | 0.0052527 | 0.0052667 | -0.0016753 | 0.018685 | 95 | 93.8272 |  | 0.01034 | 0.02814 | 0.014355 | 0.018179 | 0.034312 | 0.030548 | 0.051613 | 95.092
560 | IE2 | 1000 | 0.0065046 | 0.0093921 | 0.0086386 | 0.0051172 | 0.0049539 | -0.0019221 | 0.016517 | 95 | 93.8272 |  | 0.010044 | 0.025577 | 0.014149 | 0.017478 | 0.031753 | 0.030221 | 0.049202 | 95.3106
630 | IE2 | 1000 | 0.0061152 | 0.0091522 | 0.0094403 | 0.0052135 | 0.0052691 | -0.00084412 | 0.01317 | 95 | 93.8272 |  | 0.0097074 | 0.022952 | 0.013909 | 0.016903 | 0.029301 | 0.030199 | 0.047516 | 95.4639
710 | IE2 | 1000 | 0.0061563 | 0.0091858 | 0.010076 | 0.0052332 | 0.0052655 | -0.00084304 | 0.012773 | 95 | 93.8272 |  | 0.0097725 | 0.02265 | 0.014102 | 0.017023 | 0.029131 | 0.030815 | 0.047847 | 95.4338
800 | IE2 | 1000 | 0.0062005 | 0.0092168 | 0.010709 | 0.0052382 | 0.0052609 | -0.0008512 | 0.012386 | 95 | 93.8272 |  | 0.0098378 | 0.022347 | 0.014293 | 0.017141 | 0.028956 | 0.031422 | 0.048161 | 95.4052
900 | IE2 | 1000 | 0.0058365 | 0.008749 | 0.0096429 | 0.0052325 | 0.0052548 | -0.00090598 | 0.012234 | 95 | 93.8272 |  | 0.0092669 | 0.021591 | 0.013406 | 0.01621 | 0.02788 | 0.029456 | 0.046044 | 95.5983
1000 | IE2 | 1000 | 0.0054558 | 0.0082845 | 0.0085773 | 0.0052168 | 0.005242 | -0.00089111 | 0.012018 | 95 | 93.8272 |  | 0.0086933 | 0.020822 | 0.012516 | 0.015281 | 0.026788 | 0.027491 | 0.043903 | 95.7943
0.12 | IE2 | 750 | 0.70884 | 0.25482 | 0.16721 | 0.0065292 | 0.0085554 | -0.64001 | 1.2062 | 39.8 | 36.5037 |  | 0.69851 | 1.3513 | 0.79377 | 0.86094 | 1.4496 | 1.1162 | 1.7121 | 36.8717
0.18 | IE2 | 750 | 0.49258 | 0.15066 | 0.20726 | 0.0046516 | 0.0084653 | -0.62726 | 1.0087 | 45.9 | 42.4548 |  | 0.44953 | 0.92636 | 0.52623 | 0.55939 | 1.0056 | 0.79233 | 1.2451 | 44.5416
0.25 | IE2 | 750 | 0.30111 | 0.13151 | 0.15988 | 0.0069495 | 0.012601 | -0.34002 | 0.79244 | 50.6 | 47.1092 |  | 0.30866 | 0.79892 | 0.37177 | 0.43659 | 0.86587 | 0.62548 | 1.0645 | 48.4388
0.37 | IE2 | 750 | 0.19679 | 0.098298 | 0.13121 | 0.016222 | 0.021289 | -0.21584 | 0.55482 | 56.1 | 52.634 |  | 0.21061 | 0.57393 | 0.26029 | 0.31288 | 0.63115 | 0.46645 | 0.80278 | 55.4698
0.55 | IE2 | 750 | 0.14021 | 0.086277 | 0.112 | 0.018489 | 0.023404 | -0.16107 | 0.45999 | 61.7 | 58.3479 |  | 0.15764 | 0.47378 | 0.20077 | 0.24959 | 0.52536 | 0.38342 | 0.6793 | 59.5487
0.75 | IE2 | 750 | 0.12304 | 0.061179 | 0.057236 | 0.015294 | 0.023243 | -0.085831 | 0.41739 | 66.2 | 63.0056 |  | 0.14687 | 0.47875 | 0.17341 | 0.23274 | 0.51296 | 0.31252 | 0.61155 | 62.0519
1.1 | IE2 | 750 | 0.090739 | 0.050376 | 0.049663 | 0.0093229 | 0.011449 | -0.057603 | 0.28993 | 70.8 | 67.8291 |  | 0.11035 | 0.34181 | 0.13253 | 0.1739 | 0.36819 | 0.23965 | 0.44387 | 69.2581
1.5 | IE2 | 750 | 0.091466 | 0.046848 | 0.061921 | 0.0013732 | 0.0024214 | -0.034545 | 0.20772 | 74.1 | 71.3289 |  | 0.11143 | 0.28072 | 0.1348 | 0.16535 | 0.30484 | 0.23584 | 0.3772 | 72.6109
2.2 | IE2 | 750 | 0.084575 | 0.044588 | 0.047621 | 0.0027359 | 0.0036977 | -0.040577 | 0.19617 | 77.6 | 75.0774 |  | 0.10087 | 0.2552 | 0.12103 | 0.1481 | 0.27666 | 0.20715 | 0.33881 | 74.6933
3 | IE2 | 750 | 0.059613 | 0.03585 | 0.038792 | 0.0079113 | 0.008373 | -0.016075 | 0.15315 | 80 | 77.6699 |  | 0.076709 | 0.21058 | 0.093167 | 0.119 | 0.23036 | 0.16858 | 0.28761 | 77.663
4 | IE2 | 750 | 0.042442 | 0.031034 | 0.036336 | 0.017244 | 0.017641 | -0.01659 | 0.12796 | 81.9 | 79.7352 |  | 0.05666 | 0.16925 | 0.071708 | 0.093996 | 0.19144 | 0.14223 | 0.25606 | 79.6138
5.5 | IE2 | 750 | 0.037459 | 0.027177 | 0.038846 | 0.0035698 | 0.004076 | -0.013895 | 0.11401 | 83.8 | 81.812 |  | 0.050405 | 0.14795 | 0.064587 | 0.083016 | 0.16368 | 0.12695 | 0.21125 | 82.5595
7.5 | IE2 | 750 | 0.031137 | 0.019531 | 0.025295 | 0.011048 | 0.011048 | -0.019255 | 0.10919 | 85.3 | 83.4597 |  | 0.039827 | 0.13099 | 0.049755 | 0.066968 | 0.14545 | 0.099157 | 0.18799 | 84.1755
11 | IE2 | 750 | 0.021059 | 0.016818 | 0.018918 | 0.0078045 | 0.0080034 | -0.0095507 | 0.086325 | 86.9 | 85.2253 |  | 0.029606 | 0.10567 | 0.037574 | 0.052479 | 0.11687 | 0.077552 | 0.14938 | 87.0037
15 | IE2 | 750 | 0.020778 | 0.017224 | 0.032511 | 0.0070771 | 0.0074239 | -0.0062287 | 0.075751 | 88 | 86.444 |  | 0.030433 | 0.098872 | 0.041032 | 0.05469 | 0.11243 | 0.089962 | 0.15454 | 86.6148
18.5 | IE2 | 750 | 0.018951 | 0.015242 | 0.031132 | 0.0065673 | 0.0067654 | -0.0069865 | 0.066864 | 88.6 | 87.1104 |  | 0.027269 | 0.086649 | 0.037098 | 0.048821 | 0.099207 | 0.081881 | 0.13854 | 87.8322
22 | IE2 | 750 | 0.014256 | 0.014414 | 0.024548 | 0.0077929 | 0.0079689 | -0.0053604 | 0.061621 | 89.1 | 87.6667 |  | 0.022058 | 0.0781 | 0.030479 | 0.041797 | 0.089749 | 0.069883 | 0.12524 | 88.8699
30 | IE2 | 750 | 0.014227 | 0.014015 | 0.031236 | 0.0088715 | 0.0090896 | -0.0021791 | 0.053329 | 89.8 | 88.4468 |  | 0.022646 | 0.07362 | 0.032251 | 0.042964 | 0.086902 | 0.076211 | 0.12859 | 88.6062
37 | IE2 | 750 | 0.013041 | 0.012075 | 0.027743 | 0.008798 | 0.0092173 | -0.0088053 | 0.059591 | 90.3 | 89.005 |  | 0.019491 | 0.071355 | 0.027957 | 0.038186 | 0.083504 | 0.067859 | 0.12166 | 89.1535
45 | IE2 | 750 | 0.0107 | 0.015078 | 0.02589 | 0.0053663 | 0.0058672 | -0.0039065 | 0.041811 | 90.7 | 89.4521 |  | 0.017831 | 0.055701 | 0.026607 | 0.034248 | 0.066766 | 0.062975 | 0.10081 | 90.8425
55 | IE2 | 750 | 0.010953 | 0.012845 | 0.029693 | 0.0067479 | 0.0065589 | -0.00063303 | 0.041136 | 91 | 89.7879 |  | 0.018563 | 0.058619 | 0.027524 | 0.036019 | 0.070315 | 0.066784 | 0.1073 | 90.3098
75 | IE2 | 750 | 0.011341 | 0.013213 | 0.036256 | 0.0031148 | 0.0035327 | -0.0020404 | 0.035587 | 91.6 | 90.4602 |  | 0.018686 | 0.051456 | 0.028878 | 0.035498 | 0.062999 | 0.070348 | 0.101 | 90.8262
90 | IE2 | 750 | 0.014716 | 0.017482 | 0.02836 | 0.0064566 | 0.0064558 | -0.001194 | 0.034062 | 91.9 | 90.7968 |  | 0.022815 | 0.055744 | 0.032679 | 0.039676 | 0.068257 | 0.071704 | 0.10634 | 90.3883
110 | IE2 | 750 | 0.011681 | 0.013961 | 0.026774 | 0.0055897 | 0.005629 | -0.0017267 | 0.027004 | 92.3 | 90.5568 |  | 0.01821 | 0.043871 | 0.026874 | 0.032293 | 0.054834 | 0.061109 | 0.088912 | 91.8348
132 | IE2 | 750 | 0.011165 | 0.012498 | 0.024992 | 0.0064425 | 0.0064966 | -0.001624 | 0.027108 | 92.6 | 90.918 |  | 0.017266 | 0.043352 | 0.025253 | 0.030838 | 0.053991 | 0.057855 | 0.087078 | 91.9897
160 | IE2 | 750 | 0.010276 | 0.010619 | 0.022372 | 0.0070636 | 0.00714 | -0.0014832 | 0.026309 | 93 | 91.4005 |  | 0.015741 | 0.041367 | 0.022784 | 0.028343 | 0.051321 | 0.052653 | 0.082296 | 92.3961
200 | IE2 | 750 | 0.009923 | 0.010579 | 0.017351 | 0.0076409 | 0.008301 | -0.0048086 | 0.026952 | 93.5 | 92.0049 |  | 0.014286 | 0.038224 | 0.020401 | 0.025358 | 0.047589 | 0.046172 | 0.075938 | 92.9421
250 | IE2 | 750 | 0.0096895 | 0.0098147 | 0.020725 | 0.0068172 | 0.0068454 | -0.0014677 | 0.0221 | 93.5 | 92.0049 |  | 0.014586 | 0.036203 | 0.021113 | 0.025849 | 0.045531 | 0.048436 | 0.074525 | 93.0644
315 | IE2 | 750 | 0.0085866 | 0.0092331 | 0.016948 | 0.00679 | 0.0068168 | -0.0015385 | 0.021689 | 93.5 | 92.0049 |  | 0.013058 | 0.034228 | 0.01873 | 0.023368 | 0.04269 | 0.042823 | 0.068525 | 93.5869
355 | IE2 | 750 | 0.0081848 | 0.0087619 | 0.016196 | 0.0067738 | 0.0068008 | -0.0015285 | 0.0204 | 93.5 | 92.0049 |  | 0.012413 | 0.032378 | 0.017826 | 0.022222 | 0.040574 | 0.040872 | 0.065589 | 93.8448
400 | IE2 | 750 | 0.0077764 | 0.0082857 | 0.015431 | 0.0067722 | 0.0068059 | -0.0014846 | 0.01909 | 93.5 | 92.0049 |  | 0.011767 | 0.030536 | 0.016917 | 0.021079 | 0.03847 | 0.038918 | 0.062676 | 94.102
500 | IE2 | 750 | 0.0073581 | 0.0078134 | 0.01468 | 0.0067553 | 0.0067898 | -0.0013923 | 0.017728 | 93.5 | 92.0049 |  | 0.011121 | 0.028678 | 0.016012 | 0.019939 | 0.036346 | 0.036973 | 0.059732 | 94.3634
560 | IE2 | 750 | 0.0071665 | 0.007713 | 0.014651 | 0.006698 | 0.006849 | -0.001333 | 0.016455 | 93.5 | 92.0049 |  | 0.010837 | 0.027235 | 0.015697 | 0.019398 | 0.034869 | 0.036365 | 0.0582 | 94.5001
630 | IE2 | 750 | 0.0068978 | 0.0075736 | 0.014735 | 0.0066999 | 0.0067954 | -0.00089585 | 0.014842 | 93.5 | 92.0049 |  | 0.010547 | 0.025758 | 0.015388 | 0.018893 | 0.033363 | 0.035843 | 0.056648 | 94.6389
710 | IE2 | 750 | 0.0069029 | 0.00747 | 0.016284 | 0.0067296 | 0.0067917 | -0.00076247 | 0.013007 | 93.5 | 92.0049 |  | 0.010542 | 0.02414 | 0.015648 | 0.018845 | 0.032017 | 0.036908 | 0.056423 | 94.659
800 | IE2 | 750 | 0.0068896 | 0.0073881 | 0.017812 | 0.006702 | 0.0068188 | -0.00057486 | 0.011146 | 93.5 | 92.0049 |  | 0.010534 | 0.022523 | 0.015905 | 0.0188 | 0.030664 | 0.037969 | 0.056181 | 94.6807
900 | IE2 | 750 | 0.0066756 | 0.0070102 | 0.016004 | 0.0067229 | 0.0067839 | -0.00086298 | 0.012474 | 93.5 | 92.0049 |  | 0.010124 | 0.023145 | 0.015062 | 0.018133 | 0.030851 | 0.035754 | 0.054808 | 94.804
1000 | IE2 | 750 | 0.0064386 | 0.006657 | 0.014165 | 0.0067338 | 0.0067643 | -0.0010751 | 0.013741 | 93.5 | 92.0049 |  | 0.0097099 | 0.02376 | 0.014215 | 0.017471 | 0.031032 | 0.033533 | 0.053425 | 94.9285
IE1
[10 empty] | 34-30-2 | 34-30-2 | Losses | PL7 | PL3 | PL6 | PL5 | PL2 | PL4 | PL1 | Eff / %
[10 empty] | Reference | Nominal | n= | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
Power / kW | Class | Speed | cL1 | cL2 | cL3 | cL4 | cL5 | cL6 | cL7 | % | % | T= | 0.25 | 1 | 0.25 | 0.5 | 1 | 0.5 | 1 | 1
0.12 | IE1 | 1500 | 0.46863 | 0.16847 | 0.11055 | 0.0043167 | 0.0056562 | -0.42313 | 0.79743 | 50 | 46.5116 |  | 0.46181 | 0.89339 | 0.52478 | 0.56919 | 0.95838 | 0.73794 | 1.1319 | 46.906
0.18 | IE1 | 1500 | 0.34598 | 0.1303 | 0.085655 | 0.0028793 | 0.0040769 | -0.16525 | 0.43779 | 57 | 53.5463 |  | 0.37002 | 0.65742 | 0.41875 | 0.45998 | 0.70754 | 0.5905 | 0.84143 | 54.3056
0.25 | IE1 | 1500 | 0.26636 | 0.11408 | 0.082446 | 0.0081127 | 0.0092364 | -0.13642 | 0.33945 | 61.5 | 58.1423 |  | 0.2873 | 0.50566 | 0.33151 | 0.36225 | 0.5534 | 0.48387 | 0.68326 | 59.4087
0.37 | IE1 | 1500 | 0.18808 | 0.085735 | 0.057774 | 0.0055751 | 0.0062575 | -0.058732 | 0.28036 | 66 | 62.7973 |  | 0.21608 | 0.43654 | 0.2485 | 0.2872 | 0.47137 | 0.37527 | 0.56505 | 63.8957
0.55 | IE1 | 1500 | 0.16086 | 0.068293 | 0.045905 | 1.3761e-05 | 0.00060005 | -0.038175 | 0.23283 | 70 | 66.9856 |  | 0.18581 | 0.3755 | 0.2115 | 0.24564 | 0.4013 | 0.31433 | 0.47033 | 68.0121
0.75 | IE1 | 1500 | 0.12952 | 0.062903 | 0.040353 | 0.0023132 | 0.0028018 | -0.031598 | 0.23011 | 72.1 | 69.2038 |  | 0.1543 | 0.34704 | 0.17766 | 0.21326 | 0.37143 | 0.27579 | 0.43641 | 69.6181
1.1 | IE1 | 1500 | 0.10091 | 0.05579 | 0.039737 | 0.0012719 | 0.0019219 | -0.023619 | 0.20535 | 75 | 72.2892 |  | 0.1243 | 0.2995 | 0.14574 | 0.17854 | 0.32158 | 0.23676 | 0.38135 | 72.3927
1.5 | IE1 | 1500 | 0.084707 | 0.04942 | 0.031622 | 0.0016422 | 0.0023297 | -0.026692 | 0.1966 | 77.2 | 74.6471 |  | 0.10469 | 0.2695 | 0.12302 | 0.15348 | 0.28863 | 0.20254 | 0.33962 | 74.6478
2.2 | IE1 | 1500 | 0.050571 | 0.042871 | 0.028971 | 0.013508 | 0.011552 | 0.022142 | 0.12495 | 79.7 | 77.3448 |  | 0.076701 | 0.21429 | 0.093197 | 0.12397 | 0.23599 | 0.17099 | 0.29457 | 77.2459
3 | IE1 | 1500 | 0.051993 | 0.03527 | 0.021358 | 0.0059116 | 0.0061645 | -0.011194 | 0.14813 | 81.5 | 79.2994 |  | 0.068722 | 0.20094 | 0.081709 | 0.10753 | 0.2164 | 0.14308 | 0.25763 | 79.5145
4 | IE1 | 1500 | 0.045807 | 0.036163 | 0.025205 | 0.0054719 | 0.0061659 | -0.017041 | 0.12913 | 83.1 | 81.0455 |  | 0.060343 | 0.17026 | 0.074268 | 0.095021 | 0.18656 | 0.13385 | 0.2309 | 81.2413
5.5 | IE1 | 1500 | 0.037616 | 0.031606 | 0.02355 | 0.0093665 | 0.0098713 | -0.012154 | 0.10941 | 84.7 | 82.7997 |  | 0.050973 | 0.1472 | 0.063553 | 0.082369 | 0.16371 | 0.11886 | 0.20926 | 82.695
7.5 | IE1 | 1500 | 0.030341 | 0.028275 | 0.019479 | 0.0086291 | 0.0091951 | -0.020567 | 0.11721 | 86 | 84.2311 |  | 0.040982 | 0.138 | 0.051945 | 0.07002 | 0.1526 | 0.10157 | 0.19256 | 83.8532
11 | IE1 | 1500 | 0.024891 | 0.025316 | 0.018524 | 0.0071818 | 0.007434 | -0.011256 | 0.090757 | 87.6 | 86.0004 |  | 0.035378 | 0.11414 | 0.045379 | 0.060604 | 0.12713 | 0.089447 | 0.16285 | 85.9958
15 | IE1 | 1500 | 0.020305 | 0.022711 | 0.017065 | 0.0075792 | 0.0078437 | -0.0095356 | 0.079536 | 88.7 | 87.2216 |  | 0.029785 | 0.099434 | 0.038873 | 0.05248 | 0.11168 | 0.079053 | 0.1455 | 87.2978
18.5 | IE1 | 1500 | 0.018521 | 0.021168 | 0.015422 | 0.0069029 | 0.0071138 | -0.0065926 | 0.078374 | 89.3 | 87.8894 |  | 0.028163 | 0.098729 | 0.036537 | 0.050565 | 0.10997 | 0.074912 | 0.14091 | 87.6494
22 | IE1 | 1500 | 0.01779 | 0.02035 | 0.015453 | 0.0031459 | 0.0034624 | -0.0068732 | 0.074015 | 89.9 | 88.5583 |  | 0.026813 | 0.091988 | 0.034888 | 0.047505 | 0.10141 | 0.070312 | 0.12734 | 88.7041
30 | IE1 | 1500 | 0.012729 | 0.017178 | 0.010584 | 0.0080636 | 0.01141 | 0.00041465 | 0.059032 | 90.7 | 89.4521 |  | 0.021649 | 0.079861 | 0.028188 | 0.040651 | 0.090296 | 0.060326 | 0.11941 | 89.3326
37 | IE1 | 1500 | 0.027029 | 0.0037393 | 0.017812 | 0.011064 | -0.0031393 | -0.0099021 | 0.065224 | 91.2 | 90.0118 |  | 0.030838 | 0.086969 | 0.035249 | 0.045893 | 0.093421 | 0.061916 | 0.11183 | 89.9421
45 | IE1 | 1500 | 0.012787 | 0.016031 | 0.014543 | 0.0057007 | 0.0058226 | -0.0035951 | 0.055492 | 91.7 | 90.5724 |  | 0.020385 | 0.071389 | 0.027277 | 0.03759 | 0.080641 | 0.058317 | 0.10678 | 90.3522
55 | IE1 | 1500 | 0.0098131 | 0.016453 | 0.015493 | 0.0060446 | 0.0063269 | 0.0012987 | 0.041506 | 92.1 | 91.0214 |  | 0.017933 | 0.059605 | 0.025119 | 0.03409 | 0.069321 | 0.055878 | 0.096935 | 91.1631
75 | IE1 | 1500 | 0.010052 | 0.015726 | 0.015494 | 0.0084728 | 0.0095582 | -0.0077097 | 0.038122 | 92.7 | 91.6959 |  | 0.015576 | 0.048079 | 0.022657 | 0.02912 | 0.058826 | 0.051455 | 0.089714 | 91.7672
90 | IE1 | 1500 | 0.0090735 | 0.015798 | 0.013985 | 0.0077529 | 0.0077665 | -0.0026581 | 0.033652 | 93 | 92.0336 |  | 0.015487 | 0.047315 | 0.022271 | 0.029007 | 0.057281 | 0.04982 | 0.08537 | 92.1345
110 | IE1 | 1500 | 0.012323 | 0.019463 | 0.015792 | 0.0076454 | 0.0077023 | -0.002984 | 0.029409 | 93.3 | 91.763 |  | 0.019417 | 0.046993 | 0.027454 | 0.0333 | 0.058176 | 0.057275 | 0.089351 | 91.7978
132 | IE1 | 1500 | 0.011366 | 0.015556 | 0.010822 | 0.0086967 | 0.008981 | -0.0054883 | 0.036596 | 93.5 | 92.0049 |  | 0.017017 | 0.049775 | 0.023177 | 0.029903 | 0.059551 | 0.048569 | 0.08653 | 92.0361
160 | IE1 | 1500 | 0.010682 | 0.016158 | 0.010266 | 0.0091157 | 0.0093413 | -0.0041307 | 0.030825 | 93.8 | 92.3683 |  | 0.016436 | 0.04492 | 0.022652 | 0.028692 | 0.054915 | 0.047361 | 0.082257 | 92.3995
200 | IE1 | 1500 | 0.010224 | 0.015313 | 0.011505 | 0.0079681 | 0.0082328 | -0.0041 | 0.030534 | 94 | 92.6108 |  | 0.015811 | 0.043712 | 0.022018 | 0.027851 | 0.053233 | 0.046676 | 0.079677 | 92.6203
250 | IE1 | 1500 | 0.0098773 | 0.014238 | 0.010879 | 0.0073133 | 0.0075985 | -0.0032944 | 0.027967 | 94 | 92.6108 |  | 0.015185 | 0.041092 | 0.020987 | 0.026449 | 0.049944 | 0.044066 | 0.074578 | 93.0598
315 | IE1 | 1500 | 0.0095708 | 0.013169 | 0.01024 | 0.0066564 | 0.006965 | -0.0026884 | 0.025561 | 94 | 92.6108 |  | 0.01456 | 0.038475 | 0.019958 | 0.025029 | 0.046657 | 0.041431 | 0.069474 | 93.5039
355 | IE1 | 1500 | 0.0090484 | 0.012632 | 0.010039 | 0.0065539 | 0.0067799 | -0.0024542 | 0.024589 | 94 | 92.6108 |  | 0.013886 | 0.037031 | 0.019108 | 0.024037 | 0.044981 | 0.039973 | 0.067188 | 93.7042
400 | IE1 | 1500 | 0.0081125 | 0.012072 | 0.0096677 | 0.0065145 | 0.0068224 | -0.00041518 | 0.02234 | 94 | 92.6108 |  | 0.013156 | 0.035715 | 0.018168 | 0.023184 | 0.043453 | 0.038564 | 0.065114 | 93.8866
500 | IE1 | 1500 | 0.0080176 | 0.011548 | 0.0096429 | 0.0063703 | 0.0063873 | -0.0020318 | 0.02266 | 94 | 92.6108 |  | 0.01254 | 0.034128 | 0.01741 | 0.022047 | 0.041613 | 0.037047 | 0.062595 | 94.1093
560 | IE1 | 1500 | 0.0078886 | 0.01139 | 0.010477 | 0.006206 | 0.006008 | -0.0023311 | 0.020032 | 94 | 92.6108 |  | 0.012181 | 0.031018 | 0.01716 | 0.021197 | 0.038508 | 0.036651 | 0.05967 | 94.369
630 | IE1 | 1500 | 0.0074163 | 0.011099 | 0.011449 | 0.0063228 | 0.0063901 | -0.0010237 | 0.015972 | 94 | 92.6108 |  | 0.011773 | 0.027835 | 0.016868 | 0.020499 | 0.035535 | 0.036624 | 0.057626 | 94.5514
710 | IE1 | 1500 | 0.0074662 | 0.01114 | 0.01222 | 0.0063467 | 0.0063858 | -0.0010224 | 0.015491 | 94 | 92.6108 |  | 0.011852 | 0.027469 | 0.017102 | 0.020645 | 0.03533 | 0.037371 | 0.058027 | 94.5155
800 | IE1 | 1500 | 0.0075198 | 0.011178 | 0.012988 | 0.0063528 | 0.0063803 | -0.0010323 | 0.015022 | 94 | 92.6108 |  | 0.011931 | 0.027102 | 0.017335 | 0.020788 | 0.035116 | 0.038108 | 0.058408 | 94.4815
900 | IE1 | 1500 | 0.0070783 | 0.01061 | 0.011695 | 0.0063458 | 0.0063728 | -0.0010987 | 0.014837 | 94 | 92.6108 |  | 0.011239 | 0.026185 | 0.016258 | 0.019659 | 0.033812 | 0.035723 | 0.055841 | 94.7113
1000 | IE1 | 1500 | 0.0066166 | 0.010047 | 0.010402 | 0.0063267 | 0.0063573 | -0.0010807 | 0.014575 | 94 | 92.6108 |  | 0.010543 | 0.025252 | 0.015179 | 0.018532 | 0.032488 | 0.03334 | 0.053244 | 94.9447
0.12 | IE1 | 3000 | 0.43657 | 0.1576 | 0.15641 | -0.0018668 | 0.0041786 | -0.54152 | 1.0193 | 45 | 41.5704 |  | 0.41406 | 0.96329 | 0.48281 | 0.53856 | 1.0323 | 0.73521 | 1.2306 | 44.8303
0.18 | IE1 | 3000 | 0.37359 | 0.11427 | 0.1572 | 0.003528 | 0.0064204 | -0.47574 | 0.76507 | 52.8 | 49.3089 |  | 0.34095 | 0.70259 | 0.39912 | 0.42426 | 0.76272 | 0.60094 | 0.94433 | 51.4315
0.25 | IE1 | 3000 | 0.22152 | 0.096744 | 0.11762 | 0.0051124 | 0.0092699 | -0.25014 | 0.58296 | 58.2 | 54.7662 |  | 0.22707 | 0.58773 | 0.2735 | 0.32118 | 0.63699 | 0.46014 | 0.78308 | 56.0827
0.37 | IE1 | 3000 | 0.14207 | 0.070966 | 0.094724 | 0.011711 | 0.015369 | -0.15582 | 0.40055 | 63.9 | 60.6176 |  | 0.15205 | 0.41434 | 0.18792 | 0.22588 | 0.45566 | 0.33675 | 0.57956 | 63.3086
0.55 | IE1 | 3000 | 0.10148 | 0.062445 | 0.08106 | 0.013382 | 0.016939 | -0.11658 | 0.33293 | 69 | 65.9341 |  | 0.1141 | 0.34291 | 0.14531 | 0.18064 | 0.38024 | 0.27751 | 0.49165 | 67.0397
0.75 | IE1 | 3000 | 0.093251 | 0.046368 | 0.043379 | 0.011591 | 0.017616 | -0.065051 | 0.31634 | 72.1 | 69.2038 |  | 0.11131 | 0.36284 | 0.13143 | 0.17639 | 0.38877 | 0.23686 | 0.4635 | 68.3296
1.1 | IE1 | 3000 | 0.073337 | 0.040715 | 0.040138 | 0.0075349 | 0.0092535 | -0.046556 | 0.23432 | 75 | 72.2892 |  | 0.089185 | 0.27626 | 0.10712 | 0.14055 | 0.29758 | 0.19369 | 0.35875 | 73.5972
1.5 | IE1 | 3000 | 0.077285 | 0.039585 | 0.052321 | 0.0011603 | 0.002046 | -0.029189 | 0.17551 | 77.2 | 74.6471 |  | 0.09415 | 0.23719 | 0.1139 | 0.13971 | 0.25757 | 0.19928 | 0.31872 | 75.831
2.2 | IE1 | 3000 | 0.074627 | 0.039343 | 0.04202 | 0.0024141 | 0.0032627 | -0.035804 | 0.17309 | 79.7 | 77.3448 |  | 0.089007 | 0.22518 | 0.1068 | 0.13068 | 0.24411 | 0.18278 | 0.29895 | 76.985
3 | IE1 | 3000 | 0.054127 | 0.032551 | 0.035222 | 0.0071833 | 0.0076025 | -0.014596 | 0.13906 | 81.5 | 79.2994 |  | 0.06965 | 0.1912 | 0.084593 | 0.10805 | 0.20916 | 0.15306 | 0.26115 | 79.2929
4 | IE1 | 3000 | 0.039056 | 0.028558 | 0.033437 | 0.015868 | 0.016234 | -0.015266 | 0.11775 | 83.1 | 81.0455 |  | 0.05214 | 0.15575 | 0.065987 | 0.086497 | 0.17617 | 0.13088 | 0.23563 | 80.93
5.5 | IE1 | 3000 | 0.035002 | 0.025395 | 0.036298 | 0.0033357 | 0.0038087 | -0.012984 | 0.10654 | 84.7 | 82.7997 |  | 0.047099 | 0.13824 | 0.060351 | 0.077571 | 0.15295 | 0.11862 | 0.19739 | 83.5148
7.5 | IE1 | 3000 | 0.029413 | 0.018449 | 0.023894 | 0.010436 | 0.010436 | -0.018189 | 0.10315 | 86 | 84.2311 |  | 0.037622 | 0.12374 | 0.047 | 0.06326 | 0.13739 | 0.093666 | 0.17758 | 84.9196
11 | IE1 | 3000 | 0.019774 | 0.015792 | 0.017764 | 0.0073284 | 0.0075152 | -0.0089681 | 0.081059 | 87.6 | 86.0004 |  | 0.0278 | 0.099225 | 0.035282 | 0.049278 | 0.10975 | 0.072821 | 0.14026 | 87.699
15 | IE1 | 3000 | 0.019411 | 0.016092 | 0.030373 | 0.0066117 | 0.0069356 | -0.0058191 | 0.070769 | 88.7 | 87.2216 |  | 0.028431 | 0.092369 | 0.038334 | 0.051093 | 0.10504 | 0.084046 | 0.14437 | 87.3841
18.5 | IE1 | 3000 | 0.017648 | 0.014194 | 0.028991 | 0.0061157 | 0.0063002 | -0.0065061 | 0.062266 | 89.3 | 87.8894 |  | 0.025394 | 0.080691 | 0.034547 | 0.045464 | 0.092386 | 0.076251 | 0.12901 | 88.5732
22 | IE1 | 3000 | 0.013092 | 0.013237 | 0.022544 | 0.0071566 | 0.0073183 | -0.0049227 | 0.05659 | 89.9 | 88.5583 |  | 0.020257 | 0.071724 | 0.027991 | 0.038385 | 0.082422 | 0.064178 | 0.11502 | 89.6848
30 | IE1 | 3000 | 0.012843 | 0.012651 | 0.028197 | 0.0080085 | 0.0082054 | -0.0019671 | 0.048141 | 90.7 | 89.4521 |  | 0.020443 | 0.066458 | 0.029114 | 0.038784 | 0.078448 | 0.068797 | 0.11608 | 89.5993
37 | IE1 | 3000 | 0.011715 | 0.010847 | 0.024921 | 0.0079029 | 0.0082795 | -0.0079094 | 0.053528 | 91.2 | 90.0118 |  | 0.017508 | 0.064096 | 0.025113 | 0.034301 | 0.075008 | 0.060955 | 0.10928 | 90.1483
45 | IE1 | 3000 | 0.0094452 | 0.01331 | 0.022854 | 0.0047371 | 0.0051792 | -0.0034485 | 0.036909 | 91.7 | 90.5724 |  | 0.01574 | 0.049169 | 0.023487 | 0.030232 | 0.058937 | 0.055591 | 0.088985 | 91.8286
55 | IE1 | 3000 | 0.0094992 | 0.01114 | 0.025753 | 0.0058524 | 0.0056885 | -0.00054903 | 0.035677 | 92.1 | 91.0214 |  | 0.0161 | 0.05084 | 0.023872 | 0.031239 | 0.060983 | 0.057922 | 0.09306 | 91.4863
75 | IE1 | 3000 | 0.0097386 | 0.011347 | 0.031134 | 0.0026748 | 0.0030337 | -0.0017522 | 0.03056 | 92.7 | 91.6959 |  | 0.016047 | 0.044187 | 0.024798 | 0.030483 | 0.054099 | 0.06041 | 0.086736 | 92.0187
90 | IE1 | 3000 | 0.012567 | 0.014929 | 0.024218 | 0.0055138 | 0.0055131 | -0.0010196 | 0.029088 | 93 | 92.0336 |  | 0.019483 | 0.047604 | 0.027907 | 0.033882 | 0.05829 | 0.061233 | 0.09081 | 91.675
110 | IE1 | 3000 | 0.010055 | 0.012018 | 0.023048 | 0.0048116 | 0.0048454 | -0.0014863 | 0.023245 | 93.3 | 91.763 |  | 0.015675 | 0.037764 | 0.023133 | 0.027798 | 0.047201 | 0.052603 | 0.076536 | 92.8905
132 | IE1 | 3000 | 0.0097125 | 0.010873 | 0.021741 | 0.0056045 | 0.0056515 | -0.0014128 | 0.023582 | 93.5 | 92.0049 |  | 0.01502 | 0.037713 | 0.021968 | 0.026827 | 0.046968 | 0.050329 | 0.075751 | 92.9583
160 | IE1 | 3000 | 0.009024 | 0.0093248 | 0.019646 | 0.006203 | 0.0062701 | -0.0013025 | 0.023104 | 93.8 | 92.3683 |  | 0.013823 | 0.036327 | 0.020008 | 0.02489 | 0.045068 | 0.046238 | 0.072269 | 93.2601
200 | IE1 | 3000 | 0.009111 | 0.0097131 | 0.015931 | 0.0070156 | 0.0076217 | -0.0044151 | 0.024746 | 94 | 92.6108 |  | 0.013117 | 0.035096 | 0.018732 | 0.023283 | 0.043695 | 0.042394 | 0.069724 | 93.4821
250 | IE1 | 3000 | 0.0088966 | 0.0090116 | 0.019029 | 0.0062593 | 0.0062852 | -0.0013476 | 0.020292 | 94 | 92.6108 |  | 0.013392 | 0.03324 | 0.019385 | 0.023734 | 0.041805 | 0.044473 | 0.068426 | 93.5956
315 | IE1 | 3000 | 0.0078839 | 0.0084775 | 0.015561 | 0.0062343 | 0.0062589 | -0.0014126 | 0.019914 | 94 | 92.6108 |  | 0.011989 | 0.031427 | 0.017197 | 0.021456 | 0.039196 | 0.039318 | 0.062918 | 94.0807
355 | IE1 | 3000 | 0.0075151 | 0.0080449 | 0.01487 | 0.0062195 | 0.0062442 | -0.0014034 | 0.018731 | 94 | 92.6108 |  | 0.011397 | 0.029728 | 0.016367 | 0.020404 | 0.037254 | 0.037527 | 0.060222 | 94.3199
400 | IE1 | 3000 | 0.0071401 | 0.0076076 | 0.014168 | 0.006218 | 0.006249 | -0.0013631 | 0.017527 | 94 | 92.6108 |  | 0.010804 | 0.028037 | 0.015533 | 0.019354 | 0.035322 | 0.035733 | 0.057547 | 94.5584
500 | IE1 | 3000 | 0.006756 | 0.007174 | 0.013478 | 0.0062025 | 0.0062341 | -0.0012784 | 0.016278 | 94 | 92.6108 |  | 0.010211 | 0.026331 | 0.014702 | 0.018308 | 0.033372 | 0.033948 | 0.054844 | 94.8007
560 | IE1 | 3000 | 0.0065801 | 0.0070819 | 0.013452 | 0.0061499 | 0.0062885 | -0.0012239 | 0.015109 | 94 | 92.6108 |  | 0.0099503 | 0.025006 | 0.014413 | 0.017811 | 0.032016 | 0.033389 | 0.053437 | 94.9274
630 | IE1 | 3000 | 0.0063333 | 0.0069539 | 0.013529 | 0.0061516 | 0.0062393 | -0.00082254 | 0.013628 | 94 | 92.6108 |  | 0.0096839 | 0.02365 | 0.014128 | 0.017347 | 0.030633 | 0.03291 | 0.052012 | 95.0559
710 | IE1 | 3000 | 0.0063381 | 0.0068587 | 0.014952 | 0.0061789 | 0.0062359 | -0.00070008 | 0.011943 | 94 | 92.6108 |  | 0.0096795 | 0.022165 | 0.014367 | 0.017303 | 0.029397 | 0.033888 | 0.051806 | 95.0746
800 | IE1 | 3000 | 0.0063258 | 0.0067835 | 0.016354 | 0.0061536 | 0.0062608 | -0.00052781 | 0.010234 | 94 | 92.6108 |  | 0.0096721 | 0.02068 | 0.014604 | 0.017261 | 0.028154 | 0.034862 | 0.051584 | 95.0946
900 | IE1 | 3000 | 0.0061293 | 0.0064366 | 0.014694 | 0.0061728 | 0.0062288 | -0.00079236 | 0.011454 | 94 | 92.6108 |  | 0.0092954 | 0.021251 | 0.013829 | 0.016649 | 0.028326 | 0.032828 | 0.050323 | 95.2088
1000 | IE1 | 3000 | 0.0059117 | 0.0061123 | 0.013006 | 0.0061827 | 0.0062107 | -0.00098714 | 0.012616 | 94 | 92.6108 |  | 0.0089153 | 0.021816 | 0.013051 | 0.016041 | 0.028492 | 0.030789 | 0.049053 | 95.3241
0.12 | IE1 | 1000 | 0.75495 | 0.2714 | 0.17809 | 0.006954 | 0.009112 | -0.68164 | 1.2846 | 38.3 | 35.0556 |  | 0.74395 | 1.4392 | 0.84541 | 0.91695 | 1.5439 | 1.1888 | 1.8235 | 35.4172
0.18 | IE1 | 1000 | 0.54934 | 0.20689 | 0.136 | 0.0045717 | 0.0064733 | -0.26239 | 0.69512 | 45.5 | 42.0615 |  | 0.58751 | 1.0438 | 0.66488 | 0.73035 | 1.1234 | 0.93758 | 1.336 | 42.8081
0.25 | IE1 | 1000 | 0.39118 | 0.16754 | 0.12108 | 0.011915 | 0.013565 | -0.20036 | 0.49853 | 52.1 | 48.6075 |  | 0.42194 | 0.74263 | 0.48687 | 0.53201 | 0.81274 | 0.71062 | 1.0034 | 49.9139
0.37 | IE1 | 1000 | 0.24646 | 0.11234 | 0.075706 | 0.0073054 | 0.0081997 | -0.076961 | 0.36738 | 59.7 | 56.2969 |  | 0.28314 | 0.57203 | 0.32563 | 0.37634 | 0.61768 | 0.49175 | 0.74043 | 57.4571
0.55 | IE1 | 1000 | 0.19509 | 0.082823 | 0.055672 | 1.6689e-05 | 0.00072772 | -0.046298 | 0.28237 | 65.8 | 62.5892 |  | 0.22535 | 0.45539 | 0.2565 | 0.29791 | 0.48668 | 0.38121 | 0.5704 | 63.6782
0.75 | IE1 | 1000 | 0.14345 | 0.069666 | 0.044692 | 0.0025619 | 0.003103 | -0.034996 | 0.25486 | 70 | 66.9856 |  | 0.17089 | 0.38436 | 0.19676 | 0.23619 | 0.41137 | 0.30544 | 0.48333 | 67.4157
1.1 | IE1 | 1000 | 0.11253 | 0.062218 | 0.044315 | 0.0014184 | 0.0021434 | -0.026341 | 0.22901 | 72.9 | 70.0524 |  | 0.13862 | 0.33401 | 0.16253 | 0.19912 | 0.35863 | 0.26404 | 0.4253 | 70.1608
1.5 | IE1 | 1000 | 0.094588 | 0.055184 | 0.03531 | 0.0018338 | 0.0026014 | -0.029806 | 0.21953 | 75.2 | 72.5029 |  | 0.1169 | 0.30093 | 0.13738 | 0.17138 | 0.3223 | 0.22617 | 0.37924 | 72.5037
2.2 | IE1 | 1000 | 0.056984 | 0.048307 | 0.032644 | 0.015221 | 0.013017 | 0.024949 | 0.1408 | 77.7 | 75.1851 |  | 0.086427 | 0.24147 | 0.10501 | 0.13969 | 0.26591 | 0.19267 | 0.33192 | 75.0797
3 | IE1 | 1000 | 0.05834 | 0.039576 | 0.023966 | 0.0066333 | 0.0069171 | -0.01256 | 0.16621 | 79.7 | 77.3448 |  | 0.077111 | 0.22547 | 0.091683 | 0.12065 | 0.24282 | 0.16054 | 0.28908 | 77.5745
4 | IE1 | 1000 | 0.051468 | 0.040632 | 0.02832 | 0.0061482 | 0.0069279 | -0.019147 | 0.14509 | 81.4 | 79.1906 |  | 0.0678 | 0.19131 | 0.083446 | 0.10676 | 0.20961 | 0.15039 | 0.25944 | 79.4007
5.5 | IE1 | 1000 | 0.042349 | 0.035584 | 0.026514 | 0.010545 | 0.011114 | -0.013683 | 0.12318 | 83.1 | 81.0455 |  | 0.057388 | 0.16573 | 0.07155 | 0.092734 | 0.18431 | 0.13381 | 0.2356 | 80.9325
7.5 | IE1 | 1000 | 0.033667 | 0.031375 | 0.021615 | 0.0095751 | 0.010203 | -0.022821 | 0.13006 | 84.7 | 82.7997 |  | 0.045475 | 0.15313 | 0.05764 | 0.077697 | 0.16933 | 0.1127 | 0.21367 | 82.3946
11 | IE1 | 1000 | 0.027679 | 0.028152 | 0.020599 | 0.0079862 | 0.0082666 | -0.012517 | 0.10092 | 86.4 | 84.6727 |  | 0.03934 | 0.12692 | 0.050462 | 0.067392 | 0.14137 | 0.099465 | 0.18109 | 84.6677
15 | IE1 | 1000 | 0.022353 | 0.025003 | 0.018787 | 0.0083439 | 0.0086352 | -0.010498 | 0.087561 | 87.7 | 86.1112 |  | 0.032791 | 0.10947 | 0.042795 | 0.057776 | 0.12295 | 0.08703 | 0.16019 | 86.1931
18.5 | IE1 | 1000 | 0.019888 | 0.022731 | 0.01656 | 0.0074126 | 0.007639 | -0.0070794 | 0.084161 | 88.6 | 87.1104 |  | 0.030242 | 0.10602 | 0.039235 | 0.054299 | 0.11809 | 0.080443 | 0.15131 | 86.8573
22 | IE1 | 1000 | 0.019172 | 0.021931 | 0.016654 | 0.0033903 | 0.0037314 | -0.0074072 | 0.079766 | 89.2 | 87.778 |  | 0.028897 | 0.099135 | 0.037599 | 0.051196 | 0.10929 | 0.075775 | 0.13724 | 87.9324
30 | IE1 | 1000 | 0.013488 | 0.018202 | 0.011215 | 0.0085442 | 0.012091 | 0.00043937 | 0.062551 | 90.2 | 88.8933 |  | 0.022939 | 0.084621 | 0.029868 | 0.043074 | 0.095678 | 0.063921 | 0.12653 | 88.7681
37 | IE1 | 1000 | 0.028382 | 0.0039265 | 0.018703 | 0.011617 | -0.0032965 | -0.010398 | 0.06849 | 90.8 | 89.564 |  | 0.032382 | 0.091322 | 0.037014 | 0.048191 | 0.098097 | 0.065015 | 0.11742 | 89.4915
45 | IE1 | 1000 | 0.013293 | 0.016665 | 0.015118 | 0.0059261 | 0.0060528 | -0.0037373 | 0.057686 | 91.4 | 90.236 |  | 0.021191 | 0.074212 | 0.028355 | 0.039076 | 0.08383 | 0.060623 | 0.111 | 90.0088
55 | IE1 | 1000 | 0.010083 | 0.016907 | 0.015919 | 0.0062111 | 0.0065011 | 0.0013345 | 0.042649 | 91.9 | 90.7968 |  | 0.018427 | 0.061247 | 0.025811 | 0.035029 | 0.071231 | 0.057417 | 0.099605 | 90.9417
75 | IE1 | 1000 | 0.0102 | 0.015958 | 0.015724 | 0.0085981 | 0.0096996 | -0.0078238 | 0.038686 | 92.6 | 91.5834 |  | 0.015807 | 0.04879 | 0.022993 | 0.029551 | 0.059696 | 0.052216 | 0.091042 | 91.6555
90 | IE1 | 1000 | 0.009213 | 0.016041 | 0.0142 | 0.0078721 | 0.0078859 | -0.002699 | 0.03417 | 92.9 | 91.921 |  | 0.015725 | 0.048042 | 0.022614 | 0.029453 | 0.058162 | 0.050587 | 0.086683 | 92.0232
110 | IE1 | 1000 | 0.012323 | 0.019463 | 0.015792 | 0.0076454 | 0.0077023 | -0.002984 | 0.029409 | 93.3 | 91.763 |  | 0.019417 | 0.046993 | 0.027454 | 0.0333 | 0.058176 | 0.057275 | 0.089351 | 91.7978
132 | IE1 | 1000 | 0.011366 | 0.015556 | 0.010822 | 0.0086967 | 0.008981 | -0.0054883 | 0.036596 | 93.5 | 92.0049 |  | 0.017017 | 0.049775 | 0.023177 | 0.029903 | 0.059551 | 0.048569 | 0.08653 | 92.0361
160 | IE1 | 1000 | 0.010682 | 0.016158 | 0.010266 | 0.0091157 | 0.0093413 | -0.0041307 | 0.030825 | 93.8 | 92.3683 |  | 0.016436 | 0.04492 | 0.022652 | 0.028692 | 0.054915 | 0.047361 | 0.082257 | 92.3995
200 | IE1 | 1000 | 0.010224 | 0.015313 | 0.011505 | 0.0079681 | 0.0082328 | -0.0041 | 0.030534 | 94 | 92.6108 |  | 0.015811 | 0.043712 | 0.022018 | 0.027851 | 0.053233 | 0.046676 | 0.079677 | 92.6203
250 | IE1 | 1000 | 0.0098773 | 0.014238 | 0.010879 | 0.0073133 | 0.0075985 | -0.0032944 | 0.027967 | 94 | 92.6108 |  | 0.015185 | 0.041092 | 0.020987 | 0.026449 | 0.049944 | 0.044066 | 0.074578 | 93.0598
315 | IE1 | 1000 | 0.0095708 | 0.013169 | 0.01024 | 0.0066564 | 0.006965 | -0.0026884 | 0.025561 | 94 | 92.6108 |  | 0.01456 | 0.038475 | 0.019958 | 0.025029 | 0.046657 | 0.041431 | 0.069474 | 93.5039
355 | IE1 | 1000 | 0.0090484 | 0.012632 | 0.010039 | 0.0065539 | 0.0067799 | -0.0024542 | 0.024589 | 94 | 92.6108 |  | 0.013886 | 0.037031 | 0.019108 | 0.024037 | 0.044981 | 0.039973 | 0.067188 | 93.7042
400 | IE1 | 1000 | 0.0081125 | 0.012072 | 0.0096677 | 0.0065145 | 0.0068224 | -0.00041518 | 0.02234 | 94 | 92.6108 |  | 0.013156 | 0.035715 | 0.018168 | 0.023184 | 0.043453 | 0.038564 | 0.065114 | 93.8866
500 | IE1 | 1000 | 0.0080176 | 0.011548 | 0.0096429 | 0.0063703 | 0.0063873 | -0.0020318 | 0.02266 | 94 | 92.6108 |  | 0.01254 | 0.034128 | 0.01741 | 0.022047 | 0.041613 | 0.037047 | 0.062595 | 94.1093
560 | IE1 | 1000 | 0.0078886 | 0.01139 | 0.010477 | 0.006206 | 0.006008 | -0.0023311 | 0.020032 | 94 | 92.6108 |  | 0.012181 | 0.031018 | 0.01716 | 0.021197 | 0.038508 | 0.036651 | 0.05967 | 94.369
630 | IE1 | 1000 | 0.0074163 | 0.011099 | 0.011449 | 0.0063228 | 0.0063901 | -0.0010237 | 0.015972 | 94 | 92.6108 |  | 0.011773 | 0.027835 | 0.016868 | 0.020499 | 0.035535 | 0.036624 | 0.057626 | 94.5514
710 | IE1 | 1000 | 0.0074662 | 0.01114 | 0.01222 | 0.0063467 | 0.0063858 | -0.0010224 | 0.015491 | 94 | 92.6108 |  | 0.011852 | 0.027469 | 0.017102 | 0.020645 | 0.03533 | 0.037371 | 0.058027 | 94.5155
800 | IE1 | 1000 | 0.0075198 | 0.011178 | 0.012988 | 0.0063528 | 0.0063803 | -0.0010323 | 0.015022 | 94 | 92.6108 |  | 0.011931 | 0.027102 | 0.017335 | 0.020788 | 0.035116 | 0.038108 | 0.058408 | 94.4815
900 | IE1 | 1000 | 0.0070783 | 0.01061 | 0.011695 | 0.0063458 | 0.0063728 | -0.0010987 | 0.014837 | 94 | 92.6108 |  | 0.011239 | 0.026185 | 0.016258 | 0.019659 | 0.033812 | 0.035723 | 0.055841 | 94.7113
1000 | IE1 | 1000 | 0.0066166 | 0.010047 | 0.010402 | 0.0063267 | 0.0063573 | -0.0010807 | 0.014575 | 94 | 92.6108 |  | 0.010543 | 0.025252 | 0.015179 | 0.018532 | 0.032488 | 0.03334 | 0.053244 | 94.9447
0.12 | IE1 | 750 | 1.0431 | 0.37498 | 0.24606 | 0.009608 | 0.01259 | -0.9418 | 1.7749 | 31 | 28.0924 |  | 1.0279 | 1.9885 | 1.1681 | 1.2669 | 2.1332 | 1.6425 | 2.5194 | 28.4136
0.18 | IE1 | 750 | 0.68186 | 0.20856 | 0.28691 | 0.0064392 | 0.011718 | -0.86831 | 1.3964 | 38 | 34.7667 |  | 0.62228 | 1.2823 | 0.72845 | 0.77435 | 1.3921 | 1.0968 | 1.7236 | 36.7167
0.25 | IE1 | 750 | 0.40388 | 0.17639 | 0.21444 | 0.0093212 | 0.016901 | -0.45606 | 1.0629 | 43.3 | 39.906 |  | 0.414 | 1.0716 | 0.49865 | 0.58559 | 1.1614 | 0.83895 | 1.4277 | 41.1906
0.37 | IE1 | 750 | 0.25451 | 0.12713 | 0.16969 | 0.02098 | 0.027533 | -0.27915 | 0.71757 | 49.7 | 46.2132 |  | 0.27239 | 0.74228 | 0.33664 | 0.40466 | 0.81629 | 0.60328 | 1.0383 | 49.0614
0.55 | IE1 | 750 | 0.17676 | 0.10876 | 0.14119 | 0.023308 | 0.029504 | -0.20305 | 0.57988 | 56.1 | 52.634 |  | 0.19873 | 0.59727 | 0.2531 | 0.31463 | 0.66229 | 0.48335 | 0.85634 | 53.8693
0.75 | IE1 | 750 | 0.15278 | 0.075967 | 0.07107 | 0.018991 | 0.028861 | -0.10658 | 0.51828 | 61.2 | 57.8341 |  | 0.18237 | 0.59447 | 0.21532 | 0.28899 | 0.63695 | 0.38806 | 0.75938 | 56.8383
1.1 | IE1 | 750 | 0.10117 | 0.056168 | 0.055374 | 0.010395 | 0.012766 | -0.064226 | 0.32327 | 68.5 | 65.4094 |  | 0.12304 | 0.38111 | 0.14777 | 0.1939 | 0.41053 | 0.26721 | 0.49491 | 66.8934
1.5 | IE1 | 750 | 0.11109 | 0.056897 | 0.075203 | 0.0016677 | 0.0029408 | -0.041955 | 0.25227 | 70.2 | 67.1963 |  | 0.13533 | 0.34093 | 0.16371 | 0.20082 | 0.37022 | 0.28643 | 0.45812 | 68.5817
2.2 | IE1 | 750 | 0.10188 | 0.053709 | 0.057363 | 0.0032956 | 0.0044541 | -0.048877 | 0.2363 | 74.2 | 71.4354 |  | 0.12151 | 0.30741 | 0.14579 | 0.1784 | 0.33325 | 0.24952 | 0.40812 | 71.0169
3 | IE1 | 750 | 0.071226 | 0.042834 | 0.046348 | 0.0094525 | 0.010004 | -0.019206 | 0.18299 | 77 | 74.4321 |  | 0.091653 | 0.2516 | 0.11132 | 0.14218 | 0.27524 | 0.20142 | 0.34364 | 74.4245
4 | IE1 | 750 | 0.050436 | 0.03688 | 0.04318 | 0.020492 | 0.020964 | -0.019714 | 0.15206 | 79.2 | 76.8037 |  | 0.067332 | 0.20113 | 0.085214 | 0.1117 | 0.2275 | 0.16902 | 0.30429 | 76.6699
5.5 | IE1 | 750 | 0.044277 | 0.032124 | 0.045916 | 0.0042195 | 0.0048179 | -0.016424 | 0.13477 | 81.4 | 79.1906 |  | 0.059579 | 0.17487 | 0.076342 | 0.098125 | 0.19347 | 0.15006 | 0.2497 | 80.0195
7.5 | IE1 | 750 | 0.036745 | 0.023048 | 0.02985 | 0.013037 | 0.013037 | -0.022723 | 0.12886 | 83.1 | 81.0455 |  | 0.047 | 0.15458 | 0.058715 | 0.079028 | 0.17164 | 0.11701 | 0.22185 | 81.843
11 | IE1 | 750 | 0.024652 | 0.019687 | 0.022146 | 0.0091362 | 0.009369 | -0.01118 | 0.10105 | 85 | 83.1296 |  | 0.034658 | 0.1237 | 0.043985 | 0.061433 | 0.13682 | 0.090785 | 0.17486 | 85.1162
15 | IE1 | 750 | 0.024393 | 0.020222 | 0.038168 | 0.0083087 | 0.0087157 | -0.0073126 | 0.088933 | 86.2 | 84.4518 |  | 0.035728 | 0.11608 | 0.048172 | 0.064207 | 0.132 | 0.10562 | 0.18143 | 84.6433
18.5 | IE1 | 750 | 0.022203 | 0.017858 | 0.036474 | 0.0076942 | 0.0079263 | -0.0081854 | 0.078338 | 86.9 | 85.2253 |  | 0.031948 | 0.10152 | 0.043464 | 0.057199 | 0.11623 | 0.095932 | 0.16231 | 86.0357
22 | IE1 | 750 | 0.0168 | 0.016986 | 0.028928 | 0.0091835 | 0.009391 | -0.0063169 | 0.072617 | 87.4 | 85.7788 |  | 0.025994 | 0.092037 | 0.035918 | 0.049256 | 0.10576 | 0.082354 | 0.14759 | 87.1392
30 | IE1 | 750 | 0.016597 | 0.016349 | 0.036438 | 0.010349 | 0.010603 | -0.002542 | 0.062211 | 88.3 | 86.7771 |  | 0.026417 | 0.085881 | 0.037623 | 0.050119 | 0.10138 | 0.088904 | 0.15001 | 86.9561
37 | IE1 | 750 | 0.015312 | 0.014178 | 0.032575 | 0.01033 | 0.010822 | -0.010339 | 0.069968 | 88.8 | 87.3328 |  | 0.022885 | 0.083781 | 0.032825 | 0.044836 | 0.098045 | 0.079676 | 0.14285 | 87.5007
45 | IE1 | 750 | 0.012635 | 0.017804 | 0.030571 | 0.0063367 | 0.0069281 | -0.0046129 | 0.049372 | 89.2 | 87.778 |  | 0.021055 | 0.065772 | 0.031418 | 0.040441 | 0.078839 | 0.074362 | 0.11903 | 89.3628
55 | IE1 | 750 | 0.012716 | 0.014913 | 0.034474 | 0.0078345 | 0.0076151 | -0.00073497 | 0.04776 | 89.7 | 88.3352 |  | 0.021553 | 0.068059 | 0.031957 | 0.041819 | 0.081637 | 0.077539 | 0.12458 | 88.9222
75 | IE1 | 750 | 0.013284 | 0.015478 | 0.042469 | 0.0036487 | 0.0041382 | -0.0023902 | 0.041687 | 90.3 | 89.005 |  | 0.021889 | 0.060275 | 0.033827 | 0.041582 | 0.073796 | 0.082405 | 0.11831 | 89.4202
90 | IE1 | 750 | 0.017119 | 0.020337 | 0.032992 | 0.0075112 | 0.0075103 | -0.001389 | 0.039626 | 90.7 | 89.4521 |  | 0.026542 | 0.064849 | 0.038017 | 0.046156 | 0.079406 | 0.083416 | 0.12371 | 88.9912
110 | IE1 | 750 | 0.013679 | 0.01635 | 0.031355 | 0.0065459 | 0.0065919 | -0.002022 | 0.031623 | 91.1 | 89.1171 |  | 0.021325 | 0.051376 | 0.031471 | 0.037817 | 0.064215 | 0.071562 | 0.10412 | 90.5697
132 | IE1 | 750 | 0.012979 | 0.014529 | 0.029052 | 0.0074892 | 0.007552 | -0.0018878 | 0.031512 | 91.5 | 89.5961 |  | 0.020071 | 0.050395 | 0.029356 | 0.035848 | 0.062763 | 0.067254 | 0.10122 | 90.808
160 | IE1 | 750 | 0.012033 | 0.012434 | 0.026198 | 0.0082714 | 0.0083609 | -0.0017368 | 0.030808 | 91.9 | 90.076 |  | 0.018432 | 0.048441 | 0.02668 | 0.03319 | 0.060097 | 0.061657 | 0.096369 | 91.2102
200 | IE1 | 750 | 0.011573 | 0.012338 | 0.020237 | 0.0089117 | 0.0096816 | -0.0056084 | 0.031434 | 92.5 | 90.7975 |  | 0.016662 | 0.044582 | 0.023794 | 0.029575 | 0.055504 | 0.053852 | 0.088568 | 91.8638
250 | IE1 | 750 | 0.011301 | 0.011447 | 0.024172 | 0.0079511 | 0.0079839 | -0.0017118 | 0.025776 | 92.5 | 90.7975 |  | 0.017012 | 0.042224 | 0.024624 | 0.030149 | 0.053103 | 0.056492 | 0.08692 | 92.0031
315 | IE1 | 750 | 0.010015 | 0.010769 | 0.019767 | 0.0079193 | 0.0079505 | -0.0017944 | 0.025296 | 92.5 | 90.7975 |  | 0.01523 | 0.039921 | 0.021845 | 0.027255 | 0.04979 | 0.049945 | 0.079922 | 92.5992
355 | IE1 | 750 | 0.0095462 | 0.010219 | 0.018889 | 0.0079005 | 0.0079319 | -0.0017827 | 0.023793 | 92.5 | 90.7975 |  | 0.014477 | 0.037763 | 0.02079 | 0.025918 | 0.047322 | 0.04767 | 0.076498 | 92.8938
400 | IE1 | 750 | 0.0090698 | 0.0096637 | 0.017998 | 0.0078986 | 0.0079379 | -0.0017315 | 0.022265 | 92.5 | 90.7975 |  | 0.013724 | 0.035614 | 0.019731 | 0.024585 | 0.044868 | 0.045391 | 0.073101 | 93.1879
500 | IE1 | 750 | 0.0085819 | 0.0091129 | 0.017121 | 0.0078789 | 0.007919 | -0.0016239 | 0.020677 | 92.5 | 90.7975 |  | 0.012971 | 0.033448 | 0.018675 | 0.023256 | 0.042391 | 0.043123 | 0.069667 | 93.487
560 | IE1 | 750 | 0.0083585 | 0.0089959 | 0.017088 | 0.007812 | 0.0079881 | -0.0015547 | 0.019192 | 92.5 | 90.7975 |  | 0.01264 | 0.031765 | 0.018308 | 0.022625 | 0.040669 | 0.042413 | 0.06788 | 93.6435
630 | IE1 | 750 | 0.008045 | 0.0088333 | 0.017185 | 0.0078142 | 0.0079256 | -0.0010448 | 0.017311 | 92.5 | 90.7975 |  | 0.012301 | 0.030042 | 0.017947 | 0.022035 | 0.038913 | 0.041804 | 0.06607 | 93.8025
710 | IE1 | 750 | 0.008051 | 0.0087124 | 0.018993 | 0.0078488 | 0.0079212 | -0.00088929 | 0.015171 | 92.5 | 90.7975 |  | 0.012296 | 0.028155 | 0.01825 | 0.02198 | 0.037342 | 0.043047 | 0.065808 | 93.8256
800 | IE1 | 750 | 0.0080355 | 0.0086169 | 0.020774 | 0.0078167 | 0.0079529 | -0.00067047 | 0.013 | 92.5 | 90.7975 |  | 0.012286 | 0.026269 | 0.018551 | 0.021926 | 0.035764 | 0.044284 | 0.065526 | 93.8504
900 | IE1 | 750 | 0.0077859 | 0.0081762 | 0.018666 | 0.0078411 | 0.0079122 | -0.0010065 | 0.014549 | 92.5 | 90.7975 |  | 0.011808 | 0.026994 | 0.017567 | 0.021149 | 0.035982 | 0.0417 | 0.063924 | 93.9917
1000 | IE1 | 750 | 0.0075095 | 0.0077642 | 0.016521 | 0.0078537 | 0.0078893 | -0.0012539 | 0.016026 | 92.5 | 90.7975 |  | 0.011325 | 0.027712 | 0.016579 | 0.020376 | 0.036193 | 0.03911 | 0.06231 | 94.1345
IE3
[10 empty] | 34-30-2 | 34-30-2 | Losses | PL7 | PL3 | PL6 | PL5 | PL2 | PL4 | PL1 | Eff / %
[10 empty] | Reference | Nominal | n= | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
Power / kW | Class | Speed | cL1 | cL2 | cL3 | cL4 | cL5 | cL6 | cL7 | % | % | T= | 0.25 | 1 | 0.25 | 0.5 | 1 | 0.5 | 1 | 1
0.12 | IE3 | 1500 | 0.25457 | 0.091513 | 0.060052 | 0.0023448 | 0.0030725 | -0.22985 | 0.43317 | 64.8 | 61.5502 |  | 0.25086 | 0.4853 | 0.28507 | 0.30919 | 0.5206 | 0.40085 | 0.61487 | 61.9244
0.18 | IE3 | 1500 | 0.19749 | 0.074376 | 0.048893 | 0.0016435 | 0.0023272 | -0.094329 | 0.2499 | 69.9 | 66.8804 |  | 0.21121 | 0.37527 | 0.23903 | 0.26256 | 0.40388 | 0.33706 | 0.4803 | 67.5538
0.25 | IE3 | 1500 | 0.1534 | 0.065701 | 0.047483 | 0.0046724 | 0.0053196 | -0.078571 | 0.1955 | 73.5 | 70.6901 |  | 0.16547 | 0.29123 | 0.19093 | 0.20863 | 0.31872 | 0.27868 | 0.39351 | 71.7612
0.37 | IE3 | 1500 | 0.10721 | 0.048873 | 0.032934 | 0.0031781 | 0.0035671 | -0.03348 | 0.15982 | 77.3 | 74.7546 |  | 0.12317 | 0.24885 | 0.14166 | 0.16372 | 0.2687 | 0.21392 | 0.32211 | 75.6369
0.55 | IE3 | 1500 | 0.08919 | 0.037865 | 0.025452 | 7.6299e-06 | 0.0003327 | -0.021167 | 0.12909 | 80.8 | 78.5381 |  | 0.10303 | 0.2082 | 0.11727 | 0.1362 | 0.2225 | 0.17428 | 0.26078 | 79.3163
0.75 | IE3 | 1500 | 0.071 | 0.034481 | 0.022121 | 0.001268 | 0.0015358 | -0.017321 | 0.12614 | 82.5 | 80.3898 |  | 0.084582 | 0.19024 | 0.097388 | 0.1169 | 0.20361 | 0.15118 | 0.23923 | 80.6955
1.1 | IE3 | 1500 | 0.057233 | 0.031643 | 0.022538 | 0.00072138 | 0.0010901 | -0.013396 | 0.11647 | 84.1 | 82.1409 |  | 0.070498 | 0.16987 | 0.082659 | 0.10127 | 0.18239 | 0.13429 | 0.2163 | 82.2167
1.5 | IE3 | 1500 | 0.049428 | 0.028837 | 0.018452 | 0.00095827 | 0.0013594 | -0.015575 | 0.11472 | 85.3 | 83.4597 |  | 0.061087 | 0.15726 | 0.071786 | 0.089555 | 0.16842 | 0.11819 | 0.19818 | 83.4602
2.2 | IE3 | 1500 | 0.030458 | 0.02582 | 0.017448 | 0.0081354 | 0.0069574 | 0.013335 | 0.075256 | 86.7 | 85.0042 |  | 0.046195 | 0.12906 | 0.05613 | 0.074664 | 0.14213 | 0.10298 | 0.17741 | 84.9321
3 | IE3 | 1500 | 0.032125 | 0.021792 | 0.013197 | 0.0036526 | 0.0038088 | -0.0069162 | 0.091522 | 87.7 | 86.1112 |  | 0.04246 | 0.12415 | 0.050485 | 0.066437 | 0.1337 | 0.088401 | 0.15918 | 86.2678
4 | IE3 | 1500 | 0.028982 | 0.02288 | 0.015947 | 0.003462 | 0.0039011 | -0.010782 | 0.081698 | 88.6 | 87.1104 |  | 0.038178 | 0.10772 | 0.046988 | 0.060118 | 0.11803 | 0.084682 | 0.14609 | 87.2534
5.5 | IE3 | 1500 | 0.02417 | 0.020309 | 0.015133 | 0.0060186 | 0.006343 | -0.0078096 | 0.070301 | 89.6 | 88.2237 |  | 0.032754 | 0.094586 | 0.040837 | 0.052927 | 0.10519 | 0.076373 | 0.13447 | 88.1473
7.5 | IE3 | 1500 | 0.019793 | 0.018445 | 0.012707 | 0.0056291 | 0.0059983 | -0.013416 | 0.076459 | 90.4 | 89.1167 |  | 0.026734 | 0.090023 | 0.033886 | 0.045677 | 0.099549 | 0.066258 | 0.12561 | 88.8403
11 | IE3 | 1500 | 0.016546 | 0.016828 | 0.012313 | 0.0047738 | 0.0049415 | -0.0074819 | 0.060327 | 91.4 | 90.236 |  | 0.023516 | 0.07587 | 0.030164 | 0.040284 | 0.084506 | 0.059456 | 0.10825 | 90.2326
15 | IE3 | 1500 | 0.013671 | 0.015292 | 0.01149 | 0.0051031 | 0.0052812 | -0.0064204 | 0.053552 | 92.1 | 91.0214 |  | 0.020054 | 0.066949 | 0.026173 | 0.035335 | 0.075193 | 0.053227 | 0.097969 | 91.0773
18.5 | IE3 | 1500 | 0.012352 | 0.014118 | 0.010285 | 0.0046038 | 0.0047445 | -0.0043969 | 0.052271 | 92.6 | 91.5834 |  | 0.018783 | 0.065846 | 0.024368 | 0.033724 | 0.073345 | 0.049962 | 0.093978 | 91.4095
22 | IE3 | 1500 | 0.011918 | 0.013634 | 0.010353 | 0.0021076 | 0.0023197 | -0.0046048 | 0.049588 | 93 | 92.0336 |  | 0.017964 | 0.061629 | 0.023374 | 0.031827 | 0.06794 | 0.047107 | 0.085316 | 92.1391
30 | IE3 | 1500 | 0.0084883 | 0.011455 | 0.0070582 | 0.0053772 | 0.0076091 | 0.00027651 | 0.039366 | 93.6 | 92.71 |  | 0.014437 | 0.053255 | 0.018797 | 0.027108 | 0.060214 | 0.040228 | 0.07963 | 92.6243
37 | IE3 | 1500 | 0.018197 | 0.0025175 | 0.011992 | 0.0074485 | -0.0021135 | -0.0066666 | 0.043912 | 93.9 | 93.0486 |  | 0.020762 | 0.058552 | 0.023731 | 0.030898 | 0.062895 | 0.041685 | 0.075287 | 92.9984
45 | IE3 | 1500 | 0.0086984 | 0.010905 | 0.0098928 | 0.0038779 | 0.0039608 | -0.0024456 | 0.037748 | 94.2 | 93.3875 |  | 0.013867 | 0.048563 | 0.018555 | 0.025571 | 0.054856 | 0.03967 | 0.072637 | 93.2282
55 | IE3 | 1500 | 0.0065304 | 0.010949 | 0.01031 | 0.0040226 | 0.0042104 | 0.00086425 | 0.027621 | 94.6 | 93.8399 |  | 0.011934 | 0.039666 | 0.016716 | 0.022686 | 0.046132 | 0.037185 | 0.064508 | 93.9401
75 | IE3 | 1500 | 0.006718 | 0.01051 | 0.010356 | 0.0056628 | 0.0063882 | -0.0051528 | 0.025479 | 95 | 94.2928 |  | 0.01041 | 0.032133 | 0.015143 | 0.019462 | 0.039316 | 0.03439 | 0.059961 | 94.3431
90 | IE3 | 1500 | 0.006078 | 0.010583 | 0.009368 | 0.0051934 | 0.0052025 | -0.0017806 | 0.022542 | 95.2 | 94.5195 |  | 0.010374 | 0.031695 | 0.014919 | 0.019431 | 0.038371 | 0.033373 | 0.057187 | 94.5907
110 | IE3 | 1500 | 0.0082744 | 0.013068 | 0.010604 | 0.0051336 | 0.0051717 | -0.0020036 | 0.019747 | 95.4 | 94.3154 |  | 0.013038 | 0.031554 | 0.018434 | 0.022359 | 0.039062 | 0.038458 | 0.059995 | 94.3401
132 | IE3 | 1500 | 0.0075248 | 0.010299 | 0.0071649 | 0.0057577 | 0.0059459 | -0.0036336 | 0.024229 | 95.6 | 94.5598 |  | 0.011266 | 0.032953 | 0.015344 | 0.019797 | 0.039426 | 0.032155 | 0.057287 | 94.5817
160 | IE3 | 1500 | 0.0070854 | 0.010717 | 0.0068092 | 0.0060462 | 0.0061959 | -0.0027398 | 0.020445 | 95.8 | 94.8046 |  | 0.010902 | 0.029795 | 0.015025 | 0.019031 | 0.036424 | 0.031414 | 0.054559 | 94.8264
200 | IE3 | 1500 | 0.0066739 | 0.0099961 | 0.0075101 | 0.0052014 | 0.0053742 | -0.0026764 | 0.019932 | 96 | 95.0495 |  | 0.010321 | 0.028534 | 0.014373 | 0.01818 | 0.034749 | 0.030469 | 0.052011 | 95.056
250 | IE3 | 1500 | 0.0064476 | 0.0092942 | 0.0071015 | 0.004774 | 0.0049601 | -0.0021505 | 0.018256 | 96 | 95.0495 |  | 0.0099124 | 0.026824 | 0.0137 | 0.017266 | 0.032603 | 0.028766 | 0.048683 | 95.3577
315 | IE3 | 1500 | 0.0062476 | 0.0085962 | 0.0066847 | 0.0043451 | 0.0045466 | -0.0017549 | 0.016686 | 96 | 95.0495 |  | 0.0095042 | 0.025116 | 0.013028 | 0.016338 | 0.030457 | 0.027045 | 0.045351 | 95.6616
355 | IE3 | 1500 | 0.0059066 | 0.0082458 | 0.0065534 | 0.0042782 | 0.0044258 | -0.001602 | 0.016051 | 96 | 95.0495 |  | 0.0090645 | 0.024173 | 0.012473 | 0.015691 | 0.029363 | 0.026094 | 0.043859 | 95.7984
400 | IE3 | 1500 | 0.0052957 | 0.0078804 | 0.0063109 | 0.0042525 | 0.0044535 | -0.00027102 | 0.014583 | 96 | 95.0495 |  | 0.0085877 | 0.023314 | 0.01186 | 0.015134 | 0.028365 | 0.025174 | 0.042505 | 95.9228
500 | IE3 | 1500 | 0.0052337 | 0.0075384 | 0.0062947 | 0.0041584 | 0.0041695 | -0.0013263 | 0.014792 | 96 | 95.0495 |  | 0.0081859 | 0.022278 | 0.011365 | 0.014392 | 0.027164 | 0.024184 | 0.04086 | 96.0744
560 | IE3 | 1500 | 0.0051495 | 0.0074354 | 0.0068389 | 0.0040511 | 0.0039219 | -0.0015217 | 0.013076 | 96 | 95.0495 |  | 0.0079512 | 0.020248 | 0.011202 | 0.013837 | 0.025137 | 0.023925 | 0.038951 | 96.2509
630 | IE3 | 1500 | 0.0048412 | 0.0072455 | 0.0074736 | 0.0041274 | 0.0041713 | -0.00066826 | 0.010426 | 96 | 95.0495 |  | 0.007685 | 0.01817 | 0.011011 | 0.013381 | 0.023197 | 0.023907 | 0.037617 | 96.3747
710 | IE3 | 1500 | 0.0048738 | 0.0072721 | 0.0079769 | 0.004143 | 0.0041685 | -0.0006674 | 0.010112 | 96 | 95.0495 |  | 0.0077365 | 0.017931 | 0.011164 | 0.013477 | 0.023062 | 0.024395 | 0.037879 | 96.3503
800 | IE3 | 1500 | 0.0049087 | 0.0072966 | 0.0084782 | 0.0041469 | 0.0041649 | -0.00067387 | 0.0098058 | 96 | 95.0495 |  | 0.0077882 | 0.017692 | 0.011316 | 0.01357 | 0.022923 | 0.024876 | 0.038127 | 96.3273
900 | IE3 | 1500 | 0.0046206 | 0.0069263 | 0.007634 | 0.0041424 | 0.00416 | -0.00071724 | 0.0096855 | 96 | 95.0495 |  | 0.0073363 | 0.017093 | 0.010613 | 0.012833 | 0.022072 | 0.023319 | 0.036452 | 96.483
1000 | IE3 | 1500 | 0.0043192 | 0.0065586 | 0.0067904 | 0.0041299 | 0.0041499 | -0.00070546 | 0.0095142 | 96 | 95.0495 |  | 0.0068822 | 0.016484 | 0.0099082 | 0.012097 | 0.021207 | 0.021764 | 0.034757 | 96.6411
0.12 | IE3 | 3000 | 0.2303 | 0.083134 | 0.082508 | -0.00098475 | 0.0022043 | -0.28566 | 0.53768 | 60.8 | 57.4235 |  | 0.21842 | 0.50815 | 0.25469 | 0.2841 | 0.54457 | 0.38783 | 0.64918 | 60.6364
0.18 | IE3 | 3000 | 0.21625 | 0.066143 | 0.090993 | 0.0020422 | 0.0037164 | -0.27538 | 0.44286 | 65.9 | 62.6932 |  | 0.19735 | 0.40669 | 0.23103 | 0.24558 | 0.4415 | 0.34785 | 0.54662 | 64.6571
0.25 | IE3 | 3000 | 0.13408 | 0.058557 | 0.071191 | 0.0030945 | 0.0056109 | -0.15141 | 0.35286 | 69.7 | 66.6699 |  | 0.13744 | 0.35574 | 0.16554 | 0.19441 | 0.38556 | 0.27852 | 0.47398 | 67.8433
0.37 | IE3 | 3000 | 0.090667 | 0.04529 | 0.060452 | 0.0074741 | 0.0098086 | -0.099446 | 0.25563 | 73.5 | 70.6901 |  | 0.097038 | 0.26443 | 0.11993 | 0.14416 | 0.2908 | 0.21491 | 0.36987 | 72.9994
0.55 | IE3 | 3000 | 0.064453 | 0.03966 | 0.051483 | 0.0084993 | 0.010758 | -0.074043 | 0.21145 | 77.8 | 75.2928 |  | 0.072466 | 0.21779 | 0.092293 | 0.11473 | 0.2415 | 0.17625 | 0.31226 | 76.2043
0.75 | IE3 | 3000 | 0.057633 | 0.028657 | 0.02681 | 0.0071638 | 0.010887 | -0.040204 | 0.19551 | 80.7 | 78.4295 |  | 0.068796 | 0.22425 | 0.081226 | 0.10902 | 0.24027 | 0.14639 | 0.28646 | 77.7328
1.1 | IE3 | 3000 | 0.046024 | 0.025551 | 0.02519 | 0.0047287 | 0.0058072 | -0.029217 | 0.14705 | 82.7 | 80.6082 |  | 0.05597 | 0.17337 | 0.067223 | 0.088207 | 0.18675 | 0.12155 | 0.22514 | 81.6234
1.5 | IE3 | 3000 | 0.049105 | 0.025151 | 0.033243 | 0.0007372 | 0.0013 | -0.018546 | 0.11152 | 84.2 | 82.2507 |  | 0.05982 | 0.15071 | 0.072368 | 0.088771 | 0.16366 | 0.12661 | 0.20251 | 83.1596
2.2 | IE3 | 3000 | 0.048093 | 0.025354 | 0.02708 | 0.0015558 | 0.0021026 | -0.023074 | 0.11155 | 85.9 | 84.1208 |  | 0.05736 | 0.14512 | 0.068825 | 0.084217 | 0.15732 | 0.11779 | 0.19266 | 83.8461
3 | IE3 | 3000 | 0.035316 | 0.021238 | 0.022981 | 0.0046868 | 0.0049603 | -0.0095232 | 0.09073 | 87.1 | 85.4466 |  | 0.045444 | 0.12475 | 0.055194 | 0.070497 | 0.13647 | 0.099868 | 0.17039 | 85.4417
4 | IE3 | 3000 | 0.02594 | 0.018968 | 0.022208 | 0.010539 | 0.010782 | -0.010139 | 0.078206 | 88.1 | 86.555 |  | 0.03463 | 0.10345 | 0.043827 | 0.057449 | 0.11701 | 0.086928 | 0.1565 | 86.4675
5.5 | IE3 | 3000 | 0.023461 | 0.017021 | 0.02433 | 0.0022358 | 0.0025528 | -0.0087028 | 0.071408 | 89.2 | 87.778 |  | 0.031569 | 0.092661 | 0.040451 | 0.051994 | 0.10252 | 0.07951 | 0.13231 | 88.3153
7.5 | IE3 | 3000 | 0.019853 | 0.012453 | 0.016128 | 0.0070438 | 0.0070438 | -0.012277 | 0.06962 | 90.1 | 88.7816 |  | 0.025393 | 0.083518 | 0.031723 | 0.042698 | 0.092737 | 0.063221 | 0.11986 | 89.2966
11 | IE3 | 3000 | 0.013479 | 0.010765 | 0.012109 | 0.0049955 | 0.0051228 | -0.0061133 | 0.055255 | 91.2 | 90.0118 |  | 0.018951 | 0.067638 | 0.02405 | 0.033591 | 0.074809 | 0.04964 | 0.095613 | 91.2731
15 | IE3 | 3000 | 0.01343 | 0.011133 | 0.021014 | 0.0045743 | 0.0047985 | -0.004026 | 0.048962 | 91.9 | 90.7968 |  | 0.01967 | 0.063906 | 0.026521 | 0.035349 | 0.072673 | 0.058147 | 0.099885 | 90.9186
18.5 | IE3 | 3000 | 0.012114 | 0.0097437 | 0.019901 | 0.0041981 | 0.0043247 | -0.0044661 | 0.042743 | 92.4 | 91.3585 |  | 0.017431 | 0.05539 | 0.023715 | 0.031209 | 0.063418 | 0.052342 | 0.088558 | 91.8646
22 | IE3 | 3000 | 0.0091767 | 0.0092787 | 0.015802 | 0.0050164 | 0.0051297 | -0.0034505 | 0.039666 | 92.7 | 91.6959 |  | 0.014199 | 0.050275 | 0.01962 | 0.026905 | 0.057773 | 0.044985 | 0.080619 | 92.5395
30 | IE3 | 3000 | 0.0089948 | 0.0088605 | 0.019748 | 0.0056088 | 0.0057467 | -0.0013777 | 0.033716 | 93.3 | 92.3717 |  | 0.014317 | 0.046544 | 0.02039 | 0.027162 | 0.054941 | 0.048182 | 0.081297 | 92.4815
37 | IE3 | 3000 | 0.0081628 | 0.0075582 | 0.017365 | 0.0055068 | 0.0057693 | -0.0055114 | 0.037299 | 93.7 | 92.8228 |  | 0.0122 | 0.044663 | 0.017499 | 0.023901 | 0.052267 | 0.042474 | 0.07615 | 92.9239
45 | IE3 | 3000 | 0.0066608 | 0.0093862 | 0.016117 | 0.0033406 | 0.0036524 | -0.0024319 | 0.026028 | 94 | 93.1615 |  | 0.0111 | 0.034674 | 0.016563 | 0.02132 | 0.041563 | 0.039203 | 0.062753 | 94.0953
55 | IE3 | 3000 | 0.0066939 | 0.0078502 | 0.018147 | 0.0041241 | 0.0040086 | -0.00038689 | 0.025141 | 94.3 | 93.5006 |  | 0.011345 | 0.035826 | 0.016822 | 0.022014 | 0.042974 | 0.040817 | 0.065578 | 93.8458
75 | IE3 | 3000 | 0.0069211 | 0.0080641 | 0.022127 | 0.001901 | 0.002156 | -0.0012453 | 0.021719 | 94.7 | 93.9531 |  | 0.011404 | 0.031404 | 0.017624 | 0.021664 | 0.038448 | 0.042933 | 0.061643 | 94.1937
90 | IE3 | 3000 | 0.0087873 | 0.010439 | 0.016935 | 0.0038555 | 0.003855 | -0.00071296 | 0.02034 | 95 | 94.2928 |  | 0.013624 | 0.033287 | 0.019514 | 0.023692 | 0.040759 | 0.042817 | 0.063499 | 94.0293
110 | IE3 | 3000 | 0.0070596 | 0.0084381 | 0.016182 | 0.0033784 | 0.0034021 | -0.0010436 | 0.016321 | 95.2 | 94.0711 |  | 0.011006 | 0.026515 | 0.016242 | 0.019517 | 0.033141 | 0.036933 | 0.053737 | 94.9003
132 | IE3 | 3000 | 0.0067366 | 0.0075412 | 0.015079 | 0.0038873 | 0.0039199 | -0.00097989 | 0.016356 | 95.4 | 94.3154 |  | 0.010418 | 0.026158 | 0.015237 | 0.018607 | 0.032577 | 0.034908 | 0.052541 | 95.0082
160 | IE3 | 3000 | 0.0062835 | 0.006493 | 0.01368 | 0.0043192 | 0.004366 | -0.00090694 | 0.016087 | 95.6 | 94.5598 |  | 0.0096251 | 0.025295 | 0.013932 | 0.017331 | 0.031382 | 0.032196 | 0.050322 | 95.2089
200 | IE3 | 3000 | 0.0062578 | 0.0066714 | 0.010942 | 0.0048187 | 0.005235 | -0.0030325 | 0.016997 | 95.8 | 94.8046 |  | 0.0090095 | 0.024106 | 0.012866 | 0.015992 | 0.030012 | 0.029118 | 0.04789 | 95.4299
250 | IE3 | 3000 | 0.0061106 | 0.0061896 | 0.01307 | 0.0042992 | 0.004317 | -0.00092559 | 0.013937 | 95.8 | 94.8046 |  | 0.0091986 | 0.022831 | 0.013314 | 0.016302 | 0.028713 | 0.030546 | 0.046998 | 95.5111
315 | IE3 | 3000 | 0.005415 | 0.0058227 | 0.010688 | 0.004282 | 0.0042989 | -0.00097025 | 0.013678 | 95.8 | 94.8046 |  | 0.0082348 | 0.021586 | 0.011812 | 0.014737 | 0.026922 | 0.027006 | 0.043215 | 95.8575
355 | IE3 | 3000 | 0.0051617 | 0.0055256 | 0.010214 | 0.0042719 | 0.0042888 | -0.00096392 | 0.012865 | 95.8 | 94.8046 |  | 0.0078281 | 0.020419 | 0.011242 | 0.014014 | 0.025587 | 0.025776 | 0.041363 | 96.028
400 | IE3 | 3000 | 0.0049041 | 0.0052253 | 0.0097315 | 0.0042708 | 0.0042921 | -0.00093627 | 0.012039 | 95.8 | 94.8046 |  | 0.0074205 | 0.019257 | 0.010669 | 0.013293 | 0.02426 | 0.024543 | 0.039526 | 96.1977
500 | IE3 | 3000 | 0.0046403 | 0.0049275 | 0.0092576 | 0.0042602 | 0.0042819 | -0.00087804 | 0.01118 | 95.8 | 94.8046 |  | 0.0070133 | 0.018086 | 0.010098 | 0.012575 | 0.022921 | 0.023317 | 0.03767 | 96.3698
560 | IE3 | 3000 | 0.0045195 | 0.0048642 | 0.0092395 | 0.004224 | 0.0043193 | -0.00084063 | 0.010377 | 95.8 | 94.8046 |  | 0.0068343 | 0.017176 | 0.0098994 | 0.012233 | 0.02199 | 0.022933 | 0.036703 | 96.4596
630 | IE3 | 3000 | 0.00435 | 0.0047762 | 0.0092923 | 0.0042252 | 0.0042855 | -0.00056496 | 0.0093601 | 95.8 | 94.8046 |  | 0.0066514 | 0.016244 | 0.009704 | 0.011915 | 0.02104 | 0.022604 | 0.035724 | 96.5508
710 | IE3 | 3000 | 0.0043533 | 0.0047109 | 0.010269 | 0.0042439 | 0.0042831 | -0.00048085 | 0.008203 | 95.8 | 94.8046 |  | 0.0066484 | 0.015224 | 0.0098681 | 0.011885 | 0.020191 | 0.023276 | 0.035583 | 96.564
800 | IE3 | 3000 | 0.0043449 | 0.0046592 | 0.011233 | 0.0042266 | 0.0043002 | -0.00036253 | 0.0070292 | 95.8 | 94.8046 |  | 0.0066433 | 0.014204 | 0.010031 | 0.011856 | 0.019338 | 0.023945 | 0.03543 | 96.5782
900 | IE3 | 3000 | 0.0042099 | 0.0044209 | 0.010093 | 0.0042397 | 0.0042782 | -0.00054423 | 0.0078668 | 95.8 | 94.8046 |  | 0.0063845 | 0.014596 | 0.0094985 | 0.011436 | 0.019456 | 0.022548 | 0.034564 | 96.6591
1000 | IE3 | 3000 | 0.0040605 | 0.0041982 | 0.0089333 | 0.0042466 | 0.0042658 | -0.00067801 | 0.0086654 | 95.8 | 94.8046 |  | 0.0061234 | 0.014984 | 0.0089643 | 0.011018 | 0.01957 | 0.021147 | 0.033692 | 96.7406
0.12 | IE3 | 1000 | 0.34356 | 0.1235 | 0.081044 | 0.0031645 | 0.0041466 | -0.3102 | 0.5846 | 57.7 | 54.2574 |  | 0.33855 | 0.65495 | 0.38472 | 0.41727 | 0.70259 | 0.54098 | 0.82981 | 54.6503
0.18 | IE3 | 1000 | 0.2591 | 0.097578 | 0.064145 | 0.0021562 | 0.0030531 | -0.12375 | 0.32785 | 63.9 | 60.6176 |  | 0.2771 | 0.49233 | 0.31359 | 0.34447 | 0.52986 | 0.44221 | 0.63013 | 61.3448
0.25 | IE3 | 1000 | 0.19475 | 0.083411 | 0.060282 | 0.0059318 | 0.0067534 | -0.099749 | 0.2482 | 68.6 | 65.5143 |  | 0.21007 | 0.36972 | 0.24239 | 0.26487 | 0.40463 | 0.35379 | 0.49958 | 66.6854
0.37 | IE3 | 1000 | 0.13163 | 0.060004 | 0.040435 | 0.0039019 | 0.0043795 | -0.041105 | 0.19622 | 73.5 | 70.6901 |  | 0.15123 | 0.30553 | 0.17392 | 0.20101 | 0.3299 | 0.26265 | 0.39547 | 71.6606
0.55 | IE3 | 1000 | 0.11085 | 0.047062 | 0.031634 | 9.483e-06 | 0.00041351 | -0.026307 | 0.16045 | 77.2 | 74.6471 |  | 0.12805 | 0.25876 | 0.14575 | 0.16928 | 0.27654 | 0.21661 | 0.32411 | 75.5223
0.75 | IE3 | 1000 | 0.091131 | 0.044258 | 0.028392 | 0.0016275 | 0.0019713 | -0.022232 | 0.16191 | 78.6 | 76.1554 |  | 0.10856 | 0.24417 | 0.125 | 0.15005 | 0.26134 | 0.19404 | 0.30705 | 76.5079
1.1 | IE3 | 1000 | 0.071009 | 0.039259 | 0.027963 | 0.00089501 | 0.0013525 | -0.016621 | 0.1445 | 81 | 78.7555 |  | 0.087467 | 0.21076 | 0.10255 | 0.12564 | 0.2263 | 0.16661 | 0.26836 | 78.8419
1.5 | IE3 | 1000 | 0.06084 | 0.035495 | 0.022712 | 0.0011795 | 0.0016733 | -0.019171 | 0.1412 | 82.5 | 80.3898 |  | 0.07519 | 0.19356 | 0.08836 | 0.11023 | 0.2073 | 0.14547 | 0.24393 | 80.3904
2.2 | IE3 | 1000 | 0.036978 | 0.031347 | 0.021183 | 0.0098769 | 0.0084467 | 0.01619 | 0.091365 | 84.3 | 82.3604 |  | 0.056084 | 0.15669 | 0.068146 | 0.090646 | 0.17255 | 0.12503 | 0.21539 | 82.2783
3 | IE3 | 1000 | 0.038532 | 0.026139 | 0.015829 | 0.0043811 | 0.0045685 | -0.0082957 | 0.10978 | 85.6 | 83.7901 |  | 0.050929 | 0.14892 | 0.060554 | 0.079688 | 0.16037 | 0.10603 | 0.19093 | 83.968
4 | IE3 | 1000 | 0.034253 | 0.027042 | 0.018847 | 0.0040918 | 0.0046107 | -0.012743 | 0.096559 | 86.8 | 85.1147 |  | 0.045123 | 0.12732 | 0.055535 | 0.071054 | 0.1395 | 0.10009 | 0.17266 | 85.2761
5.5 | IE3 | 1000 | 0.028396 | 0.02386 | 0.017778 | 0.0070708 | 0.0074519 | -0.0091749 | 0.082592 | 88 | 86.444 |  | 0.03848 | 0.11112 | 0.047976 | 0.06218 | 0.12359 | 0.089725 | 0.15797 | 86.3578
7.5 | IE3 | 1000 | 0.022801 | 0.021248 | 0.014638 | 0.0064846 | 0.00691 | -0.015455 | 0.08808 | 89.1 | 87.6667 |  | 0.030797 | 0.10371 | 0.039036 | 0.052619 | 0.11468 | 0.076328 | 0.14471 | 87.3587
11 | IE3 | 1000 | 0.018889 | 0.019212 | 0.014057 | 0.00545 | 0.0056414 | -0.0085417 | 0.068872 | 90.3 | 89.005 |  | 0.026847 | 0.086617 | 0.034437 | 0.045991 | 0.096475 | 0.067878 | 0.12358 | 89.0012
15 | IE3 | 1000 | 0.015379 | 0.017202 | 0.012925 | 0.0057406 | 0.0059409 | -0.0072224 | 0.060241 | 91.2 | 90.0118 |  | 0.02256 | 0.075313 | 0.029443 | 0.039749 | 0.084586 | 0.059876 | 0.11021 | 90.0733
18.5 | IE3 | 1000 | 0.013991 | 0.01599 | 0.01165 | 0.0052144 | 0.0053737 | -0.0049801 | 0.059204 | 91.7 | 90.5724 |  | 0.021274 | 0.074579 | 0.0276 | 0.038197 | 0.083073 | 0.056589 | 0.10644 | 90.3798
22 | IE3 | 1000 | 0.013396 | 0.015324 | 0.011636 | 0.0023689 | 0.0026072 | -0.0051756 | 0.055734 | 92.2 | 91.1337 |  | 0.020191 | 0.069268 | 0.026271 | 0.035772 | 0.076362 | 0.052946 | 0.095891 | 91.25
30 | IE3 | 1000 | 0.0094877 | 0.012804 | 0.0078892 | 0.0060103 | 0.0085049 | 0.00030907 | 0.044 | 92.9 | 91.921 |  | 0.016136 | 0.059525 | 0.02101 | 0.0303 | 0.067303 | 0.044964 | 0.089006 | 91.8269
37 | IE3 | 1000 | 0.020115 | 0.0027829 | 0.013256 | 0.0082338 | -0.0023364 | -0.0073694 | 0.048542 | 93.3 | 92.3717 |  | 0.022951 | 0.064725 | 0.026233 | 0.034155 | 0.069526 | 0.046079 | 0.083224 | 92.317
45 | IE3 | 1000 | 0.0094987 | 0.011908 | 0.010803 | 0.0042347 | 0.0043252 | -0.0026706 | 0.041221 | 93.7 | 92.8228 |  | 0.015143 | 0.05303 | 0.020262 | 0.027923 | 0.059903 | 0.04332 | 0.07932 | 92.6509
55 | IE3 | 1000 | 0.007173 | 0.012027 | 0.011324 | 0.0044184 | 0.0046247 | 0.00094929 | 0.030339 | 94.1 | 93.2745 |  | 0.013108 | 0.043569 | 0.018361 | 0.024918 | 0.050671 | 0.040844 | 0.070856 | 93.3833
75 | IE3 | 1000 | 0.0072862 | 0.011399 | 0.011231 | 0.0061416 | 0.0069284 | -0.0055886 | 0.027633 | 94.6 | 93.8399 |  | 0.011291 | 0.034851 | 0.016424 | 0.021108 | 0.042641 | 0.037298 | 0.065031 | 93.894
90 | IE3 | 1000 | 0.0064783 | 0.01128 | 0.009985 | 0.0055354 | 0.0055451 | -0.0018979 | 0.024027 | 94.9 | 94.1795 |  | 0.011058 | 0.033782 | 0.015901 | 0.020711 | 0.040898 | 0.035571 | 0.060953 | 94.2549
110 | IE3 | 1000 | 0.0088419 | 0.013964 | 0.011331 | 0.0054856 | 0.0055264 | -0.002141 | 0.021101 | 95.1 | 93.9491 |  | 0.013932 | 0.033718 | 0.019698 | 0.023893 | 0.041741 | 0.041095 | 0.064109 | 93.9753
132 | IE3 | 1000 | 0.0078834 | 0.01079 | 0.0075063 | 0.006032 | 0.0062292 | -0.0038067 | 0.025383 | 95.4 | 94.3154 |  | 0.011803 | 0.034524 | 0.016075 | 0.020741 | 0.041304 | 0.033687 | 0.060017 | 94.3381
160 | IE3 | 1000 | 0.0074384 | 0.011251 | 0.0071484 | 0.0063474 | 0.0065045 | -0.0028763 | 0.021464 | 95.6 | 94.5598 |  | 0.011445 | 0.031279 | 0.015773 | 0.019979 | 0.038238 | 0.032978 | 0.057277 | 94.5826
200 | IE3 | 1000 | 0.0070223 | 0.010518 | 0.0079021 | 0.0054729 | 0.0056547 | -0.0028161 | 0.020972 | 95.8 | 94.8046 |  | 0.01086 | 0.030023 | 0.015123 | 0.019129 | 0.036563 | 0.032059 | 0.054726 | 94.8114
250 | IE3 | 1000 | 0.0067842 | 0.0097792 | 0.0074721 | 0.0050231 | 0.005219 | -0.0022627 | 0.019209 | 95.8 | 94.8046 |  | 0.01043 | 0.028224 | 0.014415 | 0.018167 | 0.034304 | 0.030267 | 0.051224 | 95.1272
315 | IE3 | 1000 | 0.0065737 | 0.0090448 | 0.0070336 | 0.0045719 | 0.0047839 | -0.0018465 | 0.017557 | 95.8 | 94.8046 |  | 0.01 | 0.026426 | 0.013708 | 0.017191 | 0.032046 | 0.028457 | 0.047718 | 95.4455
355 | IE3 | 1000 | 0.0062149 | 0.0086762 | 0.0068954 | 0.0045015 | 0.0046568 | -0.0016856 | 0.016889 | 95.8 | 94.8046 |  | 0.0095376 | 0.025435 | 0.013124 | 0.01651 | 0.030895 | 0.027455 | 0.046148 | 95.5887
400 | IE3 | 1000 | 0.005572 | 0.0082917 | 0.0066402 | 0.0044745 | 0.004686 | -0.00028516 | 0.015344 | 95.8 | 94.8046 |  | 0.0090359 | 0.024531 | 0.012479 | 0.015924 | 0.029846 | 0.026488 | 0.044724 | 95.7191
500 | IE3 | 1000 | 0.0055069 | 0.0079318 | 0.0066232 | 0.0043754 | 0.0043871 | -0.0013955 | 0.015564 | 95.8 | 94.8046 |  | 0.0086132 | 0.023441 | 0.011958 | 0.015143 | 0.028582 | 0.025446 | 0.042993 | 95.8779
560 | IE3 | 1000 | 0.0054183 | 0.0078235 | 0.0071959 | 0.0042626 | 0.0041265 | -0.0016011 | 0.013759 | 95.8 | 94.8046 |  | 0.0083662 | 0.021305 | 0.011786 | 0.014559 | 0.026449 | 0.025174 | 0.040984 | 96.0629
630 | IE3 | 1000 | 0.0050939 | 0.0076236 | 0.0078636 | 0.0043428 | 0.0043891 | -0.00070314 | 0.01097 | 95.8 | 94.8046 |  | 0.0080861 | 0.019118 | 0.011586 | 0.01408 | 0.024407 | 0.025155 | 0.03958 | 96.1927
710 | IE3 | 1000 | 0.0051281 | 0.0076516 | 0.0083932 | 0.0043592 | 0.0043861 | -0.00070224 | 0.01064 | 95.8 | 94.8046 |  | 0.0081403 | 0.018867 | 0.011746 | 0.01418 | 0.024266 | 0.025668 | 0.039856 | 96.1672
800 | IE3 | 1000 | 0.0051649 | 0.0076774 | 0.0089207 | 0.0043634 | 0.0043823 | -0.00070904 | 0.010318 | 95.8 | 94.8046 |  | 0.0081947 | 0.018615 | 0.011906 | 0.014278 | 0.02412 | 0.026174 | 0.040117 | 96.143
900 | IE3 | 1000 | 0.0048617 | 0.0072878 | 0.0080324 | 0.0043586 | 0.0043771 | -0.00075467 | 0.010191 | 95.8 | 94.8046 |  | 0.0077192 | 0.017985 | 0.011167 | 0.013503 | 0.023224 | 0.024536 | 0.038354 | 96.3063
1000 | IE3 | 1000 | 0.0045446 | 0.0069009 | 0.0071448 | 0.0043455 | 0.0043665 | -0.00074228 | 0.010011 | 95.8 | 94.8046 |  | 0.0072414 | 0.017344 | 0.010425 | 0.012729 | 0.022314 | 0.0229 | 0.036571 | 96.4719
0.12 | IE3 | 750 | 0.45569 | 0.16382 | 0.1075 | 0.0041975 | 0.0055 | -0.41144 | 0.77541 | 50.7 | 47.2089 |  | 0.44905 | 0.86872 | 0.51029 | 0.55347 | 0.93191 | 0.71756 | 1.1007 | 47.604
0.18 | IE3 | 750 | 0.29404 | 0.089935 | 0.12372 | 0.0027767 | 0.0050532 | -0.37444 | 0.60215 | 58.7 | 55.2757 |  | 0.26834 | 0.55298 | 0.31413 | 0.33392 | 0.6003 | 0.47297 | 0.74324 | 57.3645
0.25 | IE3 | 750 | 0.17274 | 0.075441 | 0.091717 | 0.0039867 | 0.0072286 | -0.19506 | 0.45459 | 64.1 | 60.8246 |  | 0.17707 | 0.45831 | 0.21327 | 0.25046 | 0.49672 | 0.35882 | 0.61065 | 62.0868
0.37 | IE3 | 750 | 0.1114 | 0.055648 | 0.074278 | 0.0091835 | 0.012052 | -0.12219 | 0.31409 | 69.3 | 66.2492 |  | 0.11923 | 0.32491 | 0.14735 | 0.17713 | 0.3573 | 0.26407 | 0.45447 | 68.7538
0.55 | IE3 | 750 | 0.083543 | 0.051407 | 0.066732 | 0.011017 | 0.013945 | -0.095973 | 0.27408 | 73 | 70.1586 |  | 0.093929 | 0.2823 | 0.11963 | 0.14871 | 0.31303 | 0.22846 | 0.40475 | 71.187
0.75 | IE3 | 750 | 0.080328 | 0.039941 | 0.037367 | 0.0099848 | 0.015175 | -0.056036 | 0.2725 | 75 | 72.2892 |  | 0.095886 | 0.31256 | 0.11321 | 0.15194 | 0.33489 | 0.20403 | 0.39926 | 71.4664
1.1 | IE3 | 750 | 0.063144 | 0.035055 | 0.034559 | 0.0064876 | 0.0079673 | -0.040085 | 0.20175 | 77.7 | 75.1851 |  | 0.076789 | 0.23786 | 0.092227 | 0.12102 | 0.25622 | 0.16677 | 0.30888 | 76.401
1.5 | IE3 | 750 | 0.066653 | 0.034139 | 0.045123 | 0.0010006 | 0.0017645 | -0.025173 | 0.15137 | 79.7 | 77.3448 |  | 0.081197 | 0.20456 | 0.098229 | 0.12049 | 0.22214 | 0.17186 | 0.27487 | 78.4391
2.2 | IE3 | 750 | 0.064752 | 0.034137 | 0.03646 | 0.0020947 | 0.002831 | -0.031066 | 0.15019 | 81.9 | 79.7352 |  | 0.077229 | 0.19539 | 0.092665 | 0.11339 | 0.21181 | 0.15859 | 0.2594 | 79.4032
3 | IE3 | 750 | 0.047119 | 0.028337 | 0.030662 | 0.0062533 | 0.0066182 | -0.012706 | 0.12105 | 83.5 | 81.4833 |  | 0.060632 | 0.16644 | 0.073641 | 0.094058 | 0.18208 | 0.13325 | 0.22734 | 81.4773
4 | IE3 | 750 | 0.034423 | 0.025171 | 0.029471 | 0.013986 | 0.014308 | -0.013455 | 0.10378 | 84.8 | 82.9097 |  | 0.045955 | 0.13727 | 0.058159 | 0.076236 | 0.15527 | 0.11536 | 0.20768 | 82.8032
5.5 | IE3 | 750 | 0.031021 | 0.022507 | 0.03217 | 0.0029563 | 0.0033755 | -0.011507 | 0.094419 | 86.2 | 84.4518 |  | 0.041742 | 0.12252 | 0.053487 | 0.068749 | 0.13555 | 0.10513 | 0.17494 | 85.1106
7.5 | IE3 | 750 | 0.026284 | 0.016487 | 0.021353 | 0.0093258 | 0.0093258 | -0.016254 | 0.092175 | 87.3 | 85.668 |  | 0.03362 | 0.11058 | 0.042 | 0.056531 | 0.12278 | 0.083703 | 0.1587 | 86.3039
11 | IE3 | 750 | 0.017974 | 0.014354 | 0.016147 | 0.0066613 | 0.0068311 | -0.0081518 | 0.073681 | 88.6 | 87.1104 |  | 0.02527 | 0.090194 | 0.03207 | 0.044792 | 0.099756 | 0.066193 | 0.1275 | 88.692
15 | IE3 | 750 | 0.017686 | 0.014661 | 0.027673 | 0.006024 | 0.0063191 | -0.0053018 | 0.064479 | 89.6 | 88.2237 |  | 0.025904 | 0.084158 | 0.034926 | 0.046551 | 0.095703 | 0.076575 | 0.13154 | 88.3751
18.5 | IE3 | 750 | 0.016183 | 0.013016 | 0.026586 | 0.0056082 | 0.0057774 | -0.0059662 | 0.057099 | 90.1 | 88.7816 |  | 0.023286 | 0.073995 | 0.031681 | 0.041692 | 0.084719 | 0.069923 | 0.1183 | 89.4211
22 | IE3 | 750 | 0.01209 | 0.012225 | 0.020819 | 0.0066092 | 0.0067585 | -0.0045462 | 0.052261 | 90.6 | 89.3403 |  | 0.018707 | 0.066238 | 0.02585 | 0.035448 | 0.076117 | 0.059269 | 0.10622 | 90.3982
30 | IE3 | 750 | 0.011936 | 0.011757 | 0.026205 | 0.0074426 | 0.0076256 | -0.0018281 | 0.04474 | 91.3 | 90.1239 |  | 0.018998 | 0.061762 | 0.027056 | 0.036043 | 0.072905 | 0.063936 | 0.10788 | 90.2627
37 | IE3 | 750 | 0.010844 | 0.010041 | 0.02307 | 0.0073159 | 0.0076646 | -0.007322 | 0.049553 | 91.8 | 90.6846 |  | 0.016207 | 0.059335 | 0.023248 | 0.031753 | 0.069437 | 0.056428 | 0.10117 | 90.8128
45 | IE3 | 750 | 0.0088281 | 0.01244 | 0.021361 | 0.0044276 | 0.0048408 | -0.0032232 | 0.034497 | 92.2 | 91.1337 |  | 0.014712 | 0.045957 | 0.021953 | 0.028257 | 0.055086 | 0.051959 | 0.083171 | 92.3215
55 | IE3 | 750 | 0.0089792 | 0.01053 | 0.024343 | 0.005532 | 0.0053771 | -0.00051897 | 0.033724 | 92.5 | 91.471 |  | 0.015219 | 0.048057 | 0.022565 | 0.029529 | 0.057645 | 0.054751 | 0.087966 | 91.9146
75 | IE3 | 750 | 0.0091654 | 0.010679 | 0.029302 | 0.0025174 | 0.0028551 | -0.0016491 | 0.028762 | 93.1 | 92.1463 |  | 0.015102 | 0.041587 | 0.023339 | 0.028689 | 0.050915 | 0.056855 | 0.081631 | 92.453
90 | IE3 | 750 | 0.011798 | 0.014016 | 0.022737 | 0.0051765 | 0.0051758 | -0.00095723 | 0.027308 | 93.4 | 92.4844 |  | 0.018291 | 0.044692 | 0.0262 | 0.031809 | 0.054723 | 0.057487 | 0.085254 | 92.1443
110 | IE3 | 750 | 0.009414 | 0.011252 | 0.021579 | 0.0045051 | 0.0045367 | -0.0013916 | 0.021764 | 93.7 | 92.2471 |  | 0.014676 | 0.035358 | 0.021659 | 0.026027 | 0.044194 | 0.049251 | 0.071659 | 93.3132
132 | IE3 | 750 | 0.0089177 | 0.0099828 | 0.019962 | 0.0051459 | 0.0051891 | -0.0012972 | 0.021652 | 94 | 92.6108 |  | 0.013791 | 0.034627 | 0.02017 | 0.024632 | 0.043125 | 0.046211 | 0.069552 | 93.4971
160 | IE3 | 750 | 0.0082523 | 0.0085274 | 0.017966 | 0.0056725 | 0.0057339 | -0.0011911 | 0.021128 | 94.3 | 92.9751 |  | 0.012641 | 0.03322 | 0.018297 | 0.022761 | 0.041214 | 0.042284 | 0.066089 | 93.8008
200 | IE3 | 750 | 0.0081479 | 0.0086863 | 0.014247 | 0.006274 | 0.006816 | -0.0039484 | 0.02213 | 94.6 | 93.3399 |  | 0.011731 | 0.031386 | 0.016751 | 0.020822 | 0.039076 | 0.037912 | 0.062354 | 94.1306
250 | IE3 | 750 | 0.0079561 | 0.008059 | 0.017018 | 0.0055977 | 0.0056208 | -0.0012051 | 0.018147 | 94.6 | 93.3399 |  | 0.011977 | 0.029727 | 0.017336 | 0.021225 | 0.037386 | 0.039772 | 0.061193 | 94.2336
315 | IE3 | 750 | 0.0070505 | 0.0075813 | 0.013917 | 0.0055753 | 0.0055973 | -0.0012633 | 0.017809 | 94.6 | 93.3399 |  | 0.010722 | 0.028105 | 0.015379 | 0.019188 | 0.035053 | 0.035162 | 0.056267 | 94.6731
355 | IE3 | 750 | 0.0067207 | 0.0071945 | 0.013298 | 0.0055621 | 0.0055842 | -0.001255 | 0.016751 | 94.6 | 93.3399 |  | 0.010192 | 0.026586 | 0.014637 | 0.018247 | 0.033316 | 0.03356 | 0.053856 | 94.8896
400 | IE3 | 750 | 0.0063853 | 0.0068034 | 0.012671 | 0.0055607 | 0.0055884 | -0.001219 | 0.015675 | 94.6 | 93.3399 |  | 0.0096617 | 0.025073 | 0.013891 | 0.017308 | 0.031588 | 0.031956 | 0.051464 | 95.1055
500 | IE3 | 750 | 0.0060418 | 0.0064157 | 0.012054 | 0.0055469 | 0.0055751 | -0.0011432 | 0.014557 | 94.6 | 93.3399 |  | 0.0091315 | 0.023548 | 0.013148 | 0.016372 | 0.029844 | 0.030359 | 0.049047 | 95.3246
560 | IE3 | 750 | 0.0058845 | 0.0063332 | 0.01203 | 0.0054998 | 0.0056238 | -0.0010945 | 0.013511 | 94.6 | 93.3399 |  | 0.0088984 | 0.022363 | 0.012889 | 0.015928 | 0.028631 | 0.029859 | 0.047788 | 95.4391
630 | IE3 | 750 | 0.0056638 | 0.0062188 | 0.012099 | 0.0055014 | 0.0055798 | -0.00073559 | 0.012187 | 94.6 | 93.3399 |  | 0.0086603 | 0.02115 | 0.012635 | 0.015513 | 0.027395 | 0.029431 | 0.046514 | 95.5553
710 | IE3 | 750 | 0.0056681 | 0.0061337 | 0.013371 | 0.0055257 | 0.0055767 | -0.00062608 | 0.01068 | 94.6 | 93.3399 |  | 0.0086563 | 0.019822 | 0.012849 | 0.015474 | 0.026289 | 0.030306 | 0.04633 | 95.5722
800 | IE3 | 750 | 0.0056571 | 0.0060664 | 0.014625 | 0.0055031 | 0.0055989 | -0.00047202 | 0.0091522 | 94.6 | 93.3399 |  | 0.0086497 | 0.018494 | 0.01306 | 0.015437 | 0.025178 | 0.031176 | 0.046131 | 95.5903
900 | IE3 | 750 | 0.0054814 | 0.0057562 | 0.013141 | 0.0055202 | 0.0055704 | -0.0007086 | 0.010243 | 94.6 | 93.3399 |  | 0.0083128 | 0.019004 | 0.012367 | 0.014889 | 0.025332 | 0.029358 | 0.045003 | 95.6935
1000 | IE3 | 750 | 0.0052868 | 0.0054662 | 0.011631 | 0.0055291 | 0.0055542 | -0.00088279 | 0.011283 | 94.6 | 93.3399 |  | 0.0079729 | 0.019509 | 0.011672 | 0.014345 | 0.025481 | 0.027534 | 0.043867 | 95.7976
IE4
[10 empty] | 34-30-2 | 34-30-2 | Losses | PL7 | PL3 | PL6 | PL5 | PL2 | PL4 | PL1 | Eff / %
[10 empty] | Reference | Nominal | n= | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
Power / kW | Class | Speed | cL1 | cL2 | cL3 | cL4 | cL5 | cL6 | cL7 | % | % | T= | 0.25 | 1 | 0.25 | 0.5 | 1 | 0.5 | 1 | 1
0.12 | IE4 | 1500 | 0.20276 | 0.07289 | 0.047831 | 0.0018677 | 0.0024472 | -0.18307 | 0.34502 | 69.8 | 66.7751 |  | 0.19981 | 0.38654 | 0.22706 | 0.24627 | 0.41466 | 0.31928 | 0.48974 | 67.1257
0.18 | IE4 | 1500 | 0.15533 | 0.058498 | 0.038455 | 0.0012927 | 0.0018304 | -0.074192 | 0.19655 | 74.7 | 71.9688 |  | 0.16612 | 0.29516 | 0.188 | 0.20651 | 0.31766 | 0.26511 | 0.37777 | 72.5812
0.25 | IE4 | 1500 | 0.12071 | 0.051698 | 0.037363 | 0.0036765 | 0.0041858 | -0.061824 | 0.15383 | 77.9 | 75.4005 |  | 0.1302 | 0.22915 | 0.15024 | 0.16416 | 0.25079 | 0.21928 | 0.30964 | 76.3571
0.37 | IE4 | 1500 | 0.085084 | 0.038785 | 0.026136 | 0.0025221 | 0.0028308 | -0.026569 | 0.12683 | 81.1 | 78.8642 |  | 0.097749 | 0.19748 | 0.11242 | 0.12993 | 0.21324 | 0.16977 | 0.25562 | 79.642
0.55 | IE4 | 1500 | 0.072027 | 0.030578 | 0.020554 | 6.1616e-06 | 0.00026868 | -0.017093 | 0.10425 | 83.9 | 81.9216 |  | 0.083199 | 0.16813 | 0.094701 | 0.10999 | 0.17968 | 0.14074 | 0.21059 | 82.6042
0.75 | IE4 | 1500 | 0.055851 | 0.027124 | 0.017401 | 0.00099746 | 0.0012081 | -0.013625 | 0.099227 | 85.7 | 83.9003 |  | 0.066535 | 0.14965 | 0.076608 | 0.091957 | 0.16017 | 0.11892 | 0.18818 | 84.1621
1.1 | IE4 | 1500 | 0.044436 | 0.024568 | 0.017499 | 0.00056008 | 0.00084635 | -0.010401 | 0.090427 | 87.2 | 85.5573 |  | 0.054736 | 0.13189 | 0.064177 | 0.078624 | 0.14161 | 0.10426 | 0.16794 | 85.6211
1.5 | IE4 | 1500 | 0.038372 | 0.022387 | 0.014325 | 0.00074393 | 0.0010553 | -0.012092 | 0.089058 | 88.2 | 86.666 |  | 0.047423 | 0.12208 | 0.05573 | 0.069524 | 0.13075 | 0.091752 | 0.15385 | 86.6665
2.2 | IE4 | 1500 | 0.023293 | 0.019747 | 0.013344 | 0.0062218 | 0.0053209 | 0.010199 | 0.057554 | 89.5 | 88.1122 |  | 0.035329 | 0.098705 | 0.042927 | 0.057101 | 0.1087 | 0.078758 | 0.13568 | 88.053
3 | IE4 | 1500 | 0.024324 | 0.016501 | 0.0099922 | 0.0027656 | 0.0028839 | -0.0052368 | 0.069298 | 90.4 | 89.1167 |  | 0.03215 | 0.094007 | 0.038226 | 0.050304 | 0.10124 | 0.066935 | 0.12053 | 89.2436
4 | IE4 | 1500 | 0.022005 | 0.017372 | 0.012108 | 0.0026286 | 0.002962 | -0.0081862 | 0.062031 | 91.1 | 89.8998 |  | 0.028988 | 0.081792 | 0.035677 | 0.045646 | 0.089618 | 0.064297 | 0.11092 | 90.0154
5.5 | IE4 | 1500 | 0.018354 | 0.015422 | 0.011491 | 0.0045702 | 0.0048165 | -0.0059302 | 0.053384 | 91.9 | 90.7968 |  | 0.024872 | 0.071824 | 0.03101 | 0.040191 | 0.07988 | 0.057994 | 0.10211 | 90.7353
7.5 | IE4 | 1500 | 0.014894 | 0.01388 | 0.0095622 | 0.004236 | 0.0045139 | -0.010096 | 0.057537 | 92.6 | 91.5834 |  | 0.020118 | 0.067744 | 0.0255 | 0.034373 | 0.074913 | 0.04986 | 0.094528 | 91.3636
11 | IE4 | 1500 | 0.012628 | 0.012843 | 0.0093974 | 0.0036434 | 0.0037713 | -0.0057102 | 0.046042 | 93.3 | 92.3717 |  | 0.017948 | 0.057904 | 0.023022 | 0.030745 | 0.064495 | 0.045377 | 0.082615 | 92.3689
15 | IE4 | 1500 | 0.010354 | 0.011581 | 0.0087019 | 0.0038648 | 0.0039997 | -0.0048625 | 0.040557 | 93.9 | 93.0486 |  | 0.015188 | 0.050704 | 0.019822 | 0.026761 | 0.056947 | 0.040311 | 0.074196 | 93.0928
18.5 | IE4 | 1500 | 0.0095171 | 0.010877 | 0.0079246 | 0.0035471 | 0.0036555 | -0.0033877 | 0.040273 | 94.2 | 93.3875 |  | 0.014472 | 0.050733 | 0.018775 | 0.025983 | 0.05651 | 0.038494 | 0.072407 | 93.2481
22 | IE4 | 1500 | 0.0092159 | 0.010542 | 0.0080055 | 0.0016297 | 0.0017937 | -0.0035606 | 0.038343 | 94.5 | 93.7268 |  | 0.013891 | 0.047654 | 0.018074 | 0.02461 | 0.052534 | 0.036425 | 0.06597 | 93.8113
30 | IE4 | 1500 | 0.0066715 | 0.0090035 | 0.0055474 | 0.0042263 | 0.0059804 | 0.00021733 | 0.03094 | 94.9 | 94.1795 |  | 0.011347 | 0.041857 | 0.014774 | 0.021306 | 0.047325 | 0.031618 | 0.062586 | 94.11
37 | IE4 | 1500 | 0.014123 | 0.0019539 | 0.0093073 | 0.0057811 | -0.0016404 | -0.0051742 | 0.034082 | 95.2 | 94.5195 |  | 0.016114 | 0.045444 | 0.018419 | 0.023981 | 0.048816 | 0.032353 | 0.058433 | 94.4793
45 | IE4 | 1500 | 0.006812 | 0.0085399 | 0.0077473 | 0.0030369 | 0.0031018 | -0.0019152 | 0.029562 | 95.4 | 94.7463 |  | 0.01086 | 0.038031 | 0.014531 | 0.020025 | 0.042959 | 0.031067 | 0.056884 | 94.6177
55 | IE4 | 1500 | 0.0051404 | 0.0086188 | 0.0081154 | 0.0031663 | 0.0033142 | 0.00068029 | 0.021742 | 95.7 | 95.0867 |  | 0.0093936 | 0.031223 | 0.013158 | 0.017857 | 0.036312 | 0.02927 | 0.050777 | 95.1677
75 | IE4 | 1500 | 0.0053185 | 0.0083205 | 0.0081982 | 0.004483 | 0.0050573 | -0.0040793 | 0.02017 | 96 | 95.4274 |  | 0.0082416 | 0.025439 | 0.011988 | 0.015408 | 0.031125 | 0.027225 | 0.047469 | 95.4682
90 | IE4 | 1500 | 0.0048922 | 0.0085179 | 0.0075402 | 0.0041801 | 0.0041875 | -0.0014332 | 0.018144 | 96.1 | 95.5411 |  | 0.0083503 | 0.025511 | 0.012008 | 0.01564 | 0.030884 | 0.026862 | 0.046029 | 95.5996
110 | IE4 | 1500 | 0.0065933 | 0.010413 | 0.0084495 | 0.0040906 | 0.004121 | -0.0015965 | 0.015735 | 96.3 | 95.4174 |  | 0.010389 | 0.025143 | 0.014689 | 0.017817 | 0.031126 | 0.030644 | 0.047806 | 95.4375
132 | IE4 | 1500 | 0.0061056 | 0.0083565 | 0.0058136 | 0.0046717 | 0.0048245 | -0.0029483 | 0.019659 | 96.4 | 95.5401 |  | 0.0091415 | 0.026738 | 0.01245 | 0.016063 | 0.03199 | 0.02609 | 0.046482 | 95.5582
160 | IE4 | 1500 | 0.0056883 | 0.0086038 | 0.0054666 | 0.004854 | 0.0049742 | -0.0021996 | 0.016414 | 96.6 | 95.7858 |  | 0.0087522 | 0.02392 | 0.012062 | 0.015278 | 0.029242 | 0.025219 | 0.043801 | 95.8037
200 | IE4 | 1500 | 0.0054661 | 0.0081871 | 0.006151 | 0.0042601 | 0.0044016 | -0.0021921 | 0.016325 | 96.7 | 95.9088 |  | 0.0084534 | 0.02337 | 0.011772 | 0.01489 | 0.028461 | 0.024955 | 0.042599 | 95.9142
250 | IE4 | 1500 | 0.0052808 | 0.0076122 | 0.0058163 | 0.00391 | 0.0040625 | -0.0017613 | 0.014952 | 96.7 | 95.9088 |  | 0.0081185 | 0.02197 | 0.011221 | 0.014141 | 0.026702 | 0.02356 | 0.039873 | 96.1656
315 | IE4 | 1500 | 0.005117 | 0.0070405 | 0.005475 | 0.0035588 | 0.0037238 | -0.0014373 | 0.013666 | 96.7 | 95.9088 |  | 0.0077842 | 0.02057 | 0.01067 | 0.013381 | 0.024945 | 0.022151 | 0.037144 | 96.4187
355 | IE4 | 1500 | 0.0048377 | 0.0067536 | 0.0053674 | 0.003504 | 0.0036248 | -0.0013121 | 0.013147 | 96.7 | 95.9088 |  | 0.0074241 | 0.019798 | 0.010216 | 0.012851 | 0.024049 | 0.021371 | 0.035922 | 96.5324
400 | IE4 | 1500 | 0.0043373 | 0.0064543 | 0.0051688 | 0.003483 | 0.0036476 | -0.00022197 | 0.011944 | 96.7 | 95.9088 |  | 0.0070336 | 0.019095 | 0.0097135 | 0.012395 | 0.023232 | 0.020618 | 0.034813 | 96.6358
500 | IE4 | 1500 | 0.0042866 | 0.0061741 | 0.0051555 | 0.0034058 | 0.0034149 | -0.0010863 | 0.012115 | 96.7 | 95.9088 |  | 0.0067045 | 0.018246 | 0.0093079 | 0.011787 | 0.022248 | 0.019807 | 0.033466 | 96.7618
560 | IE4 | 1500 | 0.0042176 | 0.0060898 | 0.0056013 | 0.003318 | 0.0032121 | -0.0012463 | 0.01071 | 96.7 | 95.9088 |  | 0.0065123 | 0.016584 | 0.0091745 | 0.011333 | 0.020588 | 0.019595 | 0.031902 | 96.9084
630 | IE4 | 1500 | 0.0039651 | 0.0059342 | 0.006121 | 0.0033804 | 0.0034164 | -0.00054732 | 0.0085394 | 96.7 | 95.9088 |  | 0.0062942 | 0.014882 | 0.0090183 | 0.01096 | 0.018999 | 0.019581 | 0.030809 | 97.0112
710 | IE4 | 1500 | 0.0039918 | 0.005956 | 0.0065333 | 0.0033932 | 0.0034141 | -0.00054662 | 0.0082822 | 96.7 | 95.9088 |  | 0.0063364 | 0.014686 | 0.0091435 | 0.011038 | 0.018889 | 0.01998 | 0.031024 | 96.991
800 | IE4 | 1500 | 0.0040204 | 0.0059761 | 0.0069439 | 0.0033965 | 0.0034112 | -0.00055192 | 0.0080312 | 96.7 | 95.9088 |  | 0.0063788 | 0.01449 | 0.0092678 | 0.011114 | 0.018775 | 0.020374 | 0.031227 | 96.9718
900 | IE4 | 1500 | 0.0037844 | 0.0056728 | 0.0062524 | 0.0033927 | 0.0034072 | -0.00058744 | 0.0079327 | 96.7 | 95.9088 |  | 0.0060086 | 0.014 | 0.0086921 | 0.01051 | 0.018077 | 0.019099 | 0.029855 | 97.1011
1000 | IE4 | 1500 | 0.0035375 | 0.0053717 | 0.0055615 | 0.0033825 | 0.0033989 | -0.00057779 | 0.0077924 | 96.7 | 95.9088 |  | 0.0056367 | 0.013501 | 0.0081151 | 0.0099082 | 0.017369 | 0.017825 | 0.028467 | 97.2321
0.12 | IE4 | 3000 | 0.17994 | 0.064956 | 0.064467 | -0.00076943 | 0.0017223 | -0.2232 | 0.42011 | 66.5 | 63.3183 |  | 0.17066 | 0.39703 | 0.199 | 0.22198 | 0.42549 | 0.30303 | 0.50723 | 66.347
0.18 | IE4 | 3000 | 0.17236 | 0.052719 | 0.072525 | 0.0016277 | 0.0029621 | -0.21949 | 0.35297 | 70.8 | 67.8291 |  | 0.1573 | 0.32415 | 0.18414 | 0.19574 | 0.35189 | 0.27725 | 0.43568 | 69.6535
0.25 | IE4 | 3000 | 0.10668 | 0.046592 | 0.056645 | 0.0024622 | 0.0044644 | -0.12047 | 0.28076 | 74.3 | 71.5421 |  | 0.10936 | 0.28306 | 0.13172 | 0.15468 | 0.30678 | 0.22161 | 0.37714 | 72.6145
0.37 | IE4 | 3000 | 0.070516 | 0.035224 | 0.047016 | 0.0058129 | 0.0076285 | -0.077343 | 0.19881 | 78.1 | 75.616 |  | 0.075471 | 0.20566 | 0.093272 | 0.11212 | 0.22616 | 0.16715 | 0.28767 | 77.6599
0.55 | IE4 | 3000 | 0.051273 | 0.03155 | 0.040955 | 0.0067612 | 0.0085583 | -0.058901 | 0.16821 | 81.5 | 79.2994 |  | 0.057647 | 0.17325 | 0.073419 | 0.091268 | 0.19211 | 0.14021 | 0.24841 | 80.1022
0.75 | IE4 | 3000 | 0.047619 | 0.023678 | 0.022152 | 0.0059191 | 0.0089957 | -0.033219 | 0.16154 | 83.5 | 81.4833 |  | 0.056843 | 0.18529 | 0.067113 | 0.090074 | 0.19853 | 0.12095 | 0.23669 | 80.8612
1.1 | IE4 | 3000 | 0.038218 | 0.021217 | 0.020917 | 0.0039266 | 0.0048222 | -0.024261 | 0.12211 | 85.2 | 83.3496 |  | 0.046477 | 0.14396 | 0.055821 | 0.073246 | 0.15508 | 0.10094 | 0.18695 | 84.2493
1.5 | IE4 | 3000 | 0.040841 | 0.020918 | 0.027649 | 0.00061314 | 0.0010812 | -0.015425 | 0.09275 | 86.5 | 84.7831 |  | 0.049753 | 0.12534 | 0.060189 | 0.073832 | 0.13611 | 0.10531 | 0.16843 | 85.5851
2.2 | IE4 | 3000 | 0.039954 | 0.021063 | 0.022497 | 0.0012925 | 0.0017468 | -0.019169 | 0.09267 | 88 | 86.444 |  | 0.047652 | 0.12056 | 0.057177 | 0.069963 | 0.13069 | 0.097856 | 0.16005 | 86.2029
3 | IE4 | 3000 | 0.029171 | 0.017543 | 0.018982 | 0.0038713 | 0.0040972 | -0.0078661 | 0.074942 | 89.1 | 87.6667 |  | 0.037537 | 0.10304 | 0.04559 | 0.05823 | 0.11272 | 0.08249 | 0.14074 | 87.6624
4 | IE4 | 3000 | 0.021338 | 0.015603 | 0.018268 | 0.0086696 | 0.0088692 | -0.0083406 | 0.064332 | 90 | 88.67 |  | 0.028486 | 0.085094 | 0.036052 | 0.047257 | 0.09625 | 0.071507 | 0.12874 | 88.5944
5.5 | IE4 | 3000 | 0.019398 | 0.014074 | 0.020117 | 0.0018486 | 0.0021108 | -0.0071958 | 0.059043 | 90.9 | 89.6759 |  | 0.026103 | 0.076615 | 0.033446 | 0.04299 | 0.084764 | 0.065742 | 0.1094 | 90.1392
7.5 | IE4 | 3000 | 0.016354 | 0.010258 | 0.013285 | 0.0058024 | 0.0058024 | -0.010113 | 0.05735 | 91.7 | 90.5724 |  | 0.020918 | 0.068798 | 0.026132 | 0.035173 | 0.076392 | 0.052079 | 0.098738 | 91.0135
11 | IE4 | 3000 | 0.011164 | 0.0089153 | 0.010029 | 0.0041372 | 0.0042427 | -0.005063 | 0.045762 | 92.6 | 91.5834 |  | 0.015695 | 0.056018 | 0.019918 | 0.02782 | 0.061957 | 0.041111 | 0.079186 | 92.6624
15 | IE4 | 3000 | 0.010942 | 0.0090706 | 0.017121 | 0.0037269 | 0.0039095 | -0.0032801 | 0.039892 | 93.3 | 92.3717 |  | 0.016026 | 0.052067 | 0.021608 | 0.028801 | 0.05921 | 0.047375 | 0.081382 | 92.4743
18.5 | IE4 | 3000 | 0.0099028 | 0.0079649 | 0.016268 | 0.0034317 | 0.0035353 | -0.0036508 | 0.03494 | 93.7 | 92.8228 |  | 0.014249 | 0.045279 | 0.019386 | 0.025512 | 0.051841 | 0.042787 | 0.072392 | 93.2495
22 | IE4 | 3000 | 0.0074381 | 0.0075208 | 0.012808 | 0.004066 | 0.0041579 | -0.0027968 | 0.032152 | 94 | 93.1615 |  | 0.011509 | 0.04075 | 0.015903 | 0.021808 | 0.046828 | 0.036463 | 0.065346 | 93.8662
30 | IE4 | 3000 | 0.00729 | 0.0071812 | 0.016005 | 0.0045457 | 0.0046575 | -0.0011166 | 0.027326 | 94.5 | 93.7268 |  | 0.011604 | 0.037722 | 0.016525 | 0.022014 | 0.044528 | 0.03905 | 0.065889 | 93.8184
37 | IE4 | 3000 | 0.0066594 | 0.0061661 | 0.014167 | 0.0044926 | 0.0047067 | -0.0044963 | 0.030429 | 94.8 | 94.0663 |  | 0.0099527 | 0.036437 | 0.014276 | 0.019499 | 0.04264 | 0.034651 | 0.062124 | 94.1509
45 | IE4 | 3000 | 0.0054922 | 0.0077395 | 0.013289 | 0.0027545 | 0.0030116 | -0.0020052 | 0.021462 | 95 | 94.2928 |  | 0.0091525 | 0.028591 | 0.013657 | 0.01758 | 0.034271 | 0.032325 | 0.051744 | 95.0802
55 | IE4 | 3000 | 0.0054616 | 0.0064051 | 0.014807 | 0.0033649 | 0.0032707 | -0.00031567 | 0.020513 | 95.3 | 94.6328 |  | 0.0092568 | 0.029231 | 0.013725 | 0.017961 | 0.035063 | 0.033303 | 0.053506 | 94.9212
75 | IE4 | 3000 | 0.0056918 | 0.0066317 | 0.018196 | 0.0015633 | 0.0017731 | -0.0010241 | 0.017861 | 95.6 | 94.9732 |  | 0.0093786 | 0.025826 | 0.014494 | 0.017816 | 0.031619 | 0.035307 | 0.050693 | 95.1753
90 | IE4 | 3000 | 0.0073197 | 0.0086957 | 0.014106 | 0.0032116 | 0.0032112 | -0.00059389 | 0.016943 | 95.8 | 95.2002 |  | 0.011348 | 0.027728 | 0.016255 | 0.019735 | 0.033952 | 0.035666 | 0.052893 | 94.9764
110 | IE4 | 3000 | 0.005834 | 0.0069731 | 0.013373 | 0.0027918 | 0.0028114 | -0.0008624 | 0.013487 | 96 | 95.0495 |  | 0.009095 | 0.021912 | 0.013422 | 0.016129 | 0.027387 | 0.030521 | 0.044408 | 95.748
132 | IE4 | 3000 | 0.0055187 | 0.0061779 | 0.012353 | 0.0031845 | 0.0032112 | -0.00080274 | 0.013399 | 96.2 | 95.2947 |  | 0.0085344 | 0.021429 | 0.012482 | 0.015243 | 0.026688 | 0.028597 | 0.043042 | 95.8734
160 | IE4 | 3000 | 0.0052455 | 0.0054204 | 0.01142 | 0.0036057 | 0.0036447 | -0.00075711 | 0.01343 | 96.3 | 95.4174 |  | 0.008035 | 0.021116 | 0.01163 | 0.014468 | 0.026197 | 0.026877 | 0.042009 | 95.9685
200 | IE4 | 3000 | 0.005177 | 0.0055192 | 0.0090526 | 0.0039864 | 0.0043308 | -0.0025088 | 0.014061 | 96.5 | 95.6629 |  | 0.0074535 | 0.019942 | 0.010644 | 0.01323 | 0.024828 | 0.024089 | 0.039619 | 96.1891
250 | IE4 | 3000 | 0.0050552 | 0.0051206 | 0.010813 | 0.0035567 | 0.0035714 | -0.00076573 | 0.01153 | 96.5 | 95.6629 |  | 0.0076099 | 0.018888 | 0.011015 | 0.013486 | 0.023754 | 0.02527 | 0.038881 | 96.2574
315 | IE4 | 3000 | 0.0044798 | 0.0048171 | 0.0088424 | 0.0035425 | 0.0035565 | -0.00080268 | 0.011316 | 96.5 | 95.6629 |  | 0.0068125 | 0.017858 | 0.0097718 | 0.012192 | 0.022272 | 0.022342 | 0.035751 | 96.5483
355 | IE4 | 3000 | 0.0042702 | 0.0045713 | 0.0084497 | 0.0035341 | 0.0035481 | -0.00079744 | 0.010643 | 96.5 | 95.6629 |  | 0.0064761 | 0.016892 | 0.0093 | 0.011594 | 0.021168 | 0.021324 | 0.034219 | 96.6913
400 | IE4 | 3000 | 0.0040571 | 0.0043228 | 0.0080508 | 0.0035332 | 0.0035508 | -0.00077456 | 0.0099594 | 96.5 | 95.6629 |  | 0.0061389 | 0.015931 | 0.008826 | 0.010997 | 0.02007 | 0.020304 | 0.0327 | 96.8336
500 | IE4 | 3000 | 0.0038389 | 0.0040764 | 0.0076587 | 0.0035244 | 0.0035424 | -0.0007264 | 0.0092493 | 96.5 | 95.6629 |  | 0.0058021 | 0.014962 | 0.0083538 | 0.010403 | 0.018962 | 0.01929 | 0.031164 | 96.9778
560 | IE4 | 3000 | 0.0037389 | 0.0040241 | 0.0076438 | 0.0034945 | 0.0035733 | -0.00069544 | 0.008585 | 96.5 | 95.6629 |  | 0.0056539 | 0.014209 | 0.0081896 | 0.010121 | 0.018192 | 0.018972 | 0.030364 | 97.0531
630 | IE4 | 3000 | 0.0035987 | 0.0039513 | 0.0076875 | 0.0034955 | 0.0035453 | -0.00046738 | 0.0077435 | 96.5 | 95.6629 |  | 0.0055026 | 0.013439 | 0.008028 | 0.009857 | 0.017406 | 0.0187 | 0.029554 | 97.1294
710 | IE4 | 3000 | 0.0036014 | 0.0038973 | 0.0084958 | 0.003511 | 0.0035434 | -0.0003978 | 0.0067862 | 96.5 | 95.6629 |  | 0.0055001 | 0.012594 | 0.0081638 | 0.009832 | 0.016704 | 0.019256 | 0.029437 | 97.1405
800 | IE4 | 3000 | 0.0035945 | 0.0038545 | 0.0092927 | 0.0034966 | 0.0035575 | -0.00029992 | 0.0058152 | 96.5 | 95.6629 |  | 0.0054959 | 0.011751 | 0.0082982 | 0.0098082 | 0.015998 | 0.019809 | 0.029311 | 97.1524
900 | IE4 | 3000 | 0.0034828 | 0.0036574 | 0.0083496 | 0.0035075 | 0.0035393 | -0.00045024 | 0.0065081 | 96.5 | 95.6629 |  | 0.0052819 | 0.012075 | 0.007858 | 0.0094605 | 0.016095 | 0.018653 | 0.028595 | 97.22
1000 | IE4 | 3000 | 0.0033592 | 0.0034731 | 0.0073904 | 0.0035131 | 0.0035291 | -0.00056091 | 0.0071688 | 96.5 | 95.6629 |  | 0.0050658 | 0.012396 | 0.0074161 | 0.0091148 | 0.01619 | 0.017495 | 0.027873 | 97.2883
0.12 | IE4 | 1000 | 0.25345 | 0.091113 | 0.059789 | 0.0023346 | 0.0030591 | -0.22884 | 0.43127 | 64.9 | 61.6539 |  | 0.24976 | 0.48317 | 0.28382 | 0.30784 | 0.51832 | 0.3991 | 0.61218 | 62.0278
0.18 | IE4 | 1000 | 0.19562 | 0.073671 | 0.04843 | 0.001628 | 0.0023051 | -0.093435 | 0.24753 | 70.1 | 67.091 |  | 0.20921 | 0.37171 | 0.23676 | 0.26008 | 0.40005 | 0.33387 | 0.47575 | 67.7622
0.25 | IE4 | 1000 | 0.14872 | 0.063694 | 0.046033 | 0.0045296 | 0.005157 | -0.07617 | 0.18953 | 74.1 | 71.3289 |  | 0.16041 | 0.28233 | 0.1851 | 0.20226 | 0.30898 | 0.27016 | 0.38149 | 72.3858
0.37 | IE4 | 1000 | 0.10298 | 0.046941 | 0.031632 | 0.0030524 | 0.0034261 | -0.032156 | 0.1535 | 78 | 75.5082 |  | 0.1183 | 0.23901 | 0.13606 | 0.15725 | 0.25808 | 0.20547 | 0.30937 | 76.3725
0.55 | IE4 | 1000 | 0.088616 | 0.037622 | 0.025288 | 7.5808e-06 | 0.00033056 | -0.02103 | 0.12826 | 80.9 | 78.6468 |  | 0.10236 | 0.20686 | 0.11651 | 0.13532 | 0.22107 | 0.17316 | 0.2591 | 79.422
0.75 | IE4 | 1000 | 0.070019 | 0.034005 | 0.021815 | 0.0012505 | 0.0015146 | -0.017082 | 0.1244 | 82.7 | 80.6082 |  | 0.083413 | 0.18761 | 0.096042 | 0.11528 | 0.2008 | 0.14909 | 0.23592 | 80.9114
1.1 | IE4 | 1000 | 0.055529 | 0.030701 | 0.021867 | 0.0006999 | 0.0010576 | -0.012997 | 0.113 | 84.5 | 82.58 |  | 0.068399 | 0.16482 | 0.080198 | 0.098251 | 0.17696 | 0.13029 | 0.20986 | 82.6543
1.5 | IE4 | 1000 | 0.047079 | 0.027467 | 0.017575 | 0.00091274 | 0.0012948 | -0.014835 | 0.10927 | 85.9 | 84.1208 |  | 0.058184 | 0.14978 | 0.068375 | 0.0853 | 0.16042 | 0.11257 | 0.18876 | 84.1214
2.2 | IE4 | 1000 | 0.028624 | 0.024265 | 0.016398 | 0.0076455 | 0.0065385 | 0.012532 | 0.070724 | 87.4 | 85.7788 |  | 0.043413 | 0.12129 | 0.05275 | 0.070167 | 0.13357 | 0.09678 | 0.16673 | 85.7098
3 | IE4 | 1000 | 0.029472 | 0.019993 | 0.012107 | 0.0033509 | 0.0034943 | -0.006345 | 0.083964 | 88.6 | 87.1104 |  | 0.038954 | 0.1139 | 0.046315 | 0.06095 | 0.12266 | 0.081101 | 0.14603 | 87.2574
4 | IE4 | 1000 | 0.026425 | 0.020861 | 0.01454 | 0.0031566 | 0.003557 | -0.0098305 | 0.074491 | 89.5 | 88.1122 |  | 0.03481 | 0.098221 | 0.042843 | 0.054815 | 0.10762 | 0.077213 | 0.1332 | 88.2456
5.5 | IE4 | 1000 | 0.021859 | 0.018367 | 0.013686 | 0.0054431 | 0.0057364 | -0.0070628 | 0.063579 | 90.5 | 89.2285 |  | 0.029622 | 0.085542 | 0.036932 | 0.047866 | 0.095136 | 0.06907 | 0.12161 | 89.1578
7.5 | IE4 | 1000 | 0.01776 | 0.016551 | 0.011402 | 0.0050511 | 0.0053824 | -0.012039 | 0.068608 | 91.3 | 90.1239 |  | 0.023989 | 0.080779 | 0.030406 | 0.040987 | 0.089327 | 0.059454 | 0.11272 | 89.8702
11 | IE4 | 1000 | 0.01467 | 0.01492 | 0.010917 | 0.0042326 | 0.0043812 | -0.0066336 | 0.053487 | 92.3 | 91.2461 |  | 0.02085 | 0.067268 | 0.026744 | 0.035717 | 0.074924 | 0.052715 | 0.095974 | 91.243
15 | IE4 | 1000 | 0.012181 | 0.013625 | 0.010237 | 0.0045468 | 0.0047056 | -0.0057205 | 0.047714 | 92.9 | 91.921 |  | 0.017868 | 0.059652 | 0.02332 | 0.031483 | 0.066996 | 0.047425 | 0.087289 | 91.9718
18.5 | IE4 | 1000 | 0.010923 | 0.012484 | 0.0090949 | 0.0040709 | 0.0041953 | -0.003888 | 0.046221 | 93.4 | 92.4844 |  | 0.016609 | 0.058225 | 0.021548 | 0.029821 | 0.064855 | 0.044179 | 0.0831 | 92.3275
22 | IE4 | 1000 | 0.010646 | 0.012179 | 0.0092482 | 0.0018827 | 0.0020721 | -0.0041134 | 0.044296 | 93.7 | 92.8228 |  | 0.016047 | 0.055052 | 0.020879 | 0.02843 | 0.060689 | 0.042079 | 0.07621 | 92.9186
30 | IE4 | 1000 | 0.0076435 | 0.010315 | 0.0063557 | 0.0048421 | 0.0068518 | 0.00024899 | 0.035448 | 94.2 | 93.3875 |  | 0.013 | 0.047955 | 0.016926 | 0.02441 | 0.054221 | 0.036225 | 0.071705 | 93.3092
37 | IE4 | 1000 | 0.016303 | 0.0022555 | 0.010744 | 0.0066732 | -0.0018936 | -0.0059727 | 0.039342 | 94.5 | 93.7268 |  | 0.018601 | 0.052457 | 0.021261 | 0.027682 | 0.056349 | 0.037346 | 0.067451 | 93.6811
45 | IE4 | 1000 | 0.0077492 | 0.0097148 | 0.0088133 | 0.0034547 | 0.0035286 | -0.0021787 | 0.033629 | 94.8 | 94.0663 |  | 0.012354 | 0.043263 | 0.01653 | 0.02278 | 0.04887 | 0.035341 | 0.064711 | 93.9222
55 | IE4 | 1000 | 0.0058946 | 0.0098833 | 0.0093062 | 0.0036309 | 0.0038005 | 0.0007801 | 0.024932 | 95.1 | 94.4061 |  | 0.010772 | 0.035804 | 0.015089 | 0.020477 | 0.04164 | 0.033565 | 0.058227 | 94.4976
75 | IE4 | 1000 | 0.0061547 | 0.0096288 | 0.0094873 | 0.0051879 | 0.0058525 | -0.0047207 | 0.023342 | 95.4 | 94.7463 |  | 0.0095375 | 0.029439 | 0.013873 | 0.01783 | 0.036019 | 0.031506 | 0.054932 | 94.7928
90 | IE4 | 1000 | 0.0055482 | 0.0096602 | 0.0085514 | 0.0047407 | 0.004749 | -0.0016254 | 0.020577 | 95.6 | 94.9732 |  | 0.0094701 | 0.028932 | 0.013618 | 0.017737 | 0.035026 | 0.030464 | 0.052202 | 95.0388
110 | IE4 | 1000 | 0.0075234 | 0.011882 | 0.0096414 | 0.0046676 | 0.0047023 | -0.0018218 | 0.017954 | 95.8 | 94.8046 |  | 0.011854 | 0.02869 | 0.016761 | 0.02033 | 0.035517 | 0.034967 | 0.054549 | 94.8273
132 | IE4 | 1000 | 0.0068122 | 0.0093237 | 0.0064864 | 0.0052124 | 0.0053829 | -0.0032895 | 0.021934 | 96 | 95.0495 |  | 0.0102 | 0.029833 | 0.013891 | 0.017922 | 0.035692 | 0.02911 | 0.051862 | 95.0695
160 | IE4 | 1000 | 0.006384 | 0.009656 | 0.0061351 | 0.0054476 | 0.0055825 | -0.0024686 | 0.018421 | 96.2 | 95.2947 |  | 0.0098225 | 0.026845 | 0.013537 | 0.017147 | 0.032818 | 0.028304 | 0.049158 | 95.3145
200 | IE4 | 1000 | 0.0061541 | 0.0092176 | 0.0069252 | 0.0047963 | 0.0049557 | -0.002468 | 0.01838 | 96.3 | 95.4174 |  | 0.0095174 | 0.026312 | 0.013253 | 0.016764 | 0.032043 | 0.028096 | 0.047961 | 95.4234
250 | IE4 | 1000 | 0.0056125 | 0.0080903 | 0.0061816 | 0.0041556 | 0.0043176 | -0.0018719 | 0.015891 | 96.5 | 95.6629 |  | 0.0086284 | 0.023349 | 0.011926 | 0.015029 | 0.028379 | 0.025039 | 0.042377 | 95.9346
315 | IE4 | 1000 | 0.0052775 | 0.0072614 | 0.0056467 | 0.0036704 | 0.0038406 | -0.0014824 | 0.014095 | 96.6 | 95.7858 |  | 0.0080284 | 0.021216 | 0.011005 | 0.013801 | 0.025728 | 0.022846 | 0.038309 | 96.3105
355 | IE4 | 1000 | 0.0049894 | 0.0069654 | 0.0055358 | 0.0036139 | 0.0037385 | -0.0013533 | 0.013559 | 96.6 | 95.7858 |  | 0.0076569 | 0.02042 | 0.010537 | 0.013255 | 0.024803 | 0.022042 | 0.037049 | 96.4275
400 | IE4 | 1000 | 0.0044733 | 0.0066568 | 0.0053309 | 0.0035922 | 0.003762 | -0.00022894 | 0.012319 | 96.6 | 95.7858 |  | 0.0072542 | 0.019694 | 0.010018 | 0.012784 | 0.023961 | 0.021265 | 0.035905 | 96.534
500 | IE4 | 1000 | 0.004421 | 0.0063678 | 0.0053172 | 0.0035127 | 0.003522 | -0.0011204 | 0.012495 | 96.6 | 95.7858 |  | 0.0069148 | 0.018819 | 0.0095999 | 0.012157 | 0.022946 | 0.020428 | 0.034516 | 96.6636
560 | IE4 | 1000 | 0.0043499 | 0.0062808 | 0.005777 | 0.0034221 | 0.0033129 | -0.0012854 | 0.011046 | 96.6 | 95.7858 |  | 0.0067166 | 0.017104 | 0.0094623 | 0.011688 | 0.021234 | 0.02021 | 0.032903 | 96.8145
630 | IE4 | 1000 | 0.0040894 | 0.0061204 | 0.0063131 | 0.0034865 | 0.0035236 | -0.00056449 | 0.0088072 | 96.6 | 95.7858 |  | 0.0064917 | 0.015349 | 0.0093012 | 0.011304 | 0.019595 | 0.020195 | 0.031776 | 96.9203
710 | IE4 | 1000 | 0.004117 | 0.0061429 | 0.0067382 | 0.0034997 | 0.0035212 | -0.00056377 | 0.008542 | 96.6 | 95.7858 |  | 0.0065352 | 0.015147 | 0.0094303 | 0.011384 | 0.019481 | 0.020607 | 0.031997 | 96.8995
800 | IE4 | 1000 | 0.0041465 | 0.0061636 | 0.0071617 | 0.003503 | 0.0035182 | -0.00056923 | 0.0082831 | 96.6 | 95.7858 |  | 0.0065789 | 0.014945 | 0.0095586 | 0.011463 | 0.019364 | 0.021013 | 0.032207 | 96.8798
900 | IE4 | 1000 | 0.0039031 | 0.0058508 | 0.0064486 | 0.0034991 | 0.0035141 | -0.00060586 | 0.0081816 | 96.6 | 95.7858 |  | 0.0061971 | 0.014439 | 0.0089648 | 0.01084 | 0.018644 | 0.019698 | 0.030791 | 97.0128
1000 | IE4 | 1000 | 0.0036485 | 0.0055402 | 0.005736 | 0.0034886 | 0.0035055 | -0.00059592 | 0.0080368 | 96.6 | 95.7858 |  | 0.0058135 | 0.013924 | 0.0083697 | 0.010219 | 0.017914 | 0.018384 | 0.02936 | 97.1478
0.12 | IE4 | 750 | 0.28359 | 0.10195 | 0.066898 | 0.0026122 | 0.0034228 | -0.25605 | 0.48255 | 62.3 | 58.9655 |  | 0.27946 | 0.54062 | 0.31757 | 0.34444 | 0.57995 | 0.44655 | 0.68497 | 59.3483
0.18 | IE4 | 750 | 0.20398 | 0.062391 | 0.085831 | 0.0019263 | 0.0035056 | -0.25976 | 0.41773 | 67.2 | 64.0488 |  | 0.18616 | 0.38362 | 0.21792 | 0.23165 | 0.41645 | 0.32812 | 0.51561 | 65.98
0.25 | IE4 | 750 | 0.1272 | 0.055554 | 0.067541 | 0.0029358 | 0.0053232 | -0.14364 | 0.33476 | 70.8 | 67.8291 |  | 0.13039 | 0.3375 | 0.15705 | 0.18444 | 0.36579 | 0.26423 | 0.44968 | 68.9807
0.37 | IE4 | 750 | 0.086983 | 0.04345 | 0.057996 | 0.0071705 | 0.0094101 | -0.095406 | 0.24524 | 74.3 | 71.5421 |  | 0.093096 | 0.25369 | 0.11505 | 0.1383 | 0.27898 | 0.20618 | 0.35485 | 73.8091
0.55 | IE4 | 750 | 0.06747 | 0.041516 | 0.053893 | 0.0088971 | 0.011262 | -0.077508 | 0.22135 | 77 | 74.4321 |  | 0.075857 | 0.22798 | 0.096612 | 0.1201 | 0.2528 | 0.1845 | 0.32688 | 75.365
0.75 | IE4 | 750 | 0.066393 | 0.033013 | 0.030885 | 0.0082527 | 0.012542 | -0.046315 | 0.22523 | 78.4 | 75.9396 |  | 0.079253 | 0.25834 | 0.093573 | 0.12559 | 0.2768 | 0.16864 | 0.33 | 75.188
1.1 | IE4 | 750 | 0.05228 | 0.029024 | 0.028614 | 0.0053714 | 0.0065965 | -0.033188 | 0.16704 | 80.8 | 78.5381 |  | 0.063577 | 0.19693 | 0.07636 | 0.1002 | 0.21214 | 0.13808 | 0.25574 | 79.6343
1.5 | IE4 | 750 | 0.055125 | 0.028235 | 0.037319 | 0.00082758 | 0.0014593 | -0.020819 | 0.12519 | 82.6 | 80.499 |  | 0.067154 | 0.16918 | 0.08124 | 0.099654 | 0.18372 | 0.14214 | 0.22733 | 81.4774
2.2 | IE4 | 750 | 0.053744 | 0.028334 | 0.030262 | 0.0017386 | 0.0023497 | -0.025785 | 0.12466 | 84.5 | 82.58 |  | 0.0641 | 0.16217 | 0.076912 | 0.094112 | 0.1758 | 0.13163 | 0.2153 | 82.2842
3 | IE4 | 750 | 0.03914 | 0.023538 | 0.02547 | 0.0051944 | 0.0054975 | -0.010554 | 0.10056 | 85.9 | 84.1208 |  | 0.050366 | 0.13826 | 0.061171 | 0.078131 | 0.15125 | 0.11068 | 0.18884 | 84.1155
4 | IE4 | 750 | 0.028443 | 0.020798 | 0.024351 | 0.011556 | 0.011822 | -0.011118 | 0.085751 | 87.1 | 85.4466 |  | 0.037971 | 0.11343 | 0.048055 | 0.062992 | 0.1283 | 0.095315 | 0.1716 | 85.3531
5.5 | IE4 | 750 | 0.025675 | 0.018628 | 0.026626 | 0.0024468 | 0.0027938 | -0.0095241 | 0.078147 | 88.3 | 86.7771 |  | 0.034549 | 0.10141 | 0.044269 | 0.056901 | 0.11219 | 0.087014 | 0.14479 | 87.3521
7.5 | IE4 | 750 | 0.021649 | 0.013579 | 0.017587 | 0.0076812 | 0.0076812 | -0.013388 | 0.07592 | 89.3 | 87.8894 |  | 0.027691 | 0.091075 | 0.034594 | 0.046562 | 0.10113 | 0.068942 | 0.13071 | 88.44
11 | IE4 | 750 | 0.014835 | 0.011847 | 0.013327 | 0.0054979 | 0.005638 | -0.006728 | 0.060812 | 90.4 | 89.1167 |  | 0.020856 | 0.07444 | 0.026469 | 0.036969 | 0.082332 | 0.054632 | 0.10523 | 90.479
15 | IE4 | 750 | 0.014702 | 0.012188 | 0.023005 | 0.0050078 | 0.0052532 | -0.0044074 | 0.053602 | 91.2 | 90.0118 |  | 0.021534 | 0.069962 | 0.029034 | 0.038699 | 0.079559 | 0.063657 | 0.10935 | 90.1428
18.5 | IE4 | 750 | 0.013331 | 0.010722 | 0.0219 | 0.0046198 | 0.0047591 | -0.0049147 | 0.047036 | 91.7 | 90.5724 |  | 0.019182 | 0.060954 | 0.026097 | 0.034344 | 0.069788 | 0.0576 | 0.097453 | 91.12
22 | IE4 | 750 | 0.0099956 | 0.010107 | 0.017212 | 0.0054641 | 0.0055875 | -0.0037585 | 0.043206 | 92.1 | 91.0214 |  | 0.015466 | 0.054761 | 0.021371 | 0.029307 | 0.062929 | 0.049 | 0.087814 | 91.9275
30 | IE4 | 750 | 0.0098637 | 0.0097164 | 0.021656 | 0.0061506 | 0.0063018 | -0.0015108 | 0.036973 | 92.7 | 91.6959 |  | 0.0157 | 0.05104 | 0.02236 | 0.029786 | 0.060249 | 0.052837 | 0.089151 | 91.8147
37 | IE4 | 750 | 0.0089978 | 0.0083314 | 0.019141 | 0.0060701 | 0.0063594 | -0.0060752 | 0.041115 | 93.1 | 92.1463 |  | 0.013448 | 0.049231 | 0.019289 | 0.026346 | 0.057613 | 0.046819 | 0.08394 | 92.2561
45 | IE4 | 750 | 0.0073739 | 0.010391 | 0.017842 | 0.0036983 | 0.0040435 | -0.0026922 | 0.028815 | 93.4 | 92.4844 |  | 0.012288 | 0.038387 | 0.018337 | 0.023603 | 0.046013 | 0.0434 | 0.069472 | 93.5041
55 | IE4 | 750 | 0.0074459 | 0.0087321 | 0.020186 | 0.0045874 | 0.0044589 | -0.00043035 | 0.027965 | 93.7 | 92.8228 |  | 0.01262 | 0.039851 | 0.018712 | 0.024487 | 0.047802 | 0.045402 | 0.072945 | 93.2014
75 | IE4 | 750 | 0.0076143 | 0.0088717 | 0.024343 | 0.0020913 | 0.002372 | -0.00137 | 0.023894 | 94.2 | 93.3875 |  | 0.012546 | 0.034549 | 0.019389 | 0.023834 | 0.042299 | 0.047233 | 0.067816 | 93.6491
90 | IE4 | 750 | 0.0099043 | 0.011766 | 0.019087 | 0.0043456 | 0.0043451 | -0.00080359 | 0.022925 | 94.4 | 93.6136 |  | 0.015356 | 0.037519 | 0.021995 | 0.026704 | 0.04594 | 0.04826 | 0.07157 | 93.321
110 | IE4 | 750 | 0.0078361 | 0.0093662 | 0.017962 | 0.00375 | 0.0037763 | -0.0011584 | 0.018116 | 94.7 | 93.4616 |  | 0.012216 | 0.029431 | 0.018029 | 0.021664 | 0.036786 | 0.040996 | 0.059648 | 94.3709
132 | IE4 | 750 | 0.0075082 | 0.0084049 | 0.016807 | 0.0043325 | 0.0043689 | -0.0010921 | 0.01823 | 94.9 | 93.7053 |  | 0.011611 | 0.029154 | 0.016982 | 0.020738 | 0.036309 | 0.038906 | 0.058559 | 94.4681
160 | IE4 | 750 | 0.0070344 | 0.0072689 | 0.015315 | 0.0048353 | 0.0048877 | -0.0010153 | 0.01801 | 95.1 | 93.9491 |  | 0.010775 | 0.028317 | 0.015597 | 0.019402 | 0.035131 | 0.036043 | 0.056335 | 94.6669
200 | IE4 | 750 | 0.0068826 | 0.0073374 | 0.012035 | 0.0052997 | 0.0057576 | -0.0033352 | 0.018694 | 95.4 | 94.3154 |  | 0.0099089 | 0.026512 | 0.01415 | 0.017588 | 0.033008 | 0.032025 | 0.052671 | 94.9965
250 | IE4 | 750 | 0.0067206 | 0.0068075 | 0.014375 | 0.0047284 | 0.004748 | -0.001018 | 0.015329 | 95.4 | 94.3154 |  | 0.010117 | 0.02511 | 0.014644 | 0.017929 | 0.03158 | 0.033595 | 0.05169 | 95.085
315 | IE4 | 750 | 0.0059556 | 0.006404 | 0.011755 | 0.0047095 | 0.0047281 | -0.0010671 | 0.015043 | 95.4 | 94.3154 |  | 0.0090568 | 0.023741 | 0.012991 | 0.016208 | 0.02961 | 0.029702 | 0.047529 | 95.4628
355 | IE4 | 750 | 0.005677 | 0.0060772 | 0.011233 | 0.0046983 | 0.004717 | -0.0010601 | 0.01415 | 95.4 | 94.3154 |  | 0.0086095 | 0.022457 | 0.012364 | 0.015413 | 0.028142 | 0.028349 | 0.045492 | 95.6487
400 | IE4 | 750 | 0.0053937 | 0.0057469 | 0.010703 | 0.0046972 | 0.0047206 | -0.0010297 | 0.01324 | 95.4 | 94.3154 |  | 0.0081613 | 0.021179 | 0.011734 | 0.01462 | 0.026682 | 0.026993 | 0.043472 | 95.8339
500 | IE4 | 750 | 0.0051036 | 0.0054194 | 0.010182 | 0.0046855 | 0.0047094 | -0.0009657 | 0.012296 | 95.4 | 94.3154 |  | 0.0077135 | 0.019891 | 0.011106 | 0.01383 | 0.025209 | 0.025645 | 0.04143 | 96.0218
560 | IE4 | 750 | 0.0049707 | 0.0053497 | 0.010162 | 0.0046457 | 0.0047505 | -0.00092455 | 0.011413 | 95.4 | 94.3154 |  | 0.0075166 | 0.01889 | 0.010888 | 0.013455 | 0.024185 | 0.025222 | 0.040367 | 96.1199
630 | IE4 | 750 | 0.0047843 | 0.0052531 | 0.01022 | 0.004647 | 0.0047133 | -0.00062136 | 0.010295 | 95.4 | 94.3154 |  | 0.0073154 | 0.017866 | 0.010673 | 0.013104 | 0.023141 | 0.02486 | 0.039291 | 96.2195
710 | IE4 | 750 | 0.0047879 | 0.0051812 | 0.011295 | 0.0046676 | 0.0047107 | -0.00052885 | 0.0090219 | 95.4 | 94.3154 |  | 0.0073121 | 0.016743 | 0.010853 | 0.013071 | 0.022207 | 0.025599 | 0.039135 | 96.2339
800 | IE4 | 750 | 0.0047786 | 0.0051244 | 0.012354 | 0.0046485 | 0.0047295 | -0.00039872 | 0.007731 | 95.4 | 94.3154 |  | 0.0073065 | 0.015622 | 0.011032 | 0.013039 | 0.021268 | 0.026335 | 0.038967 | 96.2494
900 | IE4 | 750 | 0.0046302 | 0.0048623 | 0.0111 | 0.004663 | 0.0047053 | -0.00059856 | 0.0086522 | 95.4 | 94.3154 |  | 0.0070219 | 0.016053 | 0.010447 | 0.012577 | 0.021398 | 0.024799 | 0.038015 | 96.3377
1000 | IE4 | 750 | 0.0044658 | 0.0046173 | 0.0098251 | 0.0046705 | 0.0046917 | -0.0007457 | 0.0095304 | 95.4 | 94.3154 |  | 0.0067347 | 0.01648 | 0.0098592 | 0.012118 | 0.021524 | 0.023259 | 0.037055 | 96.4269
IE5
[10 empty] | 34-30-2 | 34-30-2 | Losses | PL7 | PL3 | PL6 | PL5 | PL2 | PL4 | PL1 | Eff / %
[10 empty] | Reference | Nominal | n= | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
Power / kW | Class | Speed | cL1 | cL2 | cL3 | cL4 | cL5 | cL6 | cL7 | % | % | T= | 0.25 | 1 | 0.25 | 0.5 | 1 | 0.5 | 1 | 1
0.12 | IE5 | 1500 | 0.1621 | 0.058272 | 0.038239 | 0.0014931 | 0.0019565 | -0.14636 | 0.27583 | 74.3 | 71.5421 |  | 0.15974 | 0.30902 | 0.18152 | 0.19688 | 0.3315 | 0.25525 | 0.39153 | 71.8635
0.18 | IE5 | 1500 | 0.12413 | 0.046747 | 0.03073 | 0.001033 | 0.0014627 | -0.059287 | 0.15706 | 78.7 | 76.2634 |  | 0.13275 | 0.23586 | 0.15023 | 0.16503 | 0.25384 | 0.21185 | 0.30188 | 76.8122
0.25 | IE5 | 1500 | 0.096581 | 0.041365 | 0.029895 | 0.0029417 | 0.0033491 | -0.049467 | 0.12308 | 81.5 | 79.2994 |  | 0.10418 | 0.18335 | 0.12021 | 0.13135 | 0.20066 | 0.17545 | 0.24775 | 80.1443
0.37 | IE5 | 1500 | 0.067996 | 0.030995 | 0.020887 | 0.0020155 | 0.0022623 | -0.021233 | 0.10136 | 84.3 | 82.3604 |  | 0.078117 | 0.15782 | 0.08984 | 0.10383 | 0.17041 | 0.13567 | 0.20428 | 83.0372
0.55 | IE5 | 1500 | 0.057579 | 0.024445 | 0.016431 | 4.9256e-06 | 0.00021478 | -0.013664 | 0.083339 | 86.7 | 85.0042 |  | 0.06651 | 0.13441 | 0.075705 | 0.087925 | 0.14364 | 0.11251 | 0.16835 | 85.5909
0.75 | IE5 | 1500 | 0.04478 | 0.021748 | 0.013952 | 0.00079975 | 0.00096867 | -0.010925 | 0.079559 | 88.2 | 86.666 |  | 0.053347 | 0.11998 | 0.061423 | 0.07373 | 0.12842 | 0.095349 | 0.15088 | 86.8899
1.1 | IE5 | 1500 | 0.035515 | 0.019636 | 0.013986 | 0.00044764 | 0.00067643 | -0.0083129 | 0.072272 | 89.5 | 88.1122 |  | 0.043746 | 0.10541 | 0.051292 | 0.062839 | 0.11318 | 0.083329 | 0.13422 | 88.1663
1.5 | IE5 | 1500 | 0.030458 | 0.01777 | 0.01137 | 0.0005905 | 0.00083768 | -0.0095978 | 0.07069 | 90.4 | 89.1167 |  | 0.037643 | 0.096904 | 0.044236 | 0.055186 | 0.10378 | 0.072829 | 0.12212 | 89.1171
2.2 | IE5 | 1500 | 0.018682 | 0.015837 | 0.010702 | 0.00499 | 0.0042675 | 0.0081794 | 0.046159 | 91.4 | 90.236 |  | 0.028334 | 0.079163 | 0.034428 | 0.045796 | 0.087177 | 0.063165 | 0.10882 | 90.1862
3 | IE5 | 1500 | 0.019647 | 0.013328 | 0.0080709 | 0.0022339 | 0.0023294 | -0.0042299 | 0.055974 | 92.1 | 91.0214 |  | 0.025968 | 0.075932 | 0.030876 | 0.040632 | 0.081773 | 0.054065 | 0.097354 | 91.1283
4 | IE5 | 1500 | 0.017476 | 0.013796 | 0.0096158 | 0.0020876 | 0.0023523 | -0.0065012 | 0.049263 | 92.8 | 91.8085 |  | 0.023021 | 0.064957 | 0.028333 | 0.036251 | 0.071172 | 0.051063 | 0.08809 | 91.9042
5.5 | IE5 | 1500 | 0.014715 | 0.012364 | 0.0092127 | 0.0036641 | 0.0038616 | -0.0047544 | 0.042799 | 93.4 | 92.4844 |  | 0.01994 | 0.057584 | 0.024861 | 0.032222 | 0.064042 | 0.046496 | 0.081862 | 92.4332
7.5 | IE5 | 1500 | 0.011897 | 0.011087 | 0.0076377 | 0.0033834 | 0.0036054 | -0.0080641 | 0.045957 | 94 | 93.1615 |  | 0.016069 | 0.05411 | 0.020368 | 0.027455 | 0.059835 | 0.039825 | 0.075503 | 92.9798
11 | IE5 | 1500 | 0.010038 | 0.010209 | 0.0074699 | 0.0028961 | 0.0029978 | -0.004539 | 0.036599 | 94.6 | 93.8399 |  | 0.014266 | 0.046028 | 0.0183 | 0.024439 | 0.051267 | 0.03607 | 0.06567 | 93.8377
15 | IE5 | 1500 | 0.0082121 | 0.0091855 | 0.0069019 | 0.0030654 | 0.0031724 | -0.0038566 | 0.032168 | 95.1 | 94.4061 |  | 0.012046 | 0.040216 | 0.015722 | 0.021225 | 0.045167 | 0.031973 | 0.058848 | 94.4422
18.5 | IE5 | 1500 | 0.0076231 | 0.0087128 | 0.0063476 | 0.0028412 | 0.002928 | -0.0027135 | 0.032259 | 95.3 | 94.6328 |  | 0.011592 | 0.040636 | 0.015039 | 0.020812 | 0.045264 | 0.030834 | 0.057998 | 94.5182
22 | IE5 | 1500 | 0.0074613 | 0.0085352 | 0.0064813 | 0.0013194 | 0.0014522 | -0.0028827 | 0.031043 | 95.5 | 94.8597 |  | 0.011246 | 0.038581 | 0.014633 | 0.019924 | 0.042533 | 0.02949 | 0.05341 | 94.9298
30 | IE5 | 1500 | 0.0053074 | 0.0071626 | 0.0044132 | 0.0033622 | 0.0047577 | 0.00017289 | 0.024614 | 95.9 | 95.3138 |  | 0.0090266 | 0.033299 | 0.011753 | 0.01695 | 0.037649 | 0.025153 | 0.04979 | 95.2572
37 | IE5 | 1500 | 0.011368 | 0.0015727 | 0.0074913 | 0.0046531 | -0.0013203 | -0.0041647 | 0.027432 | 96.1 | 95.5411 |  | 0.01297 | 0.036578 | 0.014825 | 0.019302 | 0.039291 | 0.026041 | 0.047032 | 95.508
45 | IE5 | 1500 | 0.005428 | 0.0068048 | 0.0061733 | 0.0024199 | 0.0024716 | -0.0015261 | 0.023556 | 96.3 | 95.7685 |  | 0.0086532 | 0.030304 | 0.011579 | 0.015957 | 0.034231 | 0.024755 | 0.045327 | 95.6638
55 | IE5 | 1500 | 0.0041493 | 0.0069571 | 0.0065508 | 0.0025559 | 0.0026752 | 0.00054913 | 0.01755 | 96.5 | 95.996 |  | 0.0075826 | 0.025203 | 0.010621 | 0.014414 | 0.029312 | 0.023627 | 0.040988 | 96.0626
75 | IE5 | 1500 | 0.004356 | 0.0068147 | 0.0067146 | 0.0036717 | 0.0041421 | -0.0033411 | 0.01652 | 96.7 | 96.2237 |  | 0.0067501 | 0.020835 | 0.0098187 | 0.012619 | 0.025492 | 0.022298 | 0.038878 | 96.2577
90 | IE5 | 1500 | 0.0038565 | 0.0067148 | 0.005944 | 0.0032952 | 0.003301 | -0.0011298 | 0.014303 | 96.9 | 96.4515 |  | 0.0065826 | 0.02011 | 0.009466 | 0.012329 | 0.024346 | 0.021175 | 0.036285 | 96.4985
110 | IE5 | 1500 | 0.0053074 | 0.0083821 | 0.0068015 | 0.0032927 | 0.0033172 | -0.0012852 | 0.012666 | 97 | 96.2779 |  | 0.0083627 | 0.020239 | 0.011824 | 0.014342 | 0.025055 | 0.024667 | 0.038482 | 96.2944
132 | IE5 | 1500 | 0.0048829 | 0.0066831 | 0.0046494 | 0.0037362 | 0.0038584 | -0.0023579 | 0.015722 | 97.1 | 96.4011 |  | 0.0073109 | 0.021384 | 0.009957 | 0.012847 | 0.025584 | 0.020866 | 0.037174 | 96.4158
160 | IE5 | 1500 | 0.0046556 | 0.0070418 | 0.0044741 | 0.0039727 | 0.0040711 | -0.0018002 | 0.013434 | 97.2 | 96.5243 |  | 0.0071632 | 0.019577 | 0.0098723 | 0.012504 | 0.023933 | 0.020641 | 0.035849 | 96.5392
200 | IE5 | 1500 | 0.0042757 | 0.0064041 | 0.0048114 | 0.0033323 | 0.003443 | -0.0017147 | 0.01277 | 97.4 | 96.771 |  | 0.0066124 | 0.018281 | 0.0092079 | 0.011647 | 0.022262 | 0.01952 | 0.033321 | 96.7753
250 | IE5 | 1500 | 0.0041307 | 0.0059544 | 0.0045496 | 0.0030585 | 0.0031777 | -0.0013777 | 0.011696 | 97.4 | 96.771 |  | 0.0063504 | 0.017185 | 0.0087771 | 0.011061 | 0.020887 | 0.018429 | 0.031189 | 96.9754
315 | IE5 | 1500 | 0.0040026 | 0.0055072 | 0.0042826 | 0.0027837 | 0.0029128 | -0.0011243 | 0.01069 | 97.4 | 96.771 |  | 0.0060889 | 0.016091 | 0.0083464 | 0.010467 | 0.019512 | 0.017327 | 0.029054 | 97.1766
355 | IE5 | 1500 | 0.0037841 | 0.0052827 | 0.0041985 | 0.0027409 | 0.0028354 | -0.0010264 | 0.010283 | 97.4 | 96.771 |  | 0.0058072 | 0.015487 | 0.0079912 | 0.010053 | 0.018811 | 0.016717 | 0.028099 | 97.2669
400 | IE5 | 1500 | 0.0033927 | 0.0050487 | 0.0040431 | 0.0027244 | 0.0028532 | -0.00017363 | 0.0093428 | 97.4 | 96.771 |  | 0.0055018 | 0.014936 | 0.007598 | 0.0096956 | 0.018172 | 0.016128 | 0.027231 | 97.3491
500 | IE5 | 1500 | 0.003353 | 0.0048295 | 0.0040327 | 0.0026641 | 0.0026712 | -0.00084971 | 0.0094767 | 97.4 | 96.771 |  | 0.0052444 | 0.014272 | 0.0072808 | 0.0092202 | 0.017403 | 0.015493 | 0.026178 | 97.449
560 | IE5 | 1500 | 0.0032991 | 0.0047635 | 0.0043814 | 0.0025954 | 0.0025126 | -0.00097488 | 0.0083773 | 97.4 | 96.771 |  | 0.005094 | 0.012972 | 0.0071764 | 0.0088645 | 0.016104 | 0.015328 | 0.024954 | 97.5653
630 | IE5 | 1500 | 0.0031015 | 0.0046419 | 0.004788 | 0.0026442 | 0.0026724 | -0.00042812 | 0.0066796 | 97.4 | 96.771 |  | 0.0049235 | 0.011641 | 0.0070543 | 0.0085729 | 0.014861 | 0.015316 | 0.024099 | 97.6468
710 | IE5 | 1500 | 0.0031224 | 0.0046589 | 0.0051105 | 0.0026542 | 0.0026706 | -0.00042758 | 0.0064784 | 97.4 | 96.771 |  | 0.0049565 | 0.011488 | 0.0071522 | 0.008634 | 0.014775 | 0.015629 | 0.024267 | 97.6307
800 | IE5 | 1500 | 0.0031448 | 0.0046746 | 0.0054316 | 0.0026568 | 0.0026683 | -0.00043172 | 0.0062821 | 97.4 | 96.771 |  | 0.0049896 | 0.011334 | 0.0072494 | 0.0086936 | 0.014686 | 0.015937 | 0.024427 | 97.6156
900 | IE5 | 1500 | 0.0029602 | 0.0044374 | 0.0048908 | 0.0026538 | 0.0026651 | -0.0004595 | 0.0062051 | 97.4 | 96.771 |  | 0.0047 | 0.010951 | 0.0067991 | 0.0082214 | 0.01414 | 0.01494 | 0.023353 | 97.718
1000 | IE5 | 1500 | 0.0027671 | 0.0042018 | 0.0043503 | 0.0026459 | 0.0026587 | -0.00045196 | 0.0060953 | 97.4 | 96.771 |  | 0.0044091 | 0.01056 | 0.0063478 | 0.0077503 | 0.013587 | 0.013943 | 0.022267 | 97.8218
0.12 | IE5 | 3000 | 0.14308 | 0.05165 | 0.05126 | -0.00061181 | 0.0013695 | -0.17747 | 0.33405 | 71.4 | 68.4629 |  | 0.1357 | 0.3157 | 0.15823 | 0.1765 | 0.33833 | 0.24095 | 0.40332 | 71.2597
0.18 | IE5 | 3000 | 0.13782 | 0.042155 | 0.057992 | 0.0013015 | 0.0023686 | -0.17551 | 0.28225 | 75.2 | 72.5029 |  | 0.12578 | 0.2592 | 0.14724 | 0.15652 | 0.28138 | 0.2217 | 0.34838 | 74.1632
0.25 | IE5 | 3000 | 0.085478 | 0.037331 | 0.045385 | 0.0019728 | 0.003577 | -0.096523 | 0.22495 | 78.3 | 75.8317 |  | 0.08762 | 0.22679 | 0.10554 | 0.12394 | 0.2458 | 0.17756 | 0.30217 | 76.7949
0.37 | IE5 | 3000 | 0.056328 | 0.028137 | 0.037556 | 0.0046434 | 0.0060937 | -0.061782 | 0.15881 | 81.7 | 79.5173 |  | 0.060286 | 0.16428 | 0.074506 | 0.089558 | 0.18066 | 0.13352 | 0.22979 | 81.3149
0.55 | IE5 | 3000 | 0.041117 | 0.025301 | 0.032843 | 0.005422 | 0.0068632 | -0.047234 | 0.13489 | 84.6 | 82.6899 |  | 0.046229 | 0.13894 | 0.058877 | 0.073191 | 0.15406 | 0.11244 | 0.1992 | 83.3887
0.75 | IE5 | 3000 | 0.038256 | 0.019022 | 0.017796 | 0.0047552 | 0.0072268 | -0.026687 | 0.12978 | 86.3 | 84.5622 |  | 0.045665 | 0.14885 | 0.053917 | 0.072363 | 0.15949 | 0.09717 | 0.19015 | 84.0233
1.1 | IE5 | 3000 | 0.030571 | 0.016972 | 0.016732 | 0.003141 | 0.0038574 | -0.019407 | 0.09768 | 87.8 | 86.2221 |  | 0.037177 | 0.11516 | 0.044652 | 0.05859 | 0.12405 | 0.080741 | 0.14955 | 86.9908
1.5 | IE5 | 3000 | 0.032674 | 0.016735 | 0.02212 | 0.00049053 | 0.00086499 | -0.01234 | 0.074202 | 88.9 | 87.4441 |  | 0.039804 | 0.10028 | 0.048153 | 0.059067 | 0.10889 | 0.084248 | 0.13475 | 88.1254
2.2 | IE5 | 3000 | 0.031833 | 0.016782 | 0.017924 | 0.0010298 | 0.0013917 | -0.015272 | 0.073835 | 90.2 | 88.8933 |  | 0.037967 | 0.096055 | 0.045555 | 0.055743 | 0.10413 | 0.077967 | 0.12752 | 88.69
3 | IE5 | 3000 | 0.023295 | 0.014009 | 0.015159 | 0.0030916 | 0.003272 | -0.0062818 | 0.059848 | 91.1 | 89.8998 |  | 0.029976 | 0.082289 | 0.036408 | 0.046502 | 0.09002 | 0.065876 | 0.11239 | 89.8962
4 | IE5 | 3000 | 0.017154 | 0.012543 | 0.014686 | 0.0069697 | 0.0071302 | -0.0067052 | 0.051718 | 91.8 | 90.6846 |  | 0.022901 | 0.068409 | 0.028983 | 0.037991 | 0.077377 | 0.057486 | 0.1035 | 90.621
5.5 | IE5 | 3000 | 0.015485 | 0.011235 | 0.016058 | 0.0014757 | 0.001685 | -0.0057441 | 0.047131 | 92.6 | 91.5834 |  | 0.020837 | 0.061159 | 0.026699 | 0.034317 | 0.067663 | 0.052479 | 0.087326 | 91.9688
7.5 | IE5 | 3000 | 0.012975 | 0.0081384 | 0.01054 | 0.0046035 | 0.0046035 | -0.0080236 | 0.0455 | 93.3 | 92.3717 |  | 0.016596 | 0.054584 | 0.020733 | 0.027906 | 0.060609 | 0.041319 | 0.078337 | 92.7354
11 | IE5 | 3000 | 0.0089167 | 0.007121 | 0.0080102 | 0.0033046 | 0.0033888 | -0.004044 | 0.036552 | 94 | 93.1615 |  | 0.012536 | 0.044743 | 0.015909 | 0.022221 | 0.049487 | 0.032837 | 0.063249 | 94.0514
15 | IE5 | 3000 | 0.0088681 | 0.0073515 | 0.013876 | 0.0030206 | 0.0031686 | -0.0026585 | 0.032331 | 94.5 | 93.7268 |  | 0.012989 | 0.042199 | 0.017513 | 0.023342 | 0.047988 | 0.038396 | 0.065957 | 93.8124
18.5 | IE5 | 3000 | 0.0079152 | 0.0063663 | 0.013003 | 0.002743 | 0.0028257 | -0.002918 | 0.027927 | 94.9 | 94.1795 |  | 0.011389 | 0.036191 | 0.015495 | 0.020391 | 0.041436 | 0.034199 | 0.057862 | 94.5303
22 | IE5 | 3000 | 0.0060042 | 0.006071 | 0.010339 | 0.0032822 | 0.0033563 | -0.0022577 | 0.025953 | 95.1 | 94.4061 |  | 0.0092902 | 0.032894 | 0.012837 | 0.017604 | 0.0378 | 0.029433 | 0.052749 | 94.9894
30 | IE5 | 3000 | 0.0059021 | 0.005814 | 0.012958 | 0.0036803 | 0.0037708 | -0.00090398 | 0.022123 | 95.5 | 94.8597 |  | 0.0093944 | 0.030541 | 0.013379 | 0.017823 | 0.036051 | 0.031616 | 0.053345 | 94.9357
37 | IE5 | 3000 | 0.0053226 | 0.0049283 | 0.011323 | 0.0035907 | 0.0037619 | -0.0035937 | 0.024321 | 95.8 | 95.2002 |  | 0.0079548 | 0.029122 | 0.01141 | 0.015585 | 0.034081 | 0.027695 | 0.049654 | 95.2695
45 | IE5 | 3000 | 0.004348 | 0.0061271 | 0.010521 | 0.0021807 | 0.0023842 | -0.0015875 | 0.016991 | 96 | 95.4274 |  | 0.0072457 | 0.022635 | 0.010812 | 0.013917 | 0.027131 | 0.025591 | 0.040964 | 96.0648
55 | IE5 | 3000 | 0.0043745 | 0.0051301 | 0.011859 | 0.0026951 | 0.0026196 | -0.00025283 | 0.01643 | 96.2 | 95.6548 |  | 0.0074142 | 0.023412 | 0.010993 | 0.014386 | 0.028084 | 0.026674 | 0.042855 | 95.8906
75 | IE5 | 3000 | 0.0044853 | 0.005226 | 0.014339 | 0.0012319 | 0.0013972 | -0.00080702 | 0.014075 | 96.5 | 95.996 |  | 0.0073907 | 0.020351 | 0.011421 | 0.01404 | 0.024917 | 0.027823 | 0.039948 | 96.1586
90 | IE5 | 3000 | 0.0058764 | 0.0069811 | 0.011325 | 0.0025783 | 0.002578 | -0.00047678 | 0.013602 | 96.6 | 96.1098 |  | 0.0091107 | 0.02226 | 0.01305 | 0.015844 | 0.027257 | 0.028633 | 0.042464 | 95.9266
110 | IE5 | 3000 | 0.0046286 | 0.0055324 | 0.01061 | 0.002215 | 0.0022306 | -0.00068422 | 0.010701 | 96.8 | 96.0317 |  | 0.0072159 | 0.017384 | 0.010649 | 0.012797 | 0.021729 | 0.024215 | 0.035233 | 96.5966
132 | IE5 | 3000 | 0.0044696 | 0.0050034 | 0.010005 | 0.0025791 | 0.0026008 | -0.00065014 | 0.010852 | 96.9 | 96.1548 |  | 0.006912 | 0.017355 | 0.01011 | 0.012345 | 0.021614 | 0.023161 | 0.03486 | 96.6314
160 | IE5 | 3000 | 0.0042224 | 0.0043632 | 0.0091927 | 0.0029024 | 0.0029338 | -0.00060944 | 0.01081 | 97 | 96.2779 |  | 0.0064678 | 0.016998 | 0.009362 | 0.011646 | 0.021088 | 0.021635 | 0.033815 | 96.7291
200 | IE5 | 3000 | 0.0041118 | 0.0043835 | 0.0071899 | 0.0031662 | 0.0034397 | -0.0019925 | 0.011168 | 97.2 | 96.5243 |  | 0.0059198 | 0.015839 | 0.0084536 | 0.010508 | 0.01972 | 0.019132 | 0.031467 | 96.9493
250 | IE5 | 3000 | 0.0040151 | 0.0040669 | 0.008588 | 0.0028249 | 0.0028365 | -0.00060817 | 0.0091577 | 97.2 | 96.5243 |  | 0.0060441 | 0.015002 | 0.0087484 | 0.010711 | 0.018867 | 0.020071 | 0.030881 | 97.0044
315 | IE5 | 3000 | 0.003558 | 0.0038259 | 0.007023 | 0.0028136 | 0.0028247 | -0.00063752 | 0.0089873 | 97.2 | 96.5243 |  | 0.0054108 | 0.014183 | 0.0077611 | 0.009683 | 0.017689 | 0.017745 | 0.028395 | 97.2389
355 | IE5 | 3000 | 0.0033916 | 0.0036307 | 0.0067111 | 0.0028069 | 0.002818 | -0.00063336 | 0.0084534 | 97.2 | 96.5243 |  | 0.0051435 | 0.013417 | 0.0073864 | 0.0092083 | 0.016813 | 0.016936 | 0.027178 | 97.3541
400 | IE5 | 3000 | 0.0032223 | 0.0034333 | 0.0063942 | 0.0028062 | 0.0028202 | -0.00061519 | 0.0079102 | 97.2 | 96.5243 |  | 0.0048758 | 0.012653 | 0.0070099 | 0.0087346 | 0.015941 | 0.016126 | 0.025971 | 97.4686
500 | IE5 | 3000 | 0.003049 | 0.0032377 | 0.0060828 | 0.0027992 | 0.0028135 | -0.00057693 | 0.0073461 | 97.2 | 96.5243 |  | 0.0046082 | 0.011883 | 0.0066349 | 0.0082624 | 0.015061 | 0.015321 | 0.024751 | 97.5846
560 | IE5 | 3000 | 0.0029696 | 0.0031961 | 0.006071 | 0.0027755 | 0.002838 | -0.00055235 | 0.0068185 | 97.2 | 96.5243 |  | 0.0044906 | 0.011286 | 0.0065045 | 0.0080382 | 0.014449 | 0.015068 | 0.024116 | 97.6452
630 | IE5 | 3000 | 0.0028582 | 0.0031383 | 0.0061057 | 0.0027763 | 0.0028158 | -0.00037121 | 0.0061502 | 97.2 | 96.5243 |  | 0.0043704 | 0.010673 | 0.0063762 | 0.0078288 | 0.013825 | 0.014852 | 0.023473 | 97.7065
710 | IE5 | 3000 | 0.0028604 | 0.0030954 | 0.0067477 | 0.0027885 | 0.0028143 | -0.00031595 | 0.0053899 | 97.2 | 96.5243 |  | 0.0043684 | 0.010003 | 0.006484 | 0.0078089 | 0.013267 | 0.015294 | 0.02338 | 97.7154
800 | IE5 | 3000 | 0.0028549 | 0.0030614 | 0.0073806 | 0.0027771 | 0.0028255 | -0.0002382 | 0.0046187 | 97.2 | 96.5243 |  | 0.0043651 | 0.0093328 | 0.0065908 | 0.00779 | 0.012706 | 0.015733 | 0.02328 | 97.725
900 | IE5 | 3000 | 0.0027662 | 0.0029048 | 0.0066316 | 0.0027858 | 0.0028111 | -0.00035759 | 0.005169 | 97.2 | 96.5243 |  | 0.0041951 | 0.0095904 | 0.0062412 | 0.0075139 | 0.012784 | 0.014815 | 0.022711 | 97.7793
1000 | IE5 | 3000 | 0.002668 | 0.0027585 | 0.0058697 | 0.0027903 | 0.0028029 | -0.0004455 | 0.0056937 | 97.2 | 96.5243 |  | 0.0040235 | 0.0098454 | 0.0058901 | 0.0072393 | 0.012859 | 0.013895 | 0.022138 | 97.8342
0.12 | IE5 | 1000 | 0.20276 | 0.07289 | 0.047831 | 0.0018677 | 0.0024472 | -0.18307 | 0.34502 | 69.8 | 66.7751 |  | 0.19981 | 0.38654 | 0.22706 | 0.24627 | 0.41466 | 0.31928 | 0.48974 | 67.1257
0.18 | IE5 | 1000 | 0.15615 | 0.058808 | 0.038659 | 0.0012995 | 0.0018401 | -0.074585 | 0.19759 | 74.6 | 71.8621 |  | 0.167 | 0.29672 | 0.189 | 0.20761 | 0.31934 | 0.26651 | 0.37977 | 72.4759
0.25 | IE5 | 1000 | 0.11931 | 0.051099 | 0.03693 | 0.0036339 | 0.0041373 | -0.061108 | 0.15205 | 78.1 | 75.616 |  | 0.12869 | 0.2265 | 0.14849 | 0.16226 | 0.24788 | 0.21674 | 0.30605 | 76.5668
0.37 | IE5 | 1000 | 0.082326 | 0.037527 | 0.025289 | 0.0024403 | 0.002739 | -0.025708 | 0.12272 | 81.6 | 79.4083 |  | 0.09458 | 0.19108 | 0.10877 | 0.12571 | 0.20633 | 0.16426 | 0.24733 | 80.1711
0.55 | IE5 | 1000 | 0.070433 | 0.029902 | 0.020099 | 6.0252e-06 | 0.00026273 | -0.016715 | 0.10194 | 84.2 | 82.2507 |  | 0.081358 | 0.16441 | 0.092605 | 0.10755 | 0.17571 | 0.13763 | 0.20593 | 82.9235
0.75 | IE5 | 1000 | 0.055851 | 0.027124 | 0.017401 | 0.00099746 | 0.0012081 | -0.013625 | 0.099227 | 85.7 | 83.9003 |  | 0.066535 | 0.14965 | 0.076608 | 0.091957 | 0.16017 | 0.11892 | 0.18818 | 84.1621
1.1 | IE5 | 1000 | 0.044436 | 0.024568 | 0.017499 | 0.00056008 | 0.00084635 | -0.010401 | 0.090427 | 87.2 | 85.5573 |  | 0.054736 | 0.13189 | 0.064177 | 0.078624 | 0.14161 | 0.10426 | 0.16794 | 85.6211
1.5 | IE5 | 1000 | 0.037637 | 0.021958 | 0.01405 | 0.00072967 | 0.0010351 | -0.01186 | 0.08735 | 88.4 | 86.8881 |  | 0.046514 | 0.11974 | 0.054661 | 0.068191 | 0.12824 | 0.089993 | 0.1509 | 86.8886
2.2 | IE5 | 1000 | 0.022799 | 0.019327 | 0.013061 | 0.0060897 | 0.0052079 | 0.0099819 | 0.056332 | 89.7 | 88.3352 |  | 0.034579 | 0.096609 | 0.042016 | 0.055888 | 0.10639 | 0.077085 | 0.1328 | 88.277
3 | IE5 | 1000 | 0.023765 | 0.016121 | 0.0097624 | 0.002702 | 0.0028176 | -0.0051164 | 0.067705 | 90.6 | 89.3403 |  | 0.031411 | 0.091845 | 0.037347 | 0.049148 | 0.09891 | 0.065396 | 0.11776 | 89.4649
4 | IE5 | 1000 | 0.021193 | 0.016731 | 0.011661 | 0.0025317 | 0.0028528 | -0.0078843 | 0.059743 | 91.4 | 90.236 |  | 0.027919 | 0.078776 | 0.034361 | 0.043963 | 0.086313 | 0.061926 | 0.10683 | 90.3481
5.5 | IE5 | 1000 | 0.017617 | 0.014802 | 0.011029 | 0.0043866 | 0.0046231 | -0.005692 | 0.051239 | 92.2 | 91.1337 |  | 0.023873 | 0.068939 | 0.029764 | 0.038576 | 0.076671 | 0.055664 | 0.098005 | 91.0743
7.5 | IE5 | 1000 | 0.014244 | 0.013274 | 0.009145 | 0.0040511 | 0.0043169 | -0.0096555 | 0.055026 | 92.9 | 91.921 |  | 0.01924 | 0.064788 | 0.024387 | 0.032873 | 0.071643 | 0.047685 | 0.090403 | 91.7092
11 | IE5 | 1000 | 0.011823 | 0.012025 | 0.0087986 | 0.0034113 | 0.003531 | -0.0053464 | 0.043108 | 93.7 | 92.8228 |  | 0.016804 | 0.054215 | 0.021555 | 0.028786 | 0.060386 | 0.042486 | 0.077351 | 92.8203
15 | IE5 | 1000 | 0.0096339 | 0.010776 | 0.0080968 | 0.0035961 | 0.0037216 | -0.0045243 | 0.037737 | 94.3 | 93.5006 |  | 0.014132 | 0.047178 | 0.018444 | 0.0249 | 0.052987 | 0.037508 | 0.069037 | 93.5421
18.5 | IE5 | 1000 | 0.0088233 | 0.010084 | 0.0073469 | 0.0032885 | 0.003389 | -0.0031407 | 0.037337 | 94.6 | 93.8399 |  | 0.013417 | 0.047034 | 0.017406 | 0.024089 | 0.05239 | 0.035688 | 0.067129 | 93.7094
22 | IE5 | 1000 | 0.0085096 | 0.0097344 | 0.007392 | 0.0015048 | 0.0016562 | -0.0032878 | 0.035405 | 94.9 | 94.1795 |  | 0.012826 | 0.044002 | 0.016689 | 0.022724 | 0.048508 | 0.033634 | 0.060914 | 94.2583
30 | IE5 | 1000 | 0.0061224 | 0.0082625 | 0.0050909 | 0.0038784 | 0.0054882 | 0.00019944 | 0.028394 | 95.3 | 94.6328 |  | 0.010413 | 0.038412 | 0.013558 | 0.019552 | 0.043431 | 0.029016 | 0.057435 | 94.5684
37 | IE5 | 1000 | 0.012892 | 0.0017836 | 0.008496 | 0.0052772 | -0.0014974 | -0.0047232 | 0.031111 | 95.6 | 94.9732 |  | 0.01471 | 0.041483 | 0.016813 | 0.02189 | 0.04456 | 0.029533 | 0.05334 | 94.9361
45 | IE5 | 1000 | 0.0061937 | 0.0077647 | 0.0070441 | 0.0027612 | 0.0028203 | -0.0017413 | 0.026878 | 95.8 | 95.2002 |  | 0.0098738 | 0.034579 | 0.013212 | 0.018207 | 0.03906 | 0.028247 | 0.051721 | 95.0823
55 | IE5 | 1000 | 0.0047668 | 0.0079924 | 0.0075257 | 0.0029362 | 0.0030733 | 0.00063085 | 0.020162 | 96 | 95.4274 |  | 0.008711 | 0.028954 | 0.012202 | 0.016559 | 0.033673 | 0.027143 | 0.047087 | 95.5031
75 | IE5 | 1000 | 0.0049042 | 0.0076725 | 0.0075597 | 0.0041339 | 0.0046634 | -0.0037616 | 0.0186 | 96.3 | 95.7685 |  | 0.0075997 | 0.023458 | 0.011055 | 0.014208 | 0.028701 | 0.025105 | 0.043772 | 95.8064
90 | IE5 | 1000 | 0.0043722 | 0.0076126 | 0.0067388 | 0.0037358 | 0.0037424 | -0.0012809 | 0.016216 | 96.5 | 95.996 |  | 0.0074628 | 0.022799 | 0.010732 | 0.013978 | 0.027602 | 0.024007 | 0.041137 | 96.0489
110 | IE5 | 1000 | 0.0060399 | 0.0095391 | 0.0077403 | 0.0037472 | 0.0037751 | -0.0014625 | 0.014414 | 96.6 | 95.7858 |  | 0.009517 | 0.023033 | 0.013456 | 0.016321 | 0.028513 | 0.028072 | 0.043793 | 95.8044
132 | IE5 | 1000 | 0.0054048 | 0.0073973 | 0.0051463 | 0.0041355 | 0.0042707 | -0.0026098 | 0.017402 | 96.8 | 96.0317 |  | 0.0080922 | 0.023669 | 0.011021 | 0.01422 | 0.028318 | 0.023096 | 0.041147 | 96.0479
160 | IE5 | 1000 | 0.0051704 | 0.0078204 | 0.0049688 | 0.004412 | 0.0045212 | -0.0019993 | 0.014919 | 96.9 | 96.1548 |  | 0.0079552 | 0.021742 | 0.010964 | 0.013887 | 0.026579 | 0.022923 | 0.039813 | 96.1712
200 | IE5 | 1000 | 0.0049538 | 0.0074198 | 0.0055745 | 0.0038608 | 0.0039891 | -0.0019866 | 0.014795 | 97 | 96.2779 |  | 0.0076611 | 0.02118 | 0.010668 | 0.013495 | 0.025793 | 0.022616 | 0.038606 | 96.2829
250 | IE5 | 1000 | 0.0047859 | 0.0068988 | 0.0052712 | 0.0035436 | 0.0036818 | -0.0015963 | 0.013551 | 97 | 96.2779 |  | 0.0073576 | 0.019911 | 0.010169 | 0.012816 | 0.0242 | 0.021352 | 0.036136 | 96.5125
315 | IE5 | 1000 | 0.0046374 | 0.0063807 | 0.0049619 | 0.0032252 | 0.0033748 | -0.0013026 | 0.012385 | 97 | 96.2779 |  | 0.0070547 | 0.018643 | 0.0096701 | 0.012127 | 0.022607 | 0.020075 | 0.033663 | 96.7434
355 | IE5 | 1000 | 0.0043843 | 0.0061206 | 0.0048644 | 0.0031756 | 0.0032851 | -0.0011891 | 0.011914 | 97 | 96.2779 |  | 0.0067283 | 0.017943 | 0.0092586 | 0.011647 | 0.021795 | 0.019368 | 0.032555 | 96.8471
400 | IE5 | 1000 | 0.0039308 | 0.0058494 | 0.0046844 | 0.0031565 | 0.0033057 | -0.00020117 | 0.010825 | 97 | 96.2779 |  | 0.0063744 | 0.017305 | 0.0088031 | 0.011233 | 0.021055 | 0.018686 | 0.03155 | 96.9415
500 | IE5 | 1000 | 0.0038848 | 0.0055955 | 0.0046723 | 0.0030866 | 0.0030949 | -0.00098447 | 0.01098 | 97 | 96.2779 |  | 0.0060762 | 0.016536 | 0.0084356 | 0.010683 | 0.020163 | 0.017951 | 0.030329 | 97.0563
560 | IE5 | 1000 | 0.0038223 | 0.005519 | 0.0050763 | 0.003007 | 0.0029111 | -0.0011295 | 0.009706 | 97 | 96.2779 |  | 0.005902 | 0.01503 | 0.0083146 | 0.01027 | 0.018659 | 0.017759 | 0.028912 | 97.19
630 | IE5 | 1000 | 0.0035935 | 0.0053781 | 0.0055474 | 0.0030636 | 0.0030963 | -0.00049603 | 0.007739 | 97 | 96.2779 |  | 0.0057043 | 0.013487 | 0.0081731 | 0.0099325 | 0.017218 | 0.017746 | 0.027922 | 97.2837
710 | IE5 | 1000 | 0.0036176 | 0.0053978 | 0.005921 | 0.0030752 | 0.0030942 | -0.00049539 | 0.0075059 | 97 | 96.2779 |  | 0.0057426 | 0.01331 | 0.0082865 | 0.010003 | 0.017119 | 0.018108 | 0.028116 | 97.2653
800 | IE5 | 1000 | 0.0036436 | 0.005416 | 0.0062931 | 0.0030781 | 0.0030915 | -0.00050019 | 0.0072785 | 97 | 96.2779 |  | 0.0057809 | 0.013132 | 0.0083992 | 0.010072 | 0.017015 | 0.018465 | 0.028301 | 97.2478
900 | IE5 | 1000 | 0.0034297 | 0.0051412 | 0.0056664 | 0.0030748 | 0.0030879 | -0.00053238 | 0.0071893 | 97 | 96.2779 |  | 0.0054455 | 0.012688 | 0.0078775 | 0.0095254 | 0.016383 | 0.017309 | 0.027057 | 97.3656
1000 | IE5 | 1000 | 0.003206 | 0.0048682 | 0.0050403 | 0.0030655 | 0.0030803 | -0.00052364 | 0.0070621 | 97 | 96.2779 |  | 0.0051084 | 0.012235 | 0.0073546 | 0.0089796 | 0.015741 | 0.016155 | 0.025799 | 97.485
0.12 | IE5 | 750 | 0.22667 | 0.081484 | 0.053471 | 0.0020879 | 0.0027358 | -0.20466 | 0.3857 | 67.4 | 64.2578 |  | 0.22337 | 0.43211 | 0.25383 | 0.27531 | 0.46355 | 0.35692 | 0.54749 | 64.6209
0.18 | IE5 | 750 | 0.16333 | 0.049957 | 0.068725 | 0.0015424 | 0.0028069 | -0.20799 | 0.33448 | 71.9 | 68.992 |  | 0.14906 | 0.30717 | 0.17449 | 0.18548 | 0.33345 | 0.26272 | 0.41285 | 70.7788
0.25 | IE5 | 750 | 0.053577 | 0.023399 | 0.028447 | 0.0012365 | 0.002242 | -0.0605 | 0.141 | 85.2 | 83.3496 |  | 0.05492 | 0.14215 | 0.066149 | 0.077682 | 0.15406 | 0.11129 | 0.1894 | 84.0761
0.37 | IE5 | 750 | 0.069283 | 0.034608 | 0.046195 | 0.0057114 | 0.0074953 | -0.075992 | 0.19534 | 78.4 | 75.9396 |  | 0.074152 | 0.20207 | 0.091643 | 0.11016 | 0.22221 | 0.16423 | 0.28264 | 77.9642
0.55 | IE5 | 750 | 0.054367 | 0.033454 | 0.043427 | 0.0071693 | 0.0090749 | -0.062456 | 0.17836 | 80.6 | 78.3209 |  | 0.061126 | 0.18371 | 0.077851 | 0.096777 | 0.20371 | 0.14867 | 0.2634 | 79.1516
0.75 | IE5 | 750 | 0.052899 | 0.026303 | 0.024608 | 0.0065753 | 0.009993 | -0.036902 | 0.17945 | 82 | 79.8442 |  | 0.063145 | 0.20583 | 0.074554 | 0.10006 | 0.22054 | 0.13436 | 0.26293 | 79.1811
1.1 | IE5 | 750 | 0.041907 | 0.023266 | 0.022936 | 0.0043057 | 0.0052877 | -0.026603 | 0.1339 | 84 | 82.0312 |  | 0.050963 | 0.15786 | 0.061209 | 0.080316 | 0.17005 | 0.11068 | 0.205 | 82.9876
1.5 | IE5 | 750 | 0.044379 | 0.022731 | 0.030044 | 0.00066626 | 0.0011749 | -0.016761 | 0.10079 | 85.5 | 83.68 |  | 0.054064 | 0.1362 | 0.065404 | 0.080228 | 0.14791 | 0.11443 | 0.18302 | 84.5295
2.2 | IE5 | 750 | 0.043008 | 0.022674 | 0.024216 | 0.0013913 | 0.0018803 | -0.020634 | 0.099755 | 87.2 | 85.5573 |  | 0.051295 | 0.12978 | 0.061548 | 0.075312 | 0.14069 | 0.10534 | 0.17229 | 85.3031
3 | IE5 | 750 | 0.03129 | 0.018817 | 0.020361 | 0.0041525 | 0.0043949 | -0.0084376 | 0.080387 | 88.4 | 86.8881 |  | 0.040264 | 0.11053 | 0.048902 | 0.062461 | 0.12091 | 0.088483 | 0.15096 | 86.8836
4 | IE5 | 750 | 0.02277 | 0.01665 | 0.019494 | 0.0092515 | 0.0094645 | -0.0089004 | 0.068649 | 89.4 | 88.0008 |  | 0.030398 | 0.090805 | 0.038472 | 0.050429 | 0.10271 | 0.076306 | 0.13738 | 87.9214
5.5 | IE5 | 750 | 0.020577 | 0.014929 | 0.021339 | 0.001961 | 0.0022391 | -0.0076331 | 0.062631 | 90.4 | 89.1167 |  | 0.027689 | 0.081272 | 0.035479 | 0.045603 | 0.089915 | 0.069737 | 0.11604 | 89.6022
7.5 | IE5 | 750 | 0.017217 | 0.010799 | 0.013987 | 0.0061086 | 0.0061086 | -0.010647 | 0.060377 | 91.3 | 90.1239 |  | 0.022022 | 0.07243 | 0.027511 | 0.037029 | 0.080425 | 0.054828 | 0.10395 | 90.5838
11 | IE5 | 750 | 0.011818 | 0.009438 | 0.010617 | 0.0043798 | 0.0044914 | -0.0053598 | 0.048445 | 92.2 | 91.1337 |  | 0.016615 | 0.059302 | 0.021086 | 0.029451 | 0.065589 | 0.043522 | 0.083829 | 92.2655
15 | IE5 | 750 | 0.011645 | 0.0096535 | 0.018221 | 0.0039664 | 0.0041608 | -0.0034909 | 0.042455 | 92.9 | 91.921 |  | 0.017056 | 0.055413 | 0.022997 | 0.030651 | 0.063015 | 0.05042 | 0.086611 | 92.0292
18.5 | IE5 | 750 | 0.010577 | 0.0085069 | 0.017375 | 0.0036653 | 0.0037758 | -0.0038992 | 0.037318 | 93.3 | 92.3717 |  | 0.015219 | 0.04836 | 0.020705 | 0.027248 | 0.055369 | 0.045699 | 0.077318 | 92.8231
22 | IE5 | 750 | 0.0079679 | 0.0080565 | 0.01372 | 0.0043556 | 0.0044541 | -0.0029961 | 0.034442 | 93.6 | 92.71 |  | 0.012329 | 0.043653 | 0.017036 | 0.023362 | 0.050163 | 0.03906 | 0.07 | 93.4579
30 | IE5 | 750 | 0.0078535 | 0.0077362 | 0.017242 | 0.0048971 | 0.0050175 | -0.0012029 | 0.029438 | 94.1 | 93.2745 |  | 0.0125 | 0.040638 | 0.017803 | 0.023716 | 0.04797 | 0.042068 | 0.070981 | 93.3723
37 | IE5 | 750 | 0.007202 | 0.0066686 | 0.015321 | 0.0048586 | 0.0050902 | -0.0048627 | 0.032909 | 94.4 | 93.6136 |  | 0.010764 | 0.039406 | 0.015439 | 0.021088 | 0.046115 | 0.037475 | 0.067187 | 93.7043
45 | IE5 | 750 | 0.0058402 | 0.0082298 | 0.014131 | 0.0029291 | 0.0032024 | -0.0021323 | 0.022822 | 94.7 | 93.9531 |  | 0.0097324 | 0.030403 | 0.014523 | 0.018693 | 0.036442 | 0.034373 | 0.055022 | 94.7848
55 | IE5 | 750 | 0.0059514 | 0.0069795 | 0.016135 | 0.0036667 | 0.003564 | -0.00034398 | 0.022352 | 94.9 | 94.1795 |  | 0.010087 | 0.031852 | 0.014956 | 0.019572 | 0.038207 | 0.036289 | 0.058304 | 94.4908
75 | IE5 | 750 | 0.006099 | 0.0071061 | 0.019498 | 0.0016751 | 0.0018999 | -0.0010974 | 0.019139 | 95.3 | 94.6328 |  | 0.01005 | 0.027673 | 0.015531 | 0.019091 | 0.033881 | 0.037833 | 0.05432 | 94.8479
90 | IE5 | 750 | 0.0078671 | 0.0093461 | 0.015161 | 0.0034518 | 0.0034514 | -0.00063831 | 0.01821 | 95.5 | 94.8597 |  | 0.012197 | 0.029802 | 0.017471 | 0.021211 | 0.036491 | 0.038334 | 0.056849 | 94.6209
110 | IE5 | 750 | 0.0062912 | 0.0075196 | 0.014421 | 0.0030106 | 0.0030318 | -0.00092999 | 0.014544 | 95.7 | 94.6822 |  | 0.0098078 | 0.023629 | 0.014474 | 0.017393 | 0.029534 | 0.032913 | 0.047888 | 95.43
132 | IE5 | 750 | 0.005973 | 0.0066865 | 0.01337 | 0.0034467 | 0.0034756 | -0.00086883 | 0.014503 | 95.9 | 94.927 |  | 0.0092369 | 0.023193 | 0.01351 | 0.016498 | 0.028885 | 0.030952 | 0.046586 | 95.5488
160 | IE5 | 750 | 0.0055405 | 0.0057252 | 0.012062 | 0.0038085 | 0.0038497 | -0.0007997 | 0.014185 | 96.1 | 95.1721 |  | 0.0084869 | 0.022304 | 0.012285 | 0.015282 | 0.027671 | 0.028389 | 0.044372 | 95.7513
200 | IE5 | 750 | 0.0054842 | 0.0058467 | 0.0095898 | 0.004223 | 0.0045878 | -0.0026576 | 0.014896 | 96.3 | 95.4174 |  | 0.0078958 | 0.021126 | 0.011275 | 0.014015 | 0.026301 | 0.025518 | 0.041969 | 95.9721
250 | IE5 | 750 | 0.0053552 | 0.0054244 | 0.011454 | 0.0037677 | 0.0037833 | -0.00081117 | 0.012214 | 96.3 | 95.4174 |  | 0.0080614 | 0.020009 | 0.011668 | 0.014286 | 0.025164 | 0.02677 | 0.041188 | 96.0441
315 | IE5 | 750 | 0.0047456 | 0.0051029 | 0.0093671 | 0.0037527 | 0.0037675 | -0.00085031 | 0.011987 | 96.3 | 95.4174 |  | 0.0072168 | 0.018917 | 0.010352 | 0.012915 | 0.023594 | 0.023667 | 0.037873 | 96.3509
355 | IE5 | 750 | 0.0045236 | 0.0048425 | 0.0089511 | 0.0037438 | 0.0037586 | -0.00084476 | 0.011275 | 96.3 | 95.4174 |  | 0.0068603 | 0.017895 | 0.0098518 | 0.012282 | 0.022424 | 0.022589 | 0.03625 | 96.5018
400 | IE5 | 750 | 0.0042979 | 0.0045793 | 0.0085285 | 0.0037429 | 0.0037615 | -0.00082052 | 0.01055 | 96.3 | 95.4174 |  | 0.0065032 | 0.016876 | 0.0093497 | 0.01165 | 0.021261 | 0.021509 | 0.03464 | 96.652
500 | IE5 | 750 | 0.0040667 | 0.0043183 | 0.0081132 | 0.0037335 | 0.0037526 | -0.0007695 | 0.0097981 | 96.3 | 95.4174 |  | 0.0061463 | 0.01585 | 0.0088495 | 0.01102 | 0.020088 | 0.020434 | 0.033013 | 96.8042
560 | IE5 | 750 | 0.0039608 | 0.0042628 | 0.0080973 | 0.0037018 | 0.0037853 | -0.00073671 | 0.0090944 | 96.3 | 95.4174 |  | 0.0059894 | 0.015052 | 0.0086756 | 0.010721 | 0.019272 | 0.020098 | 0.032166 | 96.8837
630 | IE5 | 750 | 0.0038123 | 0.0041858 | 0.0081436 | 0.0037029 | 0.0037557 | -0.00049512 | 0.008203 | 96.3 | 95.4174 |  | 0.0058291 | 0.014236 | 0.0085044 | 0.010442 | 0.018439 | 0.01981 | 0.031308 | 96.9642
710 | IE5 | 750 | 0.0038151 | 0.0041285 | 0.0089999 | 0.0037193 | 0.0037536 | -0.0004214 | 0.0071889 | 96.3 | 95.4174 |  | 0.0058265 | 0.013342 | 0.0086482 | 0.010415 | 0.017695 | 0.020398 | 0.031184 | 96.9759
800 | IE5 | 750 | 0.0038078 | 0.0040832 | 0.0098441 | 0.0037041 | 0.0037686 | -0.00031771 | 0.0061603 | 96.3 | 95.4174 |  | 0.005822 | 0.012448 | 0.0087906 | 0.01039 | 0.016947 | 0.020985 | 0.03105 | 96.9885
900 | IE5 | 750 | 0.0036895 | 0.0038744 | 0.0088451 | 0.0037156 | 0.0037493 | -0.00047695 | 0.0068943 | 96.3 | 95.4174 |  | 0.0055953 | 0.012792 | 0.0083243 | 0.010022 | 0.01705 | 0.01976 | 0.030291 | 97.0599
1000 | IE5 | 750 | 0.0035585 | 0.0036792 | 0.0078289 | 0.0037216 | 0.0037385 | -0.0005942 | 0.0075941 | 96.3 | 95.4174 |  | 0.0053664 | 0.013132 | 0.0078561 | 0.0096556 | 0.017151 | 0.018533 | 0.029527 | 97.132

## VFD
All data is based on the tables in IEC 61800-9-2, chapter 6.2, table 18 and Annex A table A.1
|  |  | Losses | [8 empty] | Eff / %
Motor | CDM |  | n= | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9
rated power | rated power | Class | T= | 0.25 | 0.5 | 1 | 0.25 | 0.5 | 1 | 0.5 | 1 | 1
kW | kVA
0.12 | 0.278 | IE1 |  | 0.3379 | 0.3384 | 0.343 | 0.3389 | 0.3404 | 0.3484 | 0.3439 | 0.3585 | 71.5137
0.18 | 0.381 | IE1 |  | 0.2524 | 0.2528 | 0.2575 | 0.2534 | 0.2548 | 0.2628 | 0.2583 | 0.273 | 76.7263
0.25 | 0.5 | IE1 |  | 0.1974 | 0.1978 | 0.2025 | 0.1984 | 0.1999 | 0.2078 | 0.2034 | 0.218 | 80.5009
0.37 | 0.697 | IE1 |  | 0.1477 | 0.1482 | 0.1529 | 0.1487 | 0.1502 | 0.1582 | 0.1537 | 0.1684 | 84.2381
0.55 | 0.977 | IE1 |  | 0.1114 | 0.1119 | 0.1166 | 0.1124 | 0.1139 | 0.1219 | 0.1174 | 0.1321 | 87.2009
0.75 | 1.29 | IE1 |  | 0.0896 | 0.09 | 0.0947 | 0.0906 | 0.092 | 0.1 | 0.0955 | 0.1102 | 89.0913
1.1 | 1.71 | IE1 |  | 0.0686 | 0.0713 | 0.0782 | 0.0693 | 0.0733 | 0.084 | 0.0768 | 0.0951 | 90.4432
1.5 | 2.29 | IE1 |  | 0.0556 | 0.0583 | 0.0652 | 0.0563 | 0.0603 | 0.071 | 0.0638 | 0.0821 | 91.6404
2.2 | 3.3 | IE1 |  | 0.0545 | 0.0482 | 0.0551 | 0.0461 | 0.0502 | 0.0609 | 0.0537 | 0.072 | 92.5926
3 | 4.44 | IE1 |  | 0.0407 | 0.0435 | 0.0504 | 0.0141 | 0.0455 | 0.0562 | 0.049 | 0.0672 | 93.0521
4 | 5.85 | IE1 |  | 0.0374 | 0.0402 | 0.0471 | 0.0382 | 0.0422 | 0.0529 | 0.0457 | 0.0639 | 93.3707
5.5 | 7.94 | IE1 |  | 0.0335 | 0.0363 | 0.0432 | 0.0342 | 0.0383 | 0.049 | 0.0418 | 0.0601 | 93.7402
7.5 | 9.95 | IE1 |  | 0.028 | 0.0309 | 0.0402 | 0.0286 | 0.0328 | 0.0464 | 0.0361 | 0.0584 | 93.9065
11 | 14.4 | IE1 |  | 0.0239 | 0.0268 | 0.0361 | 0.0246 | 0.0287 | 0.0423 | 0.032 | 0.0543 | 94.31
15 | 19.5 | IE1 |  | 0.0215 | 0.0244 | 0.0337 | 0.0222 | 0.0263 | 0.0399 | 0.0296 | 0.0518 | 94.5577
18.5 | 23.9 | IE1 |  | 0.0202 | 0.0232 | 0.0324 | 0.0209 | 0.0251 | 0.0386 | 0.0283 | 0.0505 | 94.687
22 | 28.3 | IE1 |  | 0.0194 | 0.0223 | 0.0316 | 0.0201 | 0.0231 | 0.0378 | 0.0275 | 0.0497 | 94.7668
30 | 39.2 | IE1 |  | 0.0183 | 0.0212 | 0.0305 | 0.019 | 0.0231 | 0.0367 | 0.0264 | 0.0487 | 94.8667
37 | 47 | IE1 |  | 0.0176 | 0.02058 | 0.0298 | 0.0183 | 0.0224 | 0.036 | 0.0257 | 0.0479 | 94.9467
45 | 56.9 | IE1 |  | 0.0171 | 0.0201 | 0.0293 | 0.0178 | 0.022 | 0.0355 | 0.0252 | 0.0475 | 94.9868
55 | 68.4 | IE1 |  | 0.0162 | 0.0193 | 0.029 | 0.017 | 0.0213 | 0.0353 | 0.0247 | 0.0474 | 94.9968
75 | 92.8 | IE1 |  | 0.0158 | 0.0188 | 0.0285 | 0.0165 | 0.0208 | 0.0348 | 0.0242 | 0.0469 | 95.047
90 | 111 | IE1 |  | 0.0155 | 0.0186 | 0.0282 | 0.0162 | 0.0205 | 0.0345 | 0.0239 | 0.0466 | 95.0771
110 | 135 | IE1 |  | 0.0124 | 0.0148 | 0.0227 | 0.0132 | 0.0168 | 0.0291 | 0.0202 | 0.0411 | 95.6328
132 | 162 | IE1 |  | 0.0123 | 0.0147 | 0.0226 | 0.013 | 0.0167 | 0.0289 | 0.0201 | 0.041 | 95.6429
160 | 196 | IE1 |  | 0.0122 | 0.0146 | 0.0225 | 0.0129 | 0.0166 | 0.0288 | 0.02 | 0.0409 | 95.6531
200 | 245 | IE1 |  | 0.0121 | 0.0145 | 0.0224 | 0.0128 | 0.0165 | 0.0287 | 0.0198 | 0.0407 | 95.6734
250 | 302 | IE1 |  | 0.0117 | 0.0142 | 0.0224 | 0.0124 | 0.0161 | 0.0288 | 0.0195 | 0.041 | 95.6429
315 | 381 | IE1 |  | 0.0116 | 0.0141 | 0.0223 | 0.0123 | 0.0161 | 0.0287 | 0.0194 | 0.0409 | 95.6531
355 | 429 | IE1 |  | 0.0116 | 0.0141 | 0.0223 | 0.0123 | 0.016 | 0.0287 | 0.0194 | 0.0409 | 95.6531
400 | 483 | IE1 |  | 0.0116 | 0.0141 | 0.0223 | 0.0123 | 0.016 | 0.0287 | 0.0194 | 0.0409 | 95.6531
500 | 604 | IE1 |  | 0.0115 | 0.014 | 0.0222 | 0.0122 | 0.016 | 0.0286 | 0.0194 | 0.0408 | 95.6633
560 | 677 | IE1 |  | 0.0115 | 0.014 | 0.0222 | 0.0122 | 0.016 | 0.0286 | 0.0193 | 0.0408 | 95.6633
630 | 761 | IE1 |  | 0.0115 | 0.014 | 0.0222 | 0.0122 | 0.016 | 0.0286 | 0.0193 | 0.0408 | 95.6633
710 | 858 | IE1 |  | 0.0115 | 0.014 | 0.0222 | 0.0122 | 0.0159 | 0.0286 | 0.0193 | 0.0408 | 95.6633
800 | 967 | IE1 |  | 0.0115 | 0.014 | 0.0222 | 0.0122 | 0.0159 | 0.0286 | 0.0193 | 0.0408 | 95.6633
900 | 1088 | IE1 |  | 0.0115 | 0.0139 | 0.0221 | 0.0121 | 0.0159 | 0.0285 | 0.0193 | 0.0408 | 95.6633
1000 | 1209 | IE1 |  | 0.0114 | 0.0139 | 0.0221 | 0.0121 | 0.0159 | 0.0285 | 0.0193 | 0.0408 | 95.6633
|  |  | Losses | [8 empty] | Eff / %
Motor | CDM |  | n= | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9
rated power | rated power | Class | T= | 0.25 | 0.5 | 1 | 0.25 | 0.5 | 1 | 0.5 | 1 | 1
kW | kVA
0.12 | 0.278 | IE2 |  | 0.25343 | 0.2538 | 0.25725 | 0.25417 | 0.2553 | 0.2613 | 0.25793 | 0.26887 | 76.9971
0.18 | 0.381 | IE2 |  | 0.1893 | 0.1896 | 0.19312 | 0.19005 | 0.1911 | 0.1971 | 0.19373 | 0.20475 | 81.4664
0.25 | 0.5 | IE2 |  | 0.14805 | 0.14835 | 0.15188 | 0.1488 | 0.14993 | 0.15585 | 0.15255 | 0.1635 | 84.6262
0.37 | 0.697 | IE2 |  | 0.11077 | 0.11115 | 0.11467 | 0.11152 | 0.11265 | 0.11865 | 0.11528 | 0.1263 | 87.6937
0.55 | 0.977 | IE2 |  | 0.08355 | 0.083925 | 0.08745 | 0.0843 | 0.085425 | 0.091425 | 0.08805 | 0.099075 | 90.0833
0.75 | 1.29 | IE2 |  | 0.0672 | 0.0675 | 0.071025 | 0.06795 | 0.069 | 0.075 | 0.071625 | 0.08265 | 91.5891
1.1 | 1.71 | IE2 |  | 0.05145 | 0.053475 | 0.05865 | 0.051975 | 0.054975 | 0.063 | 0.0576 | 0.071325 | 92.6569
1.5 | 2.29 | IE2 |  | 0.0417 | 0.043725 | 0.0489 | 0.042225 | 0.045225 | 0.05325 | 0.04785 | 0.061575 | 93.5964
2.2 | 3.3 | IE2 |  | 0.040875 | 0.03615 | 0.041325 | 0.034575 | 0.03765 | 0.045675 | 0.040275 | 0.054 | 94.3396
3 | 4.44 | IE2 |  | 0.030525 | 0.032625 | 0.0378 | 0.010575 | 0.034125 | 0.04215 | 0.03675 | 0.0504 | 94.697
4 | 5.85 | IE2 |  | 0.02805 | 0.03015 | 0.035325 | 0.02865 | 0.03165 | 0.039675 | 0.034275 | 0.047925 | 94.9442
5.5 | 7.94 | IE2 |  | 0.025125 | 0.027225 | 0.0324 | 0.02565 | 0.028725 | 0.03675 | 0.03135 | 0.045075 | 95.2305
7.5 | 9.95 | IE2 |  | 0.021 | 0.023175 | 0.03015 | 0.02145 | 0.0246 | 0.0348 | 0.027075 | 0.0438 | 95.3592
11 | 14.4 | IE2 |  | 0.017925 | 0.0201 | 0.027075 | 0.01845 | 0.021525 | 0.031725 | 0.024 | 0.040725 | 95.6709
15 | 19.5 | IE2 |  | 0.016125 | 0.0183 | 0.025275 | 0.01665 | 0.019725 | 0.029925 | 0.0222 | 0.03885 | 95.862
18.5 | 23.9 | IE2 |  | 0.01515 | 0.0174 | 0.0243 | 0.015675 | 0.018825 | 0.02895 | 0.021225 | 0.037875 | 95.9616
22 | 28.3 | IE2 |  | 0.01455 | 0.016725 | 0.0237 | 0.015075 | 0.017325 | 0.02835 | 0.020625 | 0.037275 | 96.023
30 | 39.2 | IE2 |  | 0.013725 | 0.0159 | 0.022875 | 0.01425 | 0.017325 | 0.027525 | 0.0198 | 0.036525 | 96.0999
37 | 47 | IE2 |  | 0.0132 | 0.015435 | 0.02235 | 0.013725 | 0.0168 | 0.027 | 0.019275 | 0.035925 | 96.1616
45 | 56.9 | IE2 |  | 0.012825 | 0.015075 | 0.021975 | 0.01335 | 0.0165 | 0.026625 | 0.0189 | 0.035625 | 96.1924
55 | 68.4 | IE2 |  | 0.01215 | 0.014475 | 0.02175 | 0.01275 | 0.015975 | 0.026475 | 0.018525 | 0.03555 | 96.2001
75 | 92.8 | IE2 |  | 0.01185 | 0.0141 | 0.021375 | 0.012375 | 0.0156 | 0.0261 | 0.01815 | 0.035175 | 96.2387
90 | 111 | IE2 |  | 0.011625 | 0.01395 | 0.02115 | 0.01215 | 0.015375 | 0.025875 | 0.017925 | 0.03495 | 96.2618
110 | 135 | IE2 |  | 0.0093 | 0.0111 | 0.017025 | 0.0099 | 0.0126 | 0.021825 | 0.01515 | 0.030825 | 96.6884
132 | 162 | IE2 |  | 0.009225 | 0.011025 | 0.01695 | 0.00975 | 0.012525 | 0.021675 | 0.015075 | 0.03075 | 96.6962
160 | 196 | IE2 |  | 0.00915 | 0.01095 | 0.016875 | 0.009675 | 0.01245 | 0.0216 | 0.015 | 0.030675 | 96.704
200 | 245 | IE2 |  | 0.009075 | 0.010875 | 0.0168 | 0.0096 | 0.012375 | 0.021525 | 0.01485 | 0.030525 | 96.7196
250 | 302 | IE2 |  | 0.008775 | 0.01065 | 0.0168 | 0.0093 | 0.012075 | 0.0216 | 0.014625 | 0.03075 | 96.6962
315 | 381 | IE2 |  | 0.0087 | 0.010575 | 0.016725 | 0.009225 | 0.012075 | 0.021525 | 0.01455 | 0.030675 | 96.704
355 | 429 | IE2 |  | 0.0087 | 0.010575 | 0.016725 | 0.009225 | 0.012 | 0.021525 | 0.01455 | 0.030675 | 96.704
400 | 483 | IE2 |  | 0.0087 | 0.010575 | 0.016725 | 0.009225 | 0.012 | 0.021525 | 0.01455 | 0.030675 | 96.704
500 | 604 | IE2 |  | 0.008625 | 0.0105 | 0.01665 | 0.00915 | 0.012 | 0.02145 | 0.01455 | 0.0306 | 96.7118
560 | 677 | IE2 |  | 0.008625 | 0.0105 | 0.01665 | 0.00915 | 0.012 | 0.02145 | 0.014475 | 0.0306 | 96.7118
630 | 761 | IE2 |  | 0.008625 | 0.0105 | 0.01665 | 0.00915 | 0.012 | 0.02145 | 0.014475 | 0.0306 | 96.7118
710 | 858 | IE2 |  | 0.008625 | 0.0105 | 0.01665 | 0.00915 | 0.011925 | 0.02145 | 0.014475 | 0.0306 | 96.7118
800 | 967 | IE2 |  | 0.008625 | 0.0105 | 0.01665 | 0.00915 | 0.011925 | 0.02145 | 0.014475 | 0.0306 | 96.7118
900 | 1088 | IE2 |  | 0.008625 | 0.010425 | 0.016575 | 0.009075 | 0.011925 | 0.021375 | 0.014475 | 0.0306 | 96.7118
1000 | 1209 | IE2 |  | 0.00855 | 0.010425 | 0.016575 | 0.009075 | 0.011925 | 0.021375 | 0.014475 | 0.0306 | 96.7118
|  |  | Losses | [8 empty] | Eff / %
Motor | CDM |  | n= | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9
rated power | rated power | Class | T= | 0.25 | 0.5 | 1 | 0.25 | 0.5 | 1 | 0.5 | 1 | 1
kW | kVA
0.12 | 0.278 | IE3 |  | 0.19007 | 0.19035 | 0.19294 | 0.19063 | 0.19148 | 0.19598 | 0.19344 | 0.20166 | 81.6952
0.18 | 0.381 | IE3 |  | 0.14197 | 0.1422 | 0.14484 | 0.14254 | 0.14333 | 0.14783 | 0.14529 | 0.15356 | 85.4245
0.25 | 0.5 | IE3 |  | 0.11104 | 0.11126 | 0.11391 | 0.1116 | 0.11244 | 0.11689 | 0.11441 | 0.12262 | 88.0088
0.37 | 0.697 | IE3 |  | 0.083081 | 0.083363 | 0.086006 | 0.083644 | 0.084487 | 0.088987 | 0.086456 | 0.094725 | 90.4773
0.55 | 0.977 | IE3 |  | 0.062662 | 0.062944 | 0.065588 | 0.063225 | 0.064069 | 0.068569 | 0.066037 | 0.074306 | 92.3734
0.75 | 1.29 | IE3 |  | 0.0504 | 0.050625 | 0.053269 | 0.050963 | 0.05175 | 0.05625 | 0.053719 | 0.061988 | 93.5563
1.1 | 1.71 | IE3 |  | 0.038587 | 0.040106 | 0.043987 | 0.038981 | 0.041231 | 0.04725 | 0.0432 | 0.053494 | 94.3897
1.5 | 2.29 | IE3 |  | 0.031275 | 0.032794 | 0.036675 | 0.031669 | 0.033919 | 0.039938 | 0.035888 | 0.046181 | 95.1192
2.2 | 3.3 | IE3 |  | 0.030656 | 0.027113 | 0.030994 | 0.025931 | 0.028237 | 0.034256 | 0.030206 | 0.0405 | 95.6938
3 | 4.44 | IE3 |  | 0.022894 | 0.024469 | 0.02835 | 0.0079313 | 0.025594 | 0.031613 | 0.027563 | 0.0378 | 95.9693
4 | 5.85 | IE3 |  | 0.021038 | 0.022613 | 0.026494 | 0.021487 | 0.023738 | 0.029756 | 0.025706 | 0.035944 | 96.1596
5.5 | 7.94 | IE3 |  | 0.018844 | 0.020419 | 0.0243 | 0.019238 | 0.021544 | 0.027563 | 0.023512 | 0.033806 | 96.3797
7.5 | 9.95 | IE3 |  | 0.01575 | 0.017381 | 0.022613 | 0.016088 | 0.01845 | 0.0261 | 0.020306 | 0.03285 | 96.4785
11 | 14.4 | IE3 |  | 0.013444 | 0.015075 | 0.020306 | 0.013838 | 0.016144 | 0.023794 | 0.018 | 0.030544 | 96.7176
15 | 19.5 | IE3 |  | 0.012094 | 0.013725 | 0.018956 | 0.012488 | 0.014794 | 0.022444 | 0.01665 | 0.029138 | 96.864
18.5 | 23.9 | IE3 |  | 0.011362 | 0.01305 | 0.018225 | 0.011756 | 0.014119 | 0.021712 | 0.015919 | 0.028406 | 96.9403
22 | 28.3 | IE3 |  | 0.010913 | 0.012544 | 0.017775 | 0.011306 | 0.012994 | 0.021263 | 0.015469 | 0.027956 | 96.9873
30 | 39.2 | IE3 |  | 0.010294 | 0.011925 | 0.017156 | 0.010688 | 0.012994 | 0.020644 | 0.01485 | 0.027394 | 97.0462
37 | 47 | IE3 |  | 0.0099 | 0.011576 | 0.016762 | 0.010294 | 0.0126 | 0.02025 | 0.014456 | 0.026944 | 97.0933
45 | 56.9 | IE3 |  | 0.0096188 | 0.011306 | 0.016481 | 0.010013 | 0.012375 | 0.019969 | 0.014175 | 0.026719 | 97.1168
55 | 68.4 | IE3 |  | 0.0091125 | 0.010856 | 0.016313 | 0.0095625 | 0.011981 | 0.019856 | 0.013894 | 0.026662 | 97.1227
75 | 92.8 | IE3 |  | 0.0088875 | 0.010575 | 0.016031 | 0.0092812 | 0.0117 | 0.019575 | 0.013612 | 0.026381 | 97.1522
90 | 111 | IE3 |  | 0.0087188 | 0.010462 | 0.015863 | 0.0091125 | 0.011531 | 0.019406 | 0.013444 | 0.026212 | 97.1699
110 | 135 | IE3 |  | 0.006975 | 0.008325 | 0.012769 | 0.007425 | 0.00945 | 0.016369 | 0.011362 | 0.023119 | 97.4956
132 | 162 | IE3 |  | 0.0069188 | 0.0082688 | 0.012712 | 0.0073125 | 0.0093937 | 0.016256 | 0.011306 | 0.023062 | 97.5015
160 | 196 | IE3 |  | 0.0068625 | 0.0082125 | 0.012656 | 0.0072562 | 0.0093375 | 0.0162 | 0.01125 | 0.023006 | 97.5075
200 | 245 | IE3 |  | 0.0068062 | 0.0081563 | 0.0126 | 0.0072 | 0.0092812 | 0.016144 | 0.011137 | 0.022894 | 97.5194
250 | 302 | IE3 |  | 0.0065813 | 0.0079875 | 0.0126 | 0.006975 | 0.0090563 | 0.0162 | 0.010969 | 0.023062 | 97.5015
315 | 381 | IE3 |  | 0.006525 | 0.0079313 | 0.012544 | 0.0069188 | 0.0090563 | 0.016144 | 0.010913 | 0.023006 | 97.5075
355 | 429 | IE3 |  | 0.006525 | 0.0079313 | 0.012544 | 0.0069188 | 0.009 | 0.016144 | 0.010913 | 0.023006 | 97.5075
400 | 483 | IE3 |  | 0.006525 | 0.0079313 | 0.012544 | 0.0069188 | 0.009 | 0.016144 | 0.010913 | 0.023006 | 97.5075
500 | 604 | IE3 |  | 0.0064687 | 0.007875 | 0.012488 | 0.0068625 | 0.009 | 0.016088 | 0.010913 | 0.02295 | 97.5134
560 | 677 | IE3 |  | 0.0064687 | 0.007875 | 0.012488 | 0.0068625 | 0.009 | 0.016088 | 0.010856 | 0.02295 | 97.5134
630 | 761 | IE3 |  | 0.0064687 | 0.007875 | 0.012488 | 0.0068625 | 0.009 | 0.016088 | 0.010856 | 0.02295 | 97.5134
710 | 858 | IE3 |  | 0.0064687 | 0.007875 | 0.012488 | 0.0068625 | 0.0089438 | 0.016088 | 0.010856 | 0.02295 | 97.5134
800 | 967 | IE3 |  | 0.0064687 | 0.007875 | 0.012488 | 0.0068625 | 0.0089438 | 0.016088 | 0.010856 | 0.02295 | 97.5134
900 | 1088 | IE3 |  | 0.0064687 | 0.0078187 | 0.012431 | 0.0068062 | 0.0089438 | 0.016031 | 0.010856 | 0.02295 | 97.5134
1000 | 1209 | IE3 |  | 0.0064125 | 0.0078187 | 0.012431 | 0.0068062 | 0.0089438 | 0.016031 | 0.010856 | 0.02295 | 97.5134